| S N | Clause | Provision of Bidding Documents | Bidder’s Query | POWERGRID's Reply |
| --- | --- | --- | --- | --- |
| 1 | Appendix-G Vol. II Part-B 7.1 Pg. 02 of 16 | BOQ for supply for up gradation of NTAMC system 7.1 Workstation as per TS | Please provide split up of workstation quantity dedicated for SCADA/RAS/AFAS/VMS etc. systems. | Break up of Workstations are as follows: - Main NTAMC : 52 nos OperatorConsole-12, Development-3, Maintenance-13, RAS-2, AFAS-2, VOIP-1, Remote Console-5, Video Console- 9, & OTS-5 - Back up NTAMC : 26 nos OperatorConsole-4, Development-1, Maintenance-7, RAS-1, AFAS-1, VOIP-1, Remote Console-2, Video Console- 5, & OTS-4 - RTAMC : 19 nos OperatorConsole-4, Maintenance-7, VOIP-1, Remote Console-2, Video Console- 5. |
| 2 | Vol.II Part-B Section-3, 3.11.1 (h) Page 24 of 28 | 3.11.1 Substation Operation displays (h) Device wise display- Each device in a substation such as CB, Isolator, Transformer, Reactor, FSC, TCSC, SVC shall have a detailed display. All the parameters being monitored display. A sample display has been provided in Appendix- B. It shall be possible to define generic device display such as “400kV Circuit breaker of Manufacturer ‘A’ version-1” and have a defined no. of parameters. It is preferable to automatically generate device wise display by the display generation tool. This display shall have a specified no. of status and Analog values depending upon device type. Like for a circuit breaker it shall show (Analog- SF6 pressure/ Hydraulic oil pressure, Status such as Spring condition/compressor running etc.). These displays shall be provided to device experts and shall be grouped (for e.g. all transformers in a single group) for easy navigation by experts. | Is device wise display is expected for each device of substation or for each type of devices. Eg there might be 4 types of 20 CB in substation. In that case do we need to create 4 device displays? Or 20 device displays? | Device wise display shall be for each device. But similar devices can use a Device type display format. Eg. The SCADA system shall have 4 types of Device displays. The user shall be able to see any of the 20 devices in its specific device type display. |
| 3 | Vol.II Part-A Section-1 1.3. Page 10 of 32 | Existing systems at Control Centers MPLS based telecommunication link has been established by Employer/Owner at Control Centers as follows: i. 10 Mbps (2Mbps for Data & 8Mbps for Video) connectivity between substations & control centers (NTAMC, BNTAMC and respective RTAMC ii. 100 Mbps connectivity between RTAMC & NTAMC/BNTAMC. iii. 100 Mbps connectivity between ER-RTAMC & CR-RTAMC. iv. 1000 Mbps (1Gbps) connectivity between NTAMC & BNTAMC. | Is there any connectivity between CR-RTAMC and NTAMC/BNTAMC? If yes what will be bandwidth? | Yes. Bullet (ii) mentions the 100 Mbps connectivity between RTAMC(Electrical & Client) with NTAMC/BNTAMC control centers. |
| 4 | Appendix-L, Vol.II Part-B Page 1 of 2 | Cyber Security Audit Guidelines It will be the responsibility of the contractor to comply with audit Observations/recommendations and mitigate those identified threats / vulnerabilities / risks. | Please clarify cyber security scope at substation level. As we understand switches, firewalls at substation are not in bidders scope and hence any measures related to these devices and excluded from bidders scope. | - Switches, and router/ firewalls at substation level are not in Bidders scope for Cyber security. - All Substation devices provided under the project is covered in Bidder’s scope. |
| 5 | Vol.II Part-B Section-1 1.7. Page 8 of 11 | User Authentication and Authorization Authentication system shall be of Multi Factor Authentication with at least one factor being biometric type i.e. fingerprint sensor and shall work without any internet connectivity. Any hardware/Software if required for Multi factor authentication shall be provided by the Contractor at his own cost. This shall include all accounts for operators as well as for maintenance accounts. | We understand that biometric devices for MFA need to be installed on all workstations of MCC (Nos. 52), BCC (Nos. 26), RTAMC-ER (Nos. 95) and RTAMC-CR (Nos. 78). Biometric devices are not required to be installed at substation workstation. Please confirm our understanding. | Biometric MFA is envisaged in all Consoles at Control Center end only. |
| 6 | Vol.II Part-A Section-4 4.2 Page 05 of 25 | Support in case of End of Life or End of Support: The contractor has to ensure with OEM for maintenance and services support for the hardware and software delivered under this project till the completion of AMC period. In case, any hardware / software / equipment /component items of the systems supplied under the contract shall reach its End-of-Life (EOL) or End-of-Support (EOS) whichever is earlier, the Contractor shall replace such item with new Hardware or/and Software without any financial implication to employer. | Please specify the items for which OEM has to submit the EoL reports. Please be aware that there will be numerous components as part of the system (both active and passive). It is not possible to include all the items. | Bidder to Comply T.S. |
| 7 | Vol.II Part-A Section-4 4.16 Page 18 of 25 | Problem/Defect Reporting: Following Activities shall also be treated as Severity Level-2: - ·Non-availability of designated contractor’s Man-power at control centre ·Non-Availability of Spares ·Non- Completion of Preventive Maintenance Activity ·Database display activity beyond the stipulated time line ·Non-Submission of Monitoring report as specified ·Non –submission of Audit compliance report. ·Non-deployment of patches within the stipulated timeline. ·Non-completion of recommendation by OEM during Preventive maintenance Activity ·Non-completion of Integration activity within the stipulated time line. ·Non-reporting of camera due to issue in NVR server of particular SS ·Not integration of new element beyond aforesaid defined timeline. | At present there is no capping is provided on this clause. As per present clause the penalty may go beyond 100% of the quarterly amount, which is totally unacceptable. | Bidder to Comply T.S. |
| 8 | Vol.II Part-B Section-4 4.8.1 Page 17 of 21 | Auxiliary Memory Backup utility: The utility shall take image backup daily automatically on SAN Storage. It shall keep minimum two set of image backup of all the workstations. SAN storage shall have sufficient space to meet the requirement of three image backups of all servers in addition to the SCADA data storage. Each day it will take image backup, the utility shall allow restoration of the servers/workstation from this image backup without requiring any other software. | As per the clause, Contractor has to take backup of Servers and workstation each and backup will be kept on SAN storage. Also, the daily backups of images are not required, please change the same as fortnightly Back-up. For databases, daily backups will be taken and multiple backups will be kept. | Bidder to comply T.S. May also refer S.no 80 of Clarification 1. |
| 9 | Vol.II Part-B Section-4 4.8.1.1 Page 17 of 21 | Image Backup and Restoration Utility An image backup of the as built system of each of the Servers and workstations shall be provided on a user-selected archival device such as SAN Storage, which shall be used to restore the system. | There is no SAN storage defined at RTAMC-ER, please suggest where to keep the backup files. | Refer S.no 80 of Clarification 1. |
| 10 | Vol.II Part-B Section-4 4.8.1.1 Page 17 of 21 | Image Backup and Restoration Utility It shall be possible to export Image backup files to “.iso” format to enable burning to CD/DVD. | There are different software applications will be used for back up and restoration. It will not comply .iso format. Please remove this clause. | Bidder to Comply TS (OR) Equivalent format to meet the requirement can be offered. |
| 11 | Vol.II Part-A Section-4 4.2 Page 05 of 25 | Support in case of End of Life or End of Support Support in case of End of Life or End of Support: The contractor has to ensure with OEM for maintenance and services support for the hardware and software delivered under this project till the completion of AMC period. In case, any hardware / software / equipment /component items of the systems supplied under the contract shall reach its End-of-Life (EOL) or End-of-Support (EOS) whichever is earlier, the contractor shall replace such item with new Hardware or/and Software without any financial Implication to employer. | Clarification-1 Reply: The Contractor shall replace the EOL and EOS Hardware/software if it has become either non-functional or the patches/updates have been discontinued from the OEM. As Windows Server 2019 is due to End of Support in Jan 2029, We understand PGCIL is looking one mandatory software upgrade here. Similarly, there will be mandatory updates for Linux too which may require change of hardware. Please specify, if such hardware change is mandated by Linux, how the commercial implication will be settled. | Bidder to Comply TS. |
| 12 | Appendix-G, Vol.II Part-B 7.1 Page 04 of 16 | BOQ for supply for up gradation of NTAMC system Inventory Management Software | As per BOQ, Inventory Management server is not included in BOQ. Kindly share detail with which server it will be integrated | NMS Server/ Patch Management Server etc. can be used for this application. The same shall be finalized during Detail Engineering. |
| 13 | Appendix P, Volume II Part B 7 Page 16 of 27 | S. No. 15 Support for Biometric (Finger Print Sensor) Authentication | Query: Please delete this clause Suggestion: Please help remove the same. Reason: Workstations does not have any integrated Biometric(Finger Print Sensors) | Bidder to comply T.S. |
| 14 | Appendix P, Volume II Part B 10 Page 18 of 27 | Processor Terminal Laptop S. No. 3 Processor 1x8 core, Base Frequency- 3.2 GHz | Query: Kindly modify the clause as” Processor Terminal Laptop S. No. 3 Processor 1x8 core, Base Frequency- 3.2 GHz or latest equivalent offer as per Intel Suggestion: Please relax on Base frequency as with Intel 12th Gen Processor the base frequency are not mentioned on Intel sites instead they mention Maximum Turbo Frequency of processor Reason: Intel does not mention Base frequency in Intel 12th gen Processors and instead mentions Maximum Turbo Frequency. | Bidder to comply T.S. |
| 15 | Appendix P, Volume II Part B 5 Page 18 of 27 | S. No. 5 Storage 512GB SSD (expandable up to 1TB) | Query: Kindly modify the clause as "S. No. 5 Storage 512GB SSD Reason: Laptop does support 1TB SSD but it supports single drive only. So either 512GB SSD or 1 TB SSD can be installed at a time | The expansion requirement of storage (up to 1TB) is also acceptable by replacement of originally installed storage disk. |
| 16 | Appendix P, Volume II Part B 10 Page 19 of 27 | S. No. 11 Serial port support | Query: Please delete this clause Reason: There is no integrated Serial Port and it can only be though a third party USB to Serial ports splitter/converter | Serial port is required. Bidders can provide third party USB to Serial ports splitter/converter. |
| 17 | Appendix P, Volume II Part B 8 Page 16 of 27 | S No. 5 4K IPS widescreen LCD antiglare with WLED backlit colour monitor, resolution of 3840x2160 pixel | Query: In S. No 4 under resolution 3840 x 2160 is already mentioned which is 4K so please explain 4K IPS support Suggestion: Panel Type to be IPS/VA/TN Reason: mentioning IPS will restrict competition so allow IPS/VA/TN | Bidder to comply T.S. |
| 18 | Vol.II Part-B Section-5 5.2.1 Page 6,7,8 of 41 Section 5 | Bidder can offer blade servers at Main and backup NTAMC’s and Rack servers at all RTAMC’s to meet the requirement of all servers in consultation with Employer. In general, blade server will be preferred at main and backup NTAMC to cater most of the requirement and high-end rack server swill be preferred at RTAMCs. The architecture shall be in line with latest cyber security guidelines | Please clarify if Bidder can propose either blade or Rack Server as per solution; since only preference is mentioned. Is the evaluation based on some quantitative points?? | Requirement of Blade server is deleted. (Refer Amendment No 1). |
| 19 | Vol.II Part-B Section-5 5.2.1 Page 7 of 41 | 5.2.1. - Blade Chassis Interconnect - Chassis should support simultaneous housing of Ethernet FC, SAS, iSCSI, IB interconnect fabrics, offering hot pluggable & redundancy as feature | Infiniband is special purpose connectivity and limited to few vendor's blade solution. Moreover the same is not required in the proposed requirement. We therefore request the same to be removed. Suggestion: Interconnect - Chassis should support simultaneous housing of Ethernet/ FC / SAS / iSCSI interconnect fabrics, offering hot pluggable & redundancy as feature as required by solution. | Requirement of Blade server is deleted. (Refer Amendment No 1). |
| 20 | Vol.II Part-B Section-5 5.2.1 Page 7 of 41 | 5.2.1. - Blade Chassis There should be at least two number of (redundant) enabled blade SAN switches each having 20/24 ports (10/40Gbps auto negotiation) which shall connect to uplink external storage / switch and downlink to internal servers. | Query: With converged network available, it is adding additional overhead to the requirement. We suggest to ask for converged network where in SAN Switches can interconnect at least 20 blade chassis reducing the number of FC switches required. Suggestion: BLADE SERVER CONVERGED INTERCONNECT There should be at least two number of blade Converged switches / Interconnect each having 200GbE downlink and uplink ports, Switches should provide connectivity to external LAN on 6 x 10GbE Ethernet and SAN on 4 x 32 Gbps FC ports along with SFP modules per switch. | Requirement of Blade server is deleted. (Refer Amendment No 1). |
| 21 | Vol.II Part-B Section-5 5.2.1 Page 8 of 41 | Processor - It should have minimum two nos. of x86 64-bit family minimum 2.30GHz or higher Each processor should have minimum 28 core Each processor should have minimum 55 MB Cache Each processor should have minimum 8GT/s QPI Each processor should have feature of hyper threading enabled | Query: There is no processor available at 28 core and 2.3 Ghz or higher base frequency with 55MB Cache in 3rd generation or latest generation processor. Suggestion: We request the clause to be changed to: It should have minimum two nos. of x86 64-bit family minimum 2.30GHz or higher Each processor should have minimum 28 core Each processor should have minimum 42 MB Cache. Each processor should have minimum 11GT/s UPI Each processor should have feature of hyper threading enabled | Requirement of Blade server is deleted. (Refer Amendment No 1). |
| 22 | Appendix-P, Vol.II Part-B 13 & 14 Page 1 of 27 | Application / communication and other servers - point 13 and 14 13. Type of Machine Virtual/Physical 14. Hardware Mounting Rack mountable / Blade Server | Does this means we can provide Virtual Machine or physical machines meeting the requirement and also provide Rack or blade servers as per our solution for all sites. Please clarify and also confirm if the qty mentioned in Appendix G is also for virtual/ Physical servers | Bidder to comply TS. Requirement of Blade server is deleted. (Refer Amendment No 1). Quantity mentioned in Appendix-G is for physical servers. |
| 23 | General Point |  | Please mention 3rd generation or latest generation processor to be proposed by bidder. | Bidder to comply T.S |
| 24 | Vol.II Part-B Section-5 Page 09 of 41 | Industry Standard Compliance. It should have ACPI 2.06.3 | Change this to ACPI Specification v2.0c or above | Requirement of Blade server is deleted. (Refer Amendment No 1). |
| 25 | Vol.II Part-B Section-5 Page 09 of 41 | Industry Standard Compliance. It should have PCIE 34.0 | This seems typo error. It should have PCIE 3.0 or 4.0 | Requirement of Blade server is deleted. (Refer Amendment No 1). |
| 26 | Warranty |  | Warranties are asked for over 9 years Kindly change it to 7 years Maintaining a solution for 9 years in moving time is very difficult | This clause is not mentioned in TS. However, supplied systems are expected to operate for more than 9 years considering the implementation phase and 7 years AMC period. |
| 27 | General |  | kindly clarify on ask of dual LAN ports in workstations. | Yes, dual LAN ports envisaged in all workstations. |