| Sl. No. | Clause ref | Provision | Queries asked by the bidder | POWERGRID’s clarification |
| --- | --- | --- | --- | --- |
| 1. | Clause 6.8 Statutory Clearances Section 3 EHV XLPE Cable |  | Post route survey, we need some clarification on below mentioned points : 1 During route survey, we understand that proposed cable has to laid along the road , however the road is maintained by Border road organization .We presumed that we have to take the permission from NHAI . Please confirm our assumption. 2. During route survey we found that there is Earthen shoulder area of road on both side . We presumed that this area comes under NHAI. Please confirm our assumption. 3. If we will opt to lay cable on Right hand side of Road when we go from Srinagar to LEH, as per information collected the area comes under Forest (Non -wild life forest) . We understand that PGCIL will provide the forest approval including forest clearances charges. | Point no 1,2 & 3 Please refer clause no 2 (C) of section project (Rev00) regarding route survey (for XLPE cable & FO cables) |
| 2. | Road Restoration (Clasue 6.6 d Laying & installation, Section 3 EHV XLPE Cable ) |  | After laying/installation all facilities shall be made good. Necessary road cutting and backfilling & compacting shall be in the scope of work. However, top layer of Concrete/bitumen road (wherever required) is excluded from the contractor’s scope. We understand from this clause that road restoration cost is under PGCIL . Please confirm. | As clarified earlier, please refer clause no: 2.0 (b) (ix) of section project (Rev00). The road restoration is in the scope of Bidder. |
| 3 | System parameter as per meteorological data of the site |  | The cable is to be laid through tough mountainous terrain having high altitude of 3500 MTR from MSL with extremely low temperatures. Accordingly, the cable, its jointing, end termination material and other equipment being supplied shall be suitable for operation at this climatic condition. Kindly suggest the Altitude and temperature correction factors for the material to be supplied. | Please refer the clause 10.0 (ii) of Section project (Rev00) |
| 4 | Technical Specification, Section Rev 00 SECTION –PROJECT 2. SCOPE | b. The installation, testing and commissioning work shall mainly consist of : ii. Coordination for statutory Clearances from relevant authorities for laying of cables. ix. After laying/installation of underground XLPE cables & FO cables, all facilities shall be made good. Some part of cable laying is on main road. Necessary road cutting & backfilling & compacting is also in the scope of work. Road shall be made restored in original shape after completion of work. Coordination for statutory Clearances from relevant authorities for road crossing is in the scope of bidder. | - PGCIL will bear all the statutory cost toward all clearances. - Kindly refer Clause 6.6 d) of 6 LAYING AND INSTALLATION of SECTION: EHV XLPE POWER CABLE, wherein Necessary road cutting and backfilling & compacting shall be in the scope of work, however, top layer of Concrete/bitumen road (wherever required) is excluded from the contractor’s scope. Hence Clause 2. SCOPE b), ix) of SECTION –PROJECT is in contradiction with the above refererd Clause 6.6 d) of 6 LAYING AND INSTALLATION of SECTION: EHV XLPE POWER CABLE. Request to kindly delete the Clause 2. SCOPE b), ix) of SECTION –PROJECT. Further, we understand that the scope of Bidder here shall be limited to only the coordination for statutory clearances from relevant authorities for road crossing, which will be done on behalf of PowerGrid. All the cost related to such statutory clearances shall be borne by PowerGrid, and the same shall be paid by PowerGrid directly to the relevant authorities. Powergrid will be responsible for the encumbrance free land for working. | - Please refer clause no: 6.8 of TS SECTION: EHV XLPE POWER CABLE (Rev 01) regarding statutory clearance charges. - As clarified earlier, please refer clause no: 2.0 (b) (ix) of section project. The road restoration is in the scope of Bidder. - Refer the reply as clarified above. |
| 5 | TECHNICAL SPECIFICATION, SECTION: EHV XLPE POWER CABLE C/ENGG/SPEC/EHV XLPE CAB REV.NO:01 SECTION: EHV XLPE POWER CABLE 6 LAYING AND INSTALLATION 6.6 | d) After laying/installation of underground XLPE cables & FO cables, all facilities shall be made good. Part of cable laying may be through Railway Under bridges, Railway Crossing, Nallahs, Road Crossing, Army area Zone etc. Necessary road cutting and backfilling & compacting shall be in the scope of work. However, top layer of Concrete/bitumen road (wherever required) is excluded from the contractor’s scope. |  |  |
| 6 | Technical Specification, Section Rev 00 SECTION –PROJECT 2. SCOPE | c. Route Survey (for XLPE power cable & FO cables) Identification of cable route of underground power cables & Fiber Optic Cables: The Contractor shall propose most suitable route for link keeping in view the following broad criteria: 1) The route shall be as straight and as short as possible. 2) Wet or unstable ground shall be avoided to the extent possible. 3) The route for the cables shall be away from the carriage-way of the road to the extent possible. 4) The route shall be suitable for placing manholes wherever required. 5) Future expansion of roads shall be taken into consideration to the extent possible. 6) Road, rail, river, culvert (nallah) crossing, trenchless digging shall be minimum. 7) As far as possible underground cable route shall be on the opposite side of the existing cables laid by DOT/BSNL or other utilities. Wherever both routes fall on the same side of the road, a spacing of about 2.0 m is to be maintained, to the extent possible. 8) Care must be taken to avoid choosing routes, roads, areas that are prone to floods etc. After finalizing the best alternative route, some trial pits shall be dug at suitably selected locations to assess the obstacles. It is necessary to locate the trial pits at proposed manhole locations. They shall be dug carefully keeping watch for the existing underground facilities. The presence of each type of facilities shall be recorded in the inspection note of the trial pit alongwith their sites sketch and shall be kept in record for future reference. These details shall be enclosed alongwith the survey report. The Contractor shall submit the survey report with the most suitable route for cable links along with details above. Contractor shall submit the final survey report for approval before implementation. The final survey report shall include atleast the following: 1) A drawing of the proposed route indicating all details of the route including relevant details of soil strata, bridges, culverts, causeways, rail over/under bridges, canal, defence area, underground gas/oil/water pipes line, power and communication cable routes, other important landmarks etc. 2) The distance of the cable route from the center of the road / rail / canal / river / bridge / culvert etc. shall be indicated on the route maps as well as documented in table. 3) City/town/village/forest/defence etc. area coverage. 4) Sections of the links where Trenchless Digging may be required. 5) Location and number of permanent and temporary manholes. 6) Location of all turns, bends and major landmarks. 7) List of authorities from which clearance shall be required to be obtained from each relevant section. The final survey report shall have to be approved by the Employer and requisite clearances need to be obtained before the cable installation work is commenced. The contractor shall prepare and submit for approval by the Employer, specific construction drawings for all types of soil strata/crossings taking into consideration the guidelines given in this specification. The construction/implementation shall be carried out as per the approved drawings. The construction drawings shall inter-alia include the longitudinal sectional diagram of the trench for different soil strata and detailed arrangement of crossings, number of pipes, size of pipes, location and position of manholes, other details as per the technical specifications. | In the final survey report, the list of authorities from which clearance is required to be obtained has to be mentioned. Accordingly please confirm that Bidder's responsibility is limited to only identifying the authorities as required for approval, coordination and documentation on behalf of PowerGrid so as to facilitate PowerGrid in getting the statutory clearances for the scope of work. All the cost related to such statutory clearances shall be borne by PowerGrid, and the same shall be paid by PowerGrid directly to the relevant authorities..Powergrid will be responisble for the encumbrance free land for working. Kindly confirm. | Please refer clause no 2 (C) of section project (Rev00) regarding route survey (for XLPE cable & FO cables) As clarified earlier Please refer clause no: 6.8 of TS SECTION: EHV XLPE POWER CABLE regarding statutory clearance charges Bidder shall quote meeting the requirement of bidding documents. |
| 7 | Technical Specification, Section Rev 00 SECTION –PROJECT 2. SCOPE 2.3 Statutory Clearances: | The Contractor shall be responsible for necessary coordination with concerned authorities/agencies for obtaining necessary clearance for laying of cable and carrying out excavation/ digging work from the authorities on behalf of the Employer/owner and provide requisite copies of information, maps, survey report etc to the authorities. The Employer shall assist the Contractor in obtaining such clearances by providing the authority letter or any other relevant document. The Contractor shall make an all out effort with the concerned authorities to get clearances expeditiously. The Contractor shall ensure quick and speedy clearances in order to implement the project within stipulated schedule. In case the authorities have some objections on certain sections of routes proposed and are unwilling to provide clearances, the Contractor shall propose an alternate route, promptly carrying out the survey and submit specific survey report for that and reapply for clearance after taking into account the comments/objections of the authority. | We request you to kindly refer Clause 6.2 and 6.3 of GCC wherein, all right of ways, wayleaves, approvals, permits, licences, clearances as required for the project are to be acquired by PowerGrid. Hence kindly confirm that Bidder's responsibility is limited to only coordination and documentation on behalf of PowerGrid so as to facilitate PowerGrid in getting the statutory clearances for the scope of work. All the cost related to such statutory clearances shall be borne by PowerGrid, and the same shall be paid by PowerGrid directly to the relevant authorities. Powergrid will be responisble for the encumbrance free land for working. Kindly confirm. | As clarified earlier Please refer clause no: 6.8 of TS SECTION: EHV XLPE POWER CABLE regarding statutory clearances & charges. Bidder shall quote meeting the requirement of bidding documents. |