| Sl. No. | Clause No. | Existing Clause/item | Amendment |
| --- | --- | --- | --- |
| 01 | Bid Price Schedule Sh-1,2 &3) | Activity Description; Material code; Item Description; Unit; Qty. Bid Price Schedule ( Sch-1&2). Miscellaneous; 1000013240; HDPE Pipe 40 mm dia.; M; 15. Bid Price Schedule ( Sch-1,2&3). UGFO Supply UGFO Erection; 1000012674 100003362; GI Pipe 100mm dia.; M; 15000. UGFO Spares; 1000012674; GI Pipe 100mm dia.; M; 525. Bid Price Schedule ( Sch-3). Cable-Main Equipment; 100003961; Laying of One (1) Fibre Optic cables along with joints as per TS; KM; 15. Miscellaneous; 100005858; Laying & Installation of 40 NB HDPE Pipes (as per TS); KM; 15. | Deleted |
| 02 | Bid Price Schedule ( Sch-3) | Bid Price Schedule ( Sch-3). Activity Description; Material code; Item Description; Unit; Qty. UGFO Erection; 100003247; Laying of PLB HDPE pipe in Open Trench for Fibre Optic Cable; KM; 14. 100003248; Installation of PLB HDPE pipe by Trenchless digging for Fibre Optic Cable; KM; 1. | Bid Price Schedule ( Sch-3). Activity Description; Material code; Item Description; Unit; Qty. UGFO Erection; 100003247; Laying of PLB HDPE pipe in Open Trench for Fibre Optic Cable; KM; 14.9. 100003248; Installation of PLB HDPE pipe by Trenchless digging for Fibre Optic Cable; KM; 0.1. |
| 03 | 10. Specific Requirement | 10. Specific Requirement - -- - - - New Clause - New Clause - New Clause | 10. Specific Requirement - - - - - Radial Moisture barrier shall be extruded Lead alloy “E” sheath is envisaged under subject package. - Distributed Temperature Monitoring System (DTS) is not envisaged under subject package. - The clause no: 1.14 of TS SECTION: EHV XLPE POWER CABLE (Rev 01) is modified as “The outer sheath shall consist of extruded black coloured HDPE with graphite coating/ Extruded Semiconducting layer. The outer sheath shall be suitably designed by the addition of chemicals in the outer sheath for protection against termite and rodent attack and shall be coated with graphite/ Extruded Semiconducting layer to facilitate sheath integrity test during manufacturing and post installation as per IEC 60229” |