| Sl. No. | Clause ref | Provision | Queries asked by the bidder | POWERGRID’s clarification |
| --- | --- | --- | --- | --- |
| 1. | Clause 1.2 – technical specification |  | Technical specification of this clause specifies both copper/aluminium conductor material. So please confirm. | The conductor material is Copper. Please refer clause no: 2.0 of section project (Rev00). |
| 2. | Clause 1.12 – technical specification of this cause | Clause 1.12 – technical specification of this cause | Clause 1.12 – technical specification of this cause specify both lead alloy E or corrugated aluminium sheath. So please confirm. | Please refer Amendment No-2. |
| 3 | Technical specification of cable | Technical specification of cable | This point is applicable for corrugated Aluminum sheathed cable – We have manufacturing facility with seam welded type corrugated aluminium sheath, which is followed and accepted worldwide, seamwelded corrugated Aluminium Sheath is equally robust mechanically and sheath is welded online. So please also include seam welded type corrugated aluminium sheath. | Please refer Amendment No-2. |
| 4 | Clause 1.12 – Short circuit current of metallic sheath | Clause 1.12 – Short circuit current of metallic sheath | Clause 1.12 – Short circuit current of metallic sheath is not mentioned in this clause. So please confirm. | The Short circuit current of metallic sheath shall be 40 kA/1 Sec Biddier shall quote meeting the requirement as per TS. |
| 5 | Technical specification of cable-Cable drum | Technical specification of cable-Cable drum | Please confirm maximum cable drum length that will consider for this project. | Please refer clause 2.2. of Standard Section “EHV XLPE POWER CABLE-Rev01” wherein it is mention that “Standard drum lengths for each segment for manufacturing shall be finalized during detailed engineering” |
| 6 | - | Route drawing | Please share the Route drawing for the proposed routes. | Preliminary Route is already enclosed at Annexure-1 of Section Project. Detailed route survey for the entire route length is in the scope of bidder. Bidder shall quote as BPS and meeting the requirement as per TS. |
| 7 | Route Survey |  | Please arrange the joint route survey along with PGCIL to acquaint with site feasibility. | Please refer Sl.No:6 above |
| 8 | General | Road Restoration: | Please confirm Road restoration shall be paid by customer directly to the board. | Please refer clause no: 2.0 (b) (ix) of section project. The road restoration is in the scope of Bidder. |
| 9 | Section 1 of the projects | ROW/Statutory Fee | "Coordination for statutory Clearances from relevant authorities for laying of cables" we understand that all fee towards statutory clearances and ROW shall be in scope of PGCIL. Kindly confirm. Bidder we do the Cordnation for from the PGCIL and utility. | Please refer clause no: 6.8 of TS SECTION: EHV XLPE POWER CABLE (Rev 01) and clause no 2.3 of section project. Bidder shall quote meeting the requirement as per TS. |
| 10 | 1.14 OUTER SHEATH EHV cable specification | The outer sheath shall consist of extruded black coloured HDPE with graphite coating | Graphite coating will not be suitable for 220 kV cable based on project site atmoshperic conditions so we propose to have Extruded Semiconducting layer over extruded black HDPE outer sheath instead of graphite coating. | Please refer Amendment No-2 |
| 11 | 1.10 INSULATION EHV cable specification | The extruded XLPE insulation shall be applied over the conductor screen to the desired thickness in a void free manner. | Since 220kV Underground cable will be laid between Minamarg & Zojilla where the project line traverses snow-bound difficult hilly terrain so we propose to add the insulation thickness requirement of 27.0 mm Nominal strictly as per IS 7098 (P-3). | The average thickness of insulation shall be not less than the nominal value of 27.0 mm for 220 kV as per clause no: 13.2 of IS 7098(P-3) |
| 12 | Price schedule | GI Pipe 100 MM - 15000 m ( Item No. 18) and 525 mtr has given (item no. 25) | Please clarify the where it will be used/utilized. As per scope, it is not getting clear for the utilization of the GI Pipe. | Please refer Amendment No-2. Bidder to comply the bidding documents. |
| 13 | Drawing & Specification | Joint bay | Kindly provide the joint bay drawing as same is not available with the tender documents | Please refer clause no: 24 Joint bay of TS SECTION: EHV XLPE POWER CABLE (Rev 01), the Joint bay drawing is in the scope of bidder. |
| 14 | Site survey | Route survey drawing/report is not available | Since whether condition at the site is not suitable for the site survey, requesting PGCIL to provide the previous site survey report of the cable route | Please refer the reply mentioned at Sl.no-6. |
| 15 | Clause no. 6.8 of section EHV Specification | Statutory clearance charges - Statutory clearances charges shall be borne by the employer. | We understand that all the statutory clearance charges shall be directly paid by PGCIL to the concern agency. Please confirm | Please refer the reply mentioned at Sl.no-9. |
| 16 | Erection price schedule PR activity no. 60 | installment of PLB duct pipe for OFC by trenchless - 1 km | There is 100 m trenchless qty given for EHV cable, however, it is 1 km trenchless for OFC cable, please clarify the exact requirement for trenchless | Please refer Amendment No-2 Bidder to comply the bidding documents |
| 17 | Tower/line dismantling | Tower/line dismantling | We understand that EHV Cable has to be laid parallel to your transmission line and shall be terminated to the existing tower. Hence tower/line dismantling is not in the scope of the bidder. Please confirm. | Please refer clause no: 2.0(b) (XX) of Section Project. Bidder shall quote meeting the requirement as per TS and as per BPS. Tower/line dismantling is not in the scope of the bidder. |
| 18 | Clause No. IX page 4 of 13 of section project | Road restoration | We understand that road restoration is not in the bidder's scope. Bidder has to take the statutory clearance for the cable laying from the concern agency and statutory charges shall be paid by the employer directly to the conern agency. Concerned agency (NHAI/BRO/ETC) shall restore the road at their own. Please confirm | Please refer clause no: 2.0 (b)(ix) of section project. The road restoration is in the scope of bidder. Regarding statutory charges please refer clause no: 6.8 of TS SECTION: EHV XLPE POWER CABLE (Rev 01). |
| 19 | Erection Price schedule PR activity no. 40 | Termination at both ends | Kindly clarify whether termination shall be installed on existing tower at both ends or separate tower/gantry needs to be constructed. Incase termination needs to be done on existing tower, then confirm the suitability of tower for the same. | Please refer clause no: 2.0(b) (XX) of Section Project. Bidder shall quote meeting the requirement as per TS and as per BPS. |
| 20 | Technical Specification (Vide letter dt:21.01.2022 & email dt:24.01.2022) | Lead Alloy/Corrugated aluminum sheath | To incorporate ‘Smooth welded aluminum sheath’ also which is superior design to that of Traditional ‘Corrugated aluminum sheath’ | Please refer Amendment No-2. |
| 21 | General | Route Sketch | It is requested of you to provide the Tentative Route Sketch for our better understanding of route. | Please refer Sl.no-6 for the subject query. |
| 22 | Price Schedule- Sch 1 | HDPE Pipe 40mm dia | The unit mentioned in BOQ is 'm' which we feel is not correct rather it should be 'Km'. Pl clarify. | Please refer Amendment No-2. |
| 23 | Vol 2, Part 2 | 4 Phase Link Box | As per the attached SLD in tender, 4 phase Link boxes are shown but in price schedule no such item is present. Pl clarifies. | Please refer the description of BPS mentioned at Sl: 7 in price schedule- Sch-3. Bidder may please quote as per BPS. |
| 24 | Price Schedule- Sch 3 | Painting of Towers | The unit mentioned in the BOQ is MT instead of sqm. Pl clarifies. | Bidder may please quote as per BPS. |
| 25 | Price Schedule- Sch 3 | Laying of Fiber Optic Cable | Pl calrify the scope of the mentioned item in Erection Boq so that it is easy to differentiate between the mentioned items. | Please refer Amendment No-2. |
| 26 | Price Schedule- Sch 3 | S.no. 10-road Crossings…; S.no. 22-Laying of PLB HDPE Pipe in Open Trench...; Sno.23-Laying of PLB HDPE Pipe by Trenchless.... | The HDD Qty mentioned is 100m in the BOQ. Laying of PLB Pipe in Open Trench is mentioned as 14Km & Laying by trenchless method is 1km which could not be possible as HDD is given as 100m. So, as per our understanding either the HDD qty mentioned is not correct or the qty for laying of PLB pipe through trenchless is not correct. Pl clarify. | Please Refer Amendment No-2. Bidder to comply the bidding documents |
| 27 | General | GI Pipe 100 mm dia | Pl clarify the scope of GI Pipe for our better understanding. Is the scope of this pipe is different from HDPE PLB pipe. Pl clarify. | Please Refer Amendment No-2. Bidder to comply the bidding documents |
| 28 | Vol 2, Part 1, Section Project | Formation of buried cable trenches for 220 kV cables as per specification including supply and installation of HDPE pipes, warning tape, construction of jointing bays, backfilling of trenches & restoration as per specification. Concrete trenches with precast covers may be used in exceptional cases in smaller portions, wherever bending of cables are involved and HDPE pipes cannot be laid. 8) Road and Rail crossings (wherever applicable) through HDPE pipe for each cable and restoration as per specification through trenchless crossings. Entry and exit pits shall be closed with sand beds and concrete slab for the proper protection of the cable. Further the ends shall be sealing in such a way so that water seepage is avoided. The contractor shall submit the arrangement of sealing during detailed engineering. 9) After laying/installation of underground XLPE cables & FO cables, all facilities shall be made good. Some part of cable laying is on main road. Necessary road cutting & backfilling & compacting is also in the scope of work. Road shall be made restored in original shape after completion of work. Coordination for statutory Clearances from relevant authorities for road crossing is in the scope of bidder. | In the stated clauses it is understood that restoration is in the scope of bidder. Request you to provide the tentative cross Section area to be restored along with the requisite specifications. Also, request you to Pl provide this restoration/reinstatement as an extra line item in the amended BOQ. | The cross Section area to be restored shall be as per original shape which is to be dismantled. Please refer the description of BPS mentored at Sl: 9 & 10 in price schedule: Sch 3, restoration work is included in the same if required. |
| 29 | General | Right of Way/Necessary Approvals/Permissions/Statutaory Clearances. | Pl confirms the associated charges for Right of Way/Necessary Approvals/Permissions/Statutaory Clearances for the tendered work is under bidder's or PGCIL. If the charges are borne by bidder then, Pl confirm whether the amount will be reimbursed or not. Also, it is requested to keep the approvals/clearances/permissions along with the statutory charges under PGCIL scope for hassle free operations. | Please refer the reply mentioned at Sl.no-9 above. |
| 30 | General | - | Pl share the contact details of the concerned along with the schedule to carry out the route survey. Also, request you to allow us to submit the queries post route survey. | Please refer the reply mentioned at Sl.no-9 above. |
| 31 | Volume-II_Part_1_of_2, 03 Section-EHV XLPE cable Rev01, SECTION: EHV XLPE POWER CABLE |  | Complete Installation conditions are not specified in the tender documents. Kindly provide below details: - A) Native Soil Thermal Resistivity. B) Native Soil / Ground Temperature. | Presently, no back filling of buried cable trench with Thermal backfill or sand or sieved native soil is in the scope. However, measurement of native soil thermal resistivity and other parameters to be carried out at the proposed 220kV Cable route location shall be decided during detailed engineering if required. |
| 32 | Section project | POWERGRID is undertaking Extension of 220 kV AIS Alusteng for 1 No of 25MVAr, 245kV Bus Reactor & Extension of 220kV GIS Drass Substation for 2 Nos of 25MVAr, 245kV Bus Reactor under Transmission System Strengthening of Srinagar Leh Transmission System to POWERGRID. Further due to possibility of avalanches in 15 Km stretch between Minamarg & Zojilla Top portions of Alusteng – Drass 220 kV S/c T/L section, 220kV, XLPE cable is to be provided to overcome the problems due to snow and avalanches under the said scheme. The associated Transmission System: Associated transmission system is as follows: Substation: i) Extension of 220kV GIS Drass Substation for 2 Nos. of 25MVAr, 245Bus Reactor. ii) Extension of 220kV AIS Alusteng Substation for 1 No. of 25MVAr, 245Bus Reactor. Transmission line: i) 15Km Stretch between Minamarg – Zojilla Top portions of Alusteng-Drass 220kC S/C T/L Section with underground XLPE cable with a provision of one spare cable. ​ | kindly confirm extension of Bus reactor for 220kV GIS Drass & Alusteng substation is consider in price schedule or not extension of Bus reactor for 220kV GIS Drass & Alusteng substation is consider in price schedule or not. | Please refer clause no: 2 of Section Project (Rev00) and BPS regarding the scope of work. |