| Sl. No. | Clause/Provision | Queries asked by the bidder | POWERGRID’s clarification |
| --- | --- | --- | --- |
| 1. | 220 kV XLPE Cable Joint Kits | As per Installation BOQ, item sl.no:2-1 Set has been asked. As per drawing No: C/ENGG/220kV/CABLE/SPLIT-Only 16 sections are considered. Accordingly, average Drum length is 937 mtr which is merely not possible. (Transportation will also not feasible due to tough terrain). Hence we request you to change the item unit as No’s instead of set and increase the cable sections. | The drawing No: C/ENGG/220kV/CABLE/SPLIT provided in the bid is tentative only. No. of sections shall be decided during detailed engineering after detailed survey by successful Bidder. Bidder shall quote as per BPS. |
| 2. | Statutory clearance-official Fees | As per 01 Section project, Clause 2(b) (ii)-Only Coordination with concern authorities in the scope of bidder. As per 02A Section –GTR, Revision -15, clause 10.3-fee shall be reimbursed by POWERGRID. Kindly clarify. | Confirmed. Please refer Clarification No-1 also. |
| 3 | Road restoration | 01 Section Project, clause 2(b) (ix)-restores in original shape in Scope of bidder. 03 Section –EHV XLPE Cable rev01, Clause 6.6(d)-top layer of concrete/bitumen road (where ever) required is excluded from Contrator scope. Kindly Clarify | The cross Section area to be restored shall be as per original shape which is to be dismantled. Please refer Clarification No-1also |
| 4 | Hume Pipe | As per BoQ, item no:19, NP3 DN100mm is mentioned As per Drawing no. C/ENGG/220kV/CURVATURE AREA and C/ENGG/220KV/TRE-FLAT-NP4 600 mm has mentioned. Kindly Clarify | Requirement of minimum 100mm, NP3 RCC Hume Pipe at item no. 19 for UGFO is in line with UGFO-TS requirements envisaged at clause 1.12.9. NP4 600 mm unreinforced Hume Pipe is required for Curvature area & Trefoil to Flat formation adjacent to JB as per drawing enclosed with the bid. Please refer Amendment No-3 |
| 5 | Duct Pipe Quantity | As per Supply & Transportation BoQ, item no.6, Duct Pipe quantity is only 15M. However, as per installation BoQ, item no.7 -15 kM Quantity has been mentioned. | Please refer Amendment No-2. |
| 6 | DTS system | Not Mentioned in BoQ, however requirement is mentioned in 03 Section-EHV XLPE cable Rev01 Caluse-34 Kindly Clarify. | DTS system not envisaged in the subject package. Please refer Amendment No-2 |
| 7 | FO Cable for DTS System | Not Mentioned in BoQ, however requirement is mentioned in 03 Section-EHV XLPE cable Rev01 Caluse34 Kindly Clarify, is the system is required? | DTS system not envisaged in the subject package. Please refer Amendment No-2 |
| 8 | Site Coordinates along with tower location is required (Physical survey for bidding is not feasible now) | Since, it is not possible to visit the site due to road closures in winter. Hence, Site Coordinates along with tower location is required. Kindly provide the same. | Please refer Amendment No-3 |
| 9 | Trench drawing- No. of Duct (C/ENGG/220kV/.CABLE/BCT) | Two duct pipes are shown in Drawings No. C/ENGG/220kV/CURVATURE AREA and C/ENGG/220KV/TRE-FLAT. However, only One duct is asked in supply BoQ and Drawing No. C/ENGG/220kV/CABLE/BCT Kindly Clarify. | Please refer Amendment No-3 |
| 10 | Supply BoQ-GI Pipe | As per supply BoQ, item No.18-item are asked for entire Route 15 km. | Requirement of G.I. pipe for UGFO has been deleted. Bidder may refer the Amendment No-2 please. |
| 11 | Clarification in drawing No: C /ENGG /220kV /Cable /BCT | Kindly clarify the distance between our cable and side wall of trench. (We are the same as 50mm each side, as this is not mentioned). | The total width of Buried cable trench already provided in the drawing No: C/ENGG/220kV/Cable/BCT. The drawing shall be finalized during detailed engineering meeting the requirement as per TS. |
| 12 | 1.10 INSULATION EHV cable specification | As per clarification – 1 customer (PGCIL) reply of s. no. 11 nominal XLPE insulation thickness 27.0 mm which is as per IS 7098 Part 3, whereas as per technical specification of clause 1.1 cable shall conform to the requirements of IEC 60502-2 (applicable clauses only) for construction and IEC 60840/IEC 62067 (as applicable) for testing. Please confirm XLPE insulation thickness as per IS7098 PART3 or IEC 62067. Further if insulation thickness as per IS 7098 Part 3, please confirm, Can we consider all other thicknesses like conductor screen, insulation screen, Lead sheath & outer sheath as per IS 7098 Part 3. | Confirmed. |