| Sl. No. | Bidding Document Clause No. | Provision in bidding document | Bidders' Query | POWERGRID Reply |
| --- | --- | --- | --- | --- |
|  | Vol. II of Bidding Documents- Annexure-I_Specific Requirement with Annexures_Rev 10 Clause no 8.2.6 | Transportation of Oil The insulating oil for the Transformer shall be delivered at site generally not before 90 days from the date of commissioning, with prior information to the Employer, in view of risk involved in balk storage, pilferage and fire hazard. In case this oil is not filled in Transformer due to delay in commissioning, same oil shall be used only after testing and ensuring that oil parameters are well within the specified limits. Insulating oil shall be delivered to the site in returnable flexi bag / tanker. The flexi bag / Stainless steel tanker shall be taken back without any extra cost to Employer within generally 45 days after utilisation of oil but in any case, before contract closing. However, the spare oil shall be delivered in non-returnable drums. | We will not be able to meet this requirement, in view of following facts – · Very limited availability of tankers with oil suppliers · Handling/unloading of oil supplies in oil tanker at site due to limited resources available at site or site not ready. · Practice for supplying oil in flexibag is not common in India, and hence it is not proven for site handling, possible mechanical damage, possible rodent issue, long term usage etc. It is once again requested to review requirement & accept the supply of oil in drums, which is a good ongoing proven practice. | Bidder shall quote meeting the requirement of bidding documents. |