## TW03
Clarification No-II(Technical) dated 11/08/2025 to the bidding documents for Tower Package TW03 for Zing-Zingbar to Sissu portion of ±350 KV HVDC Pang-Kaithal Transmission Line associated with Transmission system for evacuation of RE power from renewable energy parks in Leh (5 GW Leh-Kaithal transmission corridor). Spec No.: CC/NT/W-TW/DOM/A04/25/06315
Sl. No. | Volume/Section/ Clause No. | Bidder’s Query | Clarifications to Bidder’s Querry:
KPTL
1 | Clause 2.1.3.2, Section-02-OPGW rev1, Specification for OPGW | TS Clause no.2.1.3.2, Section-02-OPGW rev1, Specification for OPGW, Page 9 of 17, the provided parameter for 350kV Pang - Kaithal HVDC are only applicable for 24F and 48F. However, the tender specifies the requirement for 48F & 96F OPGW and the given parameters are not suitable for 96 Fiber. Please provide the appropriate technical parameter for 96F OPGW. At the last of Clause no.2.1.3.2, it is stated that “Or customised OPGW design suitable to tower /transmission line.” As the total lines fall in wind zone-2 with installation in a 15mm & 25mms (Radial Ice Thickness around conductor/OPGW). In this regard, the OPGW manufacturer asking for the following details for the Customised OPGW 96F. Please provide the same. 1. Diameter of OPGW Cables 2. UTS of OPGW Cable 3. Weight of OPGW Cable 4. Modulus of Elasticity 5. Coefficient of Linear Expansion 6. Area | 96F Fiber OPGW requirement is envisaged for repeater links, if required for commissioning of ±350kV Pang-Kaithal HVDC link. 48Fiber OPGW are envisaged to be installed in both peaks of proposed ±350kV Pang-Kaithal HVDC line. requirements in bidding documents have been specified accordingly. Further, TS has provisions for customized designs offered by bidders to meet the requirements during detailed engineering stipulated at clause no. 1.2, Section-01-OPGW, Specification for OPGW, Page 2 of 7 “……In case of constraints in adopting standard design for any of the transmission line(s) or for any specific sections such as higher spans (>600m), Valley crossings, snow covered sections or for other voltage levels & wind zones etc., the Contractor may propose customized design(s) during detailed engineering to meet the requirement.” Bidder to comply the bidding documents.
2 | Survey and Forest clearance | Based on our site survey for th esubject, we understand that the entire line traverses through a demarcated forest area (Protected Forest). As per the bidding documents, the detailed survey has already been completed by POWERGRID. In this regard, we seek clarification on the following points: 1) Has POWERGRID initiated the forest clearance process? 1) If yes, what is the anticipated timeline for obtaining working permission to commence site activities? | The forest proposal is under preparation