| Clarification No-I for Bidding documents of Substation Extension Package SS-35 for construction of 400kV GIS bay at 765/400kV Kanpur POWERGRID Substation under consultancy works for UPPTCL. Spec no. CC-CS/989-NR3/GIS-4019/3/G2 |  |  |  |  |
| --- | --- | --- | --- | --- |
| S.No | REFERENCE DOCUMENT | Clause Description | Bidder’s Query/Comments | POWERGRID’s Reply/Clarification |
|  | Section/ Clause No./ PAGE No. |  |  |  |
|  | Project/clause 4.1.5c) |  | We understand that Integration of new bays with NTAMC & NRLDC is limited to integration activity at Substation end only. We understand that any activity related to NTAMC/ NRLDC at control center end is not in Bidder scope | Bidder’s understanding is correct |
|  | Project/clause 4.1.5c) |  | As per our understanding we have to furnish FOTE for communication but there is no line item in schedule 1 or schedule 3 against which we can claim the amount. Please clarify. | Communication equipment are not envisaged under present scope bidder shall quote as per BPS. |
|  | Project/clause 12.11 |  | Kindly explain the scope in detail. SDH equipment is in PGCIL scope or in contractor scope or it is already exist, if in contractor scope please furnish the detail technical specification. Please furnish detail of NMS and how to integrate with it. | Communication equipment are not envisaged under present scope bidder shall quote as per BPS. |
|  | Project/clause 4.1.5c) |  | As per Section Project we have to do Integration of new bays with NTAMC, NRLDC but there is no line item in schedule 1 or schedule 3 against which we can claim the amount. Please clarify. | Communication equipment are not envisaged under present scope bidder shall quote as per BPS. |
|  | Price Schedule/Schedule1/ Sl.no.48 |  | Mandatory spare to be provided as per the BOQ, but spare list not available. We have considered each type of numerical relay applicable for the line protection, kindly clarify. | Please find Attached Mandatory spare list Annexure-III of Section Project. |
|  | GENERAL |  | Present scope 400kV line length details required, or requirement of line Differential protection (if any) to be clarified. | Approximate Line length is 50kM, However line differential protection not envisaged under present scope. |
|  | GENERAL |  | Existing Event Logger make and model (if any) to be noted. | It is already mentioned in Section Project that existing SAS at Kanpur substation of M/s ABB make, There is no separate Event logger. |
|  | GENERAL |  | Availability of GAS density trip logic in the existing control and relay panel scheme (if any) to be noted. | Detail of Gas density trip logic scheme shall be provided to successful bidder during detailed engineering. |
|  | GENERAL |  | Ghatampur TPS Ckt -II line relay panel -bay 404(present scope) panel location details required, whether these panel will be placed nearer to the existing panel. Or it will be placed in a new location. | Preferably the relay protection panel for bay no 404 shall be kept near to the existing CB panel for bay no.404, however same shall be decided during detailed engineering as per the actual site condition. |
|  | GENERAL |  | Availability of CT module/ Input and Output module in the existing BB (REB 670) details required. | Please refer clause no 4.1.5-b of section project, supply of CT module/ Input and Output module in the existing BB (REB 670) is not envisaged under present scope. Bidders are advised to visit substation site. |
|  | GENERAL |  | CB Relay panel for Ghatampur TPS ckt-II is existing, hence, the BCU availability to be confirmed and model no: to be noted. | Bidders understanding is correct, BCU is REC670 of ABB make |
|  | GENERAL |  | Queries related to Civil Work : 1. Existing soil investigation report/type of soil. 2. Please clarify, existing GIS building is designed for future extension or not? 3. Please clarify, chapter 12 of IS 800 to be considered for design of GIS building connections/base plate? 4. Please provide existing foundation layout, cable trench layout, drain layout, GIS building detailed drawings. 5. As per Kanpur Substation GA drawing, we have not seen construction of new road of width 3.75m and 5.5m but in price schedule quantities for same are given. Please clarify. 6. We understand that bidder to follow PGCIL issued standard detailed drawings for gantry and equipment support structures foundations. | - Details of soil type and soil investigation report shall be shared with the successful bidder. - Yes, the existing GIS building is designed for future extension. - Please refer cl 10.3.18 of the Technical Specification: Section: Civil Works. - Drain layout and GIS building detailed drawings shall be shared with the successful bidder. - Bidder to quote as per BPS. - As per cl 4.1.7 (a) (a) and 4.1.7 (b) (f) of the Section: Project, POWERGRID shall provide drawings of structure and foundation of standard equipment support structure and standard gantry structure. |
|  | Section Project ,Cl.12.11 Vol.III, Price Schedule | The broad Scope of the procurement of FO based Communication Equipment shall…. i) SDH Equipment along with suitable interfaces and line cards. | As per Section Project we understand new SDH Equipment (STM-4) & DTPC need to be proposed at Kanpur & Ghatmapur end. However please note that no SDH Equipment & DTPC Equipments quantities are specified in price schedule. Please confirm following: 1. Whether New SDH Equipment to be proposed at Kanpur & Ghatampur ends for bays under this project or existing SDH Equipment at Kanpur & Ghatampur ends will be augmented for new bays proposed under this project. Please clarify. 2. As per site survey existing Tejas SDH Equipment is available at Kanpur end. We understand existing Tejas equipments will be augmented by PGCIL/UPPTCL for new Kanpur400kV- Ghatmapur D/C Line | Communication equipment are not envisaged under present scope bidder shall quote as per BPS |
|  | Section Project ,Cl.12.11.iv) Technical Specifications Cl.2.1.2.1 | Integration of supplied equipment in the existing regional NMS Bidder shall provide the telecom equipment which can be integrated with the existing NMS server/s of the respective RLDC/ SLDC. The details of existing NMS server/s shall be provided during detailed engineering or to be ascertained by Bidder conducted during site survey. | Integration with existing NMS should not be compulsion to bidder as NMS being of proprietary & only OEM can work on the existing NMS. Under existing NMS only particular OEM make can be managed. It is not possible to manage non OEM equipments. Provided equipments can be managed locally through craft terminal. Please confirm our understanding. | Communication equipment are not envisaged under present scope bidder shall quote as per BPS |
|  | Section Project ,Cl.1.2 | The following system is envisaged under Consultancy Services to UPPTCL: i. 400 kV Bays at 765/400 kV Kanpur(GIS) Substation for Termination of 400 kV Kanpur(PG)-Ghtampur D/C Line (Appr. 50 kM). | We understand that only FOTE equipment is envisaged in scope of this project no PLCC equipments are to be proposed for this project. Please confirm. | Refer our reply above for requirement of communication equipment. No PLLCC equipment envisaged bidder to quote as per BPS. |
|  | Price Schedule/Schedule1 |  | Item description column is protected; we are unable to read complete description of Supply item. | Refer Amendment No- I |
|  | Price Schedule/Schedule1/ Sl.no.9 | Controlled switching device for 420 kV, 3 phase circuit breaker | Since it is mention in AIS Equipment Category so we are understanding that we have to intall CSD relay in AIS SF6 CB, but AIS SF6 CB is not in contractor's scope so where we have to install these relays. | CSD for GIS CB as per specification is in present Scope. |
|  | Section -Project |  | We are assuming that there is no requirement of RTV coating and we are considering normal creepage. Kindly confirm | RTV coating is not envisaged under present scope. Creepage requirement shall be as per the TS |
|  | Price Schedule/Schedule1/ Sl.no.35 | Partial Discharge Monitoring System for 220kV GIS Station | We are assuming that there is typographical error for 220KV GIS Station. | Refer our reply below for similar query. |
|  | Section -Project |  | Please provide the spacing of existing earth grid or earthmat layout. Also provide the detail of earthing work link to this job. | Please find attached the existing earthmat Drawing. |
|  | Section -Project |  | Kindly specify the location of Incomer DC Tower from which line is coming. | Location of Dead end tower will be decided during detailed engg. |
|  | Price Bid | Partial Discharge Monitoring System for 220kV GIS Station | Extension package is for 400kV GIS, but PDM in BOQ is for 220kV GIS. Kindly confirm the voltage level and type of PDM? | Supply of Portable PD monitoring system is envisaged under subject contract which is suitable for 400kV and 220kV. Accordingly Bidder to quote above item under BPS line item “Partial Discharge Monitoring System for 220kV GIS Station” |
|  | Technical | Layout Drawing | Kindly provide existing PINGGAO GIS layout. | Please find attached the existing GIS layout Drawing as Annexure-I |
|  |  |  | We Request you to provide the existing GIS BUSBAR interface module drawing | GIS BUSBAR interface module drawing shall be furnished during detailed engineering to the successful bidder. |
|  | SCC/ clause 23 & GCC/ clause 22.8 |  | We request that warranty for replaced items shall have a cut-off date beyond which all obligations of Contractor for warranty shall cease to exist. We cannot accept evergreen warranty clause under the agreement. | Provisions of the Document in this regard shall remain unchanged. |
|  | SCC/ clause 24 & GCC/ clause 22.8.1 |  | Kindly modify the clause as mention below: The Contractor's liability for latent defects warranty for (400kV Class) AIS Capacitive Voltage Transformer, Circuit Breaker & GIS shall be limited to period of five (05) years from the end of Defect Liability Period. | Bidders are requested to refer Clause no 22.8.1 of GCC and SCC, which inter-alia clarifies that the latent defects warranty for GIS shall be limited to a period of ten (10) years from the end of Defect Liability Period. |