| Sl. No. | Clause Reference | Existing Provision | Amended Provision |
| --- | --- | --- | --- |
| 1 | Volume II, Section I, Clause 3, | C; Sag Tension Requirements. 1; Ruling span(m); 400. 2; Tension at every day condition (32°C, no wind) (Kg); Not exceeding 22% of UTS of proposed conductor. 3; Tension at designed maximum temperature and no wind condition (Kg); Not exceeding 22% of UTS at designed maximum temperature. 4; Sag-Tensions under Condition-I. i); Sag for ruling span at designed maximum temperature & no wind condition (m); ≤15.04. ii); Sag for ruling span at minimum temp (0 deg C) and no wind condition (m); ≥9.51. iii); Tension at 32°C and full wind condition; ≤ 11421 kg corresponding to wind pressure of 140 kg/m2 & not exceeding 70% of UTS of proposed conductor. iv); Tension at designed maximum temperature and full wind condition; ≤ 11421 kg corresponding to wind pressure of 140 kg/m2 & not exceeding 70% of UTS at designed maximum temperature of proposed conductor. | C; Sag Tension Requirements. 1; Ruling Span (m); 400. 2; Tension at every day condition (32°C, no wind) (kg); Not exceeding 22% of UTS of proposed conductor. 3; Tension at designed maximum temperature and no wind condition(kg); Not exceeding 22% of UTS at designed maximum temperature. 4; Sag-Tensions under Condition-I. i); Sag for ruling span at designed maximum temperature & no wind condition (m); ≤15.03* * Sag of any phase shall not be more than the immediate lower phase.. ii); Sag for ruling span at minimum temp (0 deg C) and no wind condition (m); ≥9.51. iii); Tension at 32°C and full wind condition. a); Wind pressure: i) Top Circuit: Top- 186 Kg/m2 wind pressure Middle-183 Kg/m2 wind pressure Bottom-178 Kg/m2 wind pressure ii) Bottom Circuit: Top-172 Kg/m2 wind pressure Middle-166 Kg/m2 wind pressure Bottom-158 Kg/m2 wind pressure; Maximum Tension (Hz) i) Top Circuit: Top phase : 7467 kg Middle phase: 7402 kg Bottom phase: 7294 kg ii) Bottom Circuit: Top phase: 7162 kg Middle phase: 7029 kg Bottom phase: 6851 kg & not exceeding 70% of UTS of proposed conductor. |
|  |  | v); Tension at knee point temperature & no wind condition (Kg); Not exceeding 40% of UTS of core@ of proposed conductor. 5; Sag-Tensions under Condition-II. i); Sag for ruling span at designed maximum temperature & no wind condition (m); ≤15.12. ii); Sag for ruling span at minimum temp (0 deg C) and no wind condition (m); ≥9.63. iii); Tension at 32°C and full wind condition; ≤ 11421 kg corresponding to wind pressure of 191 kg/m2 & not exceeding 70% of UTS of proposed conductor. iv); Tension at designed maximum temperature and Full wind condition; ≤ 11421 kg corresponding to wind pressure of 191 kg/m2 & not exceeding 70% of UTS at designed maximum temperature of proposed conductor. v); Tension at knee point temperature & no wind condition (Kg); Not exceeding 40% of UTS of core@ of proposed conductor. Note: - In case more than one sag tension conditions are specified in the above table, Bidder shall offer only one design of HTLS conductor, which shall comply with all the above sag-tension requirements. - @UTS of core shall be equal to the Breaking strength of individual core wires before stranding X no. of wires in the core of offered conductor. | iv); Tension at designed maximum temperature and full wind condition. a); Wind pressure: i) Top Circuit: Top- 186 Kg/m2 wind pressure Middle-183 Kg/m2 wind pressure Bottom-178 Kg/m2 wind pressure ii) Bottom Circuit: Top-172 Kg/m2 wind pressure Middle-166 Kg/m2 wind pressure Bottom-158 Kg/m2 wind pressure; Maximum Tension (Hz) i) Top Circuit: Top phase : 7467 kg Middle phase: 7402 kg Bottom phase: 7294 kg ii) Bottom Circuit: Top phase: 7162 kg Middle phase: 7029 kg Bottom phase: 6851 kg & not exceeding 70% of UTS of proposed conductor at designed maximum temperature. v); Tension at knee point temperature & no wind condition (kg); Not exceeding 40% of UTS of core@ of proposed conductor. 5; Sag-Tensions under Condition-II. i); Sag for ruling span at designed maximum temperature & no wind condition (m); ≤15.14* * Sag of any phase shall not be more than the immediate lower phase.. ii); Sag for ruling span at minimum temp (0 deg C) and no wind condition (m); ≥9.62. iii); Tension at 32°C and full wind condition. a); Wind pressure: i) Top Circuit: Top- 186 Kg/m2 wind pressure Middle-182 Kg/m2 wind pressure Bottom-177 Kg/m2 wind pressure ii) Bottom Circuit: Top-172 Kg/m2 wind pressure Middle-165 Kg/m2 wind pressure Bottom-157 Kg/m2 wind pressure; Maximum Tension (Hz) i) Top Circuit: Top phase : 7531 kg Middle phase: 7440 kg Bottom phase: 7312 kg ii) Bottom Circuit: Top phase: 7183 kg Middle phase: 7012 kg Bottom phase: 6818 kg & not exceeding 70% of UTS of proposed conductor. iv); Tension at designed maximum temperature and full wind condition. a); Wind pressure: i) Top Circuit: Top- 186 Kg/m2 wind pressure Middle-182 Kg/m2 wind pressure Bottom-177 Kg/m2 wind pressure ii) Bottom Circuit: Top-172 Kg/m2 wind pressure Middle-165 Kg/m2 wind pressure Bottom-157 Kg/m2 wind pressure; Maximum Tension (Hz) i) Top Circuit: Top phase : 7531 kg Middle phase: 7440 kg Bottom phase: 7312 kg ii) Bottom Circuit: Top phase: 7183 kg Middle phase: 7012 kg Bottom phase: 6818 kg & not exceeding 70% of UTS of proposed conductor at designed maximum temperature. v); Tension at knee point temperature & no wind condition (kg); Not exceeding 40% of UTS of core@ of proposed conductor. 6; Sag-Tensions under Condition-III. i); Sag for ruling span at designed maximum temperature & no wind condition (m); ≤15.03* * Sag of any phase shall not be more than the immediate lower phase.. ii); Sag for ruling span at minimum temp (0 deg C) and no wind condition (m); ≥9.51. iii); Tension at 32°C and full wind condition. a); Wind pressure: Top-140 Kg/m2 wind pressure Middle-134 Kg/m2 wind pressure Bottom-128 Kg/m2 wind pressure; Maximum Tension (Hz) Top phase: 6439 kg Middle phase: 6300 kg Bottom phase: 6160 kg & not exceeding 70% of UTS of proposed conductor. iv); Tension at designed maximum temperature and full wind condition. a); Wind pressure: Top-140 Kg/m2 wind pressure Middle-134 Kg/m2 wind pressure Bottom-128 Kg/m2 wind pressure; Maximum Tension (Hz) Top phase: 6439 kg Middle phase: 6300 kg Bottom phase: 6160 kg & not exceeding 70% of UTS of proposed conductor at designed maximum temperature. v); Tension at knee point temperature & no wind condition (kg); Not exceeding 40% of UTS of core@ of proposed conductor. Note: - In case more than one sag tension conditions are specified in the above table, Bidder shall offer only one design of HTLS conductor, which shall comply with all the above sag-tension requirements. - @UTS of core shall be equal to the Breaking strength of individual core wires before stranding X no. of wires in the core of offered conductor. |
| 2 | Volume-III, Technical Data Sheet | Schedule-1 (HTLS Conductor) | Replaced with revised schedule-1, Rev-1 of Schedule-1, Technical Data Sheet attached. |
|  | Volume-II, Section-I, Clause 1.1 | ……………….. Package Details. HTLS Conductor Package CD01 for Supply of HTLS (ACSS type) Conductor and associated clamp fittings & accessories for Tower package(s) associated with Transmission network expansion in Gujarat (Part B). | ……………. Package Details. HTLS Conductor Package CD01 for Supply of HTLS (ACSS type) Conductor and associated clamp fittings & accessories for following Tower package(s) associated with Transmission network expansion in Gujarat (Part B): - Tower Package TW01 for a) M/C portion (Part-I) of i) 400 kV D/C (twin HTLS) Navasari (New) (South Gujarat)-Kala line and ii) 400 kV D/C (twin HTLS) Navasari (New) (South Gujarat)- Magarwada line b) D/C portion of 400 kV D/c (twin HTLS) Navasari (New) (South Gujarat)-Kala line - Tower Package TW02 for M/C portion (Part-II) of i) 400 kV D/C (twin HTLS) Navasari (New) (South Gujarat)-Kala line and ii) 400 kV D/C (twin HTLS) Navasari (New) (South Gujarat)- Magarwada line. |