| Sr.No. | Ref Section | Provision in bidding document | Bidders Queries | POWERGRID Reply |
| --- | --- | --- | --- | --- |
| 1. | Annexure-II of SECTION-PROJECT of Volume-II of Bidding Documents | Technical Parameters of 160 MVA, 220/132 kV Auto Transformer, 160 MVA, 220/66 kV System Transformer and 50 MVA, 132/33 kV System Transformer | The Tech specs attached with the tender is not as per CEA guidelines: The technical parameters as per CEA are attached below for the following rating Transformers: 1.160 MVA, 220/132 kV Auto Transformer 2.160 MVA, 220/66 kV System Transformer 3.50 MVA, 132/33 kV System Transformer You are requested to get them revised as per CEA by the customer Also, the rating 100 MVA, 220/132 kV Auto Transformer doesn’t exist in CEA specs. | Please refer Amendment-I |
| 2. | Annexure-II of SECTION-PROJECT of Volume-II of Bidding Documents | Technical Parameters of 160 MVA, 220/66 kV System Transformer | It has reference to your tender for 220kV Transformer Package- 2TR-01-BULK (AM). We are regularly participating in your tenders of 220 KV transformers. We are very keen to participate in this tender. We are not getting offers timely from our vendors for brought out items. Hence we are attaching herewith our request letter for due date extension of tender by 3-4 weeks. We have studied tender documents and we have following query on 160 MVA,220/66/11 kV POWER Transformer, Specified losses in ANNEXURE II are NLL: 30kW, LL: 200 kW(I2R:145kW) & AL: 6 kW (Max). These losses are too low and not achievable. As per CEA specification, Losses specified are NLL: 60kW, LL: 320 kW(I2R:265kW) & AL: 8 kW (Max). Kindly clarify which set of losses we should consider for this transformer. | Please refer Amendment-I |