Clarification No.1 dated 12.07.2022 for Package ERS-1 for procurement of ERS for upto 400kV (Twin Moose) transmission lines through indigenous vendor development

| Sr. No. | Clause No. and Details | Request for Clarification (From M/s Advait vide letter ref. no. Advait/Powergrid/ERS/001 Dated 30.06.2022) | Reply from POWERGRID |
| --- | --- | --- | --- |
| 1 | Price Schedule BOQ # 17 Composite Long Rod Post Insulator (3.5m Length, min. 90mm Core dia,120kN Tensile Strength, 90 kN Compressive Strength) | - Cantilever Strength has not been provided which is required to input into the PLS Pole Software for modelling of Insulated Cross Arm. This Cantilever strength is pertaining to complete Cross-arm assembly i.e. the combination of Bracing & Post Insulator. - Kindly provide basis of calculation of Tensile Strength Requirement. KINDLY CONFIRM. | - Refer clause 1.10.3, Section-II of TS for loading criteria of ERS. Since, the magnitude of the loads are inter-alia dependent on the design/dimension of ERS, the cantilever load requirement as well as rating of insulator for the same is to be ascertained by the contractor. - Tensile strength requirements have been calculated based on various forces acting on insulator along-with relevant factor of safety. Bidder to quote as per the requirements stipulated in the technical specifications/BOQ. |
| 2 | BOQ Item # 27 Motorized Sliding Gin Pole Set Including Capstan Hoist With PowerPack, Rope and Other Accessories | We understand that the requirement means Gin Pole with Motorized Winch Machine to be provided. - KINDLY CONFIRM. | It is clarified that Capstan is to be provided with Motorized Sliding Gin Pole for assisting in hoisting of ERS material. Bidder to quote as per the requirements stipulated in the BOQ. |
| 3 | BOQ Item # 39 Rock Anchor Installer Kit Including Pionjar or Eqvt Rock Drilling Machine, Rock Drilling Kits (4 per set), Extensions & Accessories | Per set of Rock Installer Kit – 4 sets of Rock Drilling Kits to be provided? KINDLY CLARIFY on the exact requirement. | It is clarified that each quantity of rock anchor installer kit shall contain four nos of rock drilling kits. |
| 4 | BOQ Item # 40 Manta Ray Anchor Installer Kit Including Load Locker, Extensions &Accessories | As per BOQ Item # 12, Manta Ray or Equivalent Anchor Assembly has been asked. For the Item # 40, also the Installation Kit can be provided for Manta Ray or Equivalent. - KINDLY CONFIRM. | Bidder’s understanding that the installer kit to be provided under BOQ item #40 shall be suitable for the anchor assembly offered under BOQ item#12 is correct. |
| 5 | BOQ Item # 41 Temporary Anchor/Stake Plate Including Stake Plate Extension (3 per Set) | KINDLY ADVISE the usage of the said item and also provide Technical Specification & Drawings. In case our system does not require the same, can it be skipped? KINDLY ADVISE. | All items mentioned in the BOQ are in the scope of the Contractor. Bidder to quote for all items as per BOQ. Temporary Anchor/Stake Plate are generally used to temporarily anchor the guy wires at the time of erection/assembly of ERS. Technical details/parameters/drawings of these items for the offered ERS is in the scope of Contractor. |
| 6 | BOQ Item # 45 Tower Alignment Clamp/Tool | KINDLY ADVISE the usage of the said item and also provide Technical Specification & Drawings. In case our system does not require the same, can it be skipped? KINDLY ADVISE. | All items mentioned in the BOQ are in the scope of the Contractor. Bidder to quote for all items as per BOQ. Tower Alignment Clamp/Tool are generally used for maintaining alignment of tower sections at the time of erection/assembly of ERS. Technical details/parameters/drawings of these items for the offered ERS is in the scope of Contractor. |
| 7 | BOQ Item # 51 PLSCADD Mast/Pole Software Complete with Technical Support & Update for 5 yrs BOQ Item # 52 PLSCADD Standard Software (Including Tower Spotting) Complete WithTechnical Support & Update for 5 yrs BOQ Item # 53 PLSCADD Tower Software Complete With Technical Support & Update for 5yrs BOQ Item # 54 Software for ERS | The design of ERS to be proposed by us requires only PLS-Pole (Mast Module) for analysis and PLS-CADD for other calculations as and when required by the purchaser. However, we understand that the PLS-Tower software would not be required for ERS (Pole/Mast) kind of structure and hence would not be required. However, in case it is still required by the Purchaser, the same can also be provided. “Software for ERS” has been asked in Iterm # 54, in addition to the item # 51, 52 & 53. The required software is already covered in Item 51 & 52, so by Item # 54, which other software has been asked? KINDLY CLARIFY ON THIS POINT. | Refer Amendment-I All items mentioned in the BOQ are in the scope of the Contractor. Bidder to quote for all items as per BOQ. Computer software for analyzing failure scenarios and identifying appropriate scheme of ERS deployment is to be provided by the Contractor. Contractor may choose to provide either their own software or separate PLS Mast/ Pole software under Item #54. |
| 8 | TS Section II – Clause # 1.2.2 …… The ERS structure shall facilitate tower climbing. The structure column section shall not be more than 4.2m (14 feet) in length…… | Please note that the ERS Module Design being proposed by us is designed by CSIR-SERC which is having the length of 4.288 Meter. Hence it is requested that the Length Criteria should be given Tolerance of ±5%, so that our INDEGENOUS design can be accommodated. KINDLY ADVISE & CLARIFY | Refer amendment-I |
| 9 | TS Section II – Clause # 1.5 Para # 1: ……… Depending upon the requirement, the angle of guy plates shall be 0/0, 0/45 or 45/45. It shall be made of light weight, high strength material. | Kindly elaborate more on the Guy Plate Angle requirement i.e. 0/0, 0/45 or 45/45. It would be better if purchase also provides the drawing of each configuration of guy wire requirement. (showing these angles) KINDLY CLARIFY. | It is clarified that the guy plates used for connection of guy wires shall be able to attain atleast the specified angles. Assembly and arrangement of guy wires shall depend on the design of ERS and are in the scope of contractor. |
| 10 | TS Section II – Clause # 1.9 Earthwire/ OPGW fittings. | Since for each set ERS Structure separate assembly of Earthwire & OPGW has been asked, we request to provide below details pertaining to OPGW. Modulus of Elasticity, Coefficient of Expansion, Self-Weight, UTS, Gross Area, Gust Factor and Drag Coefficient. KINDLY CLARIFY. | Bidders may refer clause 1.10.3.2 regarding Minimum technical parameters for earthwire. Equivalent OPGW is to be considered. |
| 11 | TS Section II – Clause # 1.10.3.1 The design of ERS towers shall be carried out by the Supplier considering loads, loading conditions as per IS 802. | IS 802 Standard being for the design of Transmission Line Tower Structure which is a kind of Permanent Structure. However, ERS is a temporary structure and should be designed only for Reliability Conditions and not for Broken Wire or Narrow Front wind conditions. KINDLY CLARIFY. | No change in technical specifications envisaged. Bidder to quote as per the requirements stipulated in the technical specifications. |
| 12 | TS Section II – Clause # 1.10.3.3 and 1.10.3.4 Wind load parameters / wind loads shall be considered for design of ERS towers with reference to IS:802: - Wind Span is given as 400m and Weight span is also mentioned in tabular format. | The Wind Span & Weight Span requirement in TS-VOL Section-II seems to be given in line of the Tower Design Parameters considering permanent structures. However, ERS structure are meant for Temporary Establishment and normally spans are within 200m or less than 200m. Hence smaller values of such spans should be considered. KINDLY CLARIFY. | No change in technical specifications envisaged. Bidder to quote as per the requirements stipulated in the technical specifications. |
| 13 | TS Section II – Clause # 1.10.3.3, Sr. # 2. The wind speed is mentioned as 47m/sec. | We understand that the Kargil Region lies in high wind speed area i.e. 55m/sec as per IS:802 and that too prone to ice. Hence the wind speed of 55m/sec and ice thickness should be taken into consideration. Also provide the everyday temperature, minimum temperature and max temperature for this region to calculate forces. The above mentioned consideration may further affect the Span Length, Guy Wire Requirement & Height Requirement. KINDLY CLARIFY. | No change in technical specifications envisaged. Bidder to quote as per the requirements stipulated in the technical specifications. |
| 14 | TS Section II – Clause 1.10.3.6 The Supplier shall furnish the limit loads as well as ultimate strengths of all components (along with calculations) during engineering stage. The Ultimate strengths finalised during detailed engineering stage shall be applicable for testing purposes. | The ERS modules being proposed by us meets the loading parameters as per IEEE-1070 requirements. Hence, those values for modules can be furnished. However, for other components like insulators, guy wires, hardware, tools the values will be furnished by the vendors/suppliers but calculations of limit loads & ultimate strengths are not provided being a patented item. KINDLY CLARIFY. | No change in technical specifications envisaged. Bidder to quote as per the requirements stipulated in the technical specifications. |
| 15 | TS Section II – Clause # 1.13 Clause # 1.13.1: An extensive……. Two Sets of such programs shall be supplied on CDs for compatible personnel computers using MS-DOS or WINDOWS. The computer program(s) shall be suitable for copying & multiple use by at least 3 (three) users simultaneously & independently. | Presently, the Computer software of PLS-Pole (Mast) and PLS-CADD come with a downloadable install file and not in CD or pen-drive. Program files are not suitable for copy since they come with license having machine/system locking feature. Also 2 sets of such programs would be used only by 2 users simultaneously due to non-copying feature and cannot be used simultaneously by 3 users. KINDLY CLARIFY. | Bidders may refer clarifications at sr no. 7 wherein it is clarified that Contractor may choose to provide either their own software or separate PLS Mast/ Pole software under Item #54. Technical requirements under Clause 1.13.1 is applicable for contractors own software and not for PLS-Pole (Mast) and PLS-CADD software. |
| 16 | TS Section II – Clause # 1.13 Clause # 1.13.3: The computer programme output data (for given load design scenario ) shall include but not limited to guy wire tension, maximum span for a given conductor height, compressive loads for the foundation plate, right of way area requirement, total anchor load requirement ,graphic representations of the structures to be built. | The purchaser has to perform maximum span allowable calculation on its own using the PLS-Pole and Spreadsheets provided by us. And this values would not be calculated directly on PLS-Pole. We understand that the Right of Way will vary depending on the different site conditions, which should be calculated/worked out manually by the user. KINDLY CLARIFY. | Corridor/Right of way requirements may vary based on the guy wire assembly/arrangements and are required to be furnished by the contractor. |
| 17 | TS Section II – Clause # 1.13.3 Clause # 1.13.5: In addition to the above computer programme, Supplier shall also supply PLS-CADD software package ……………. sag tension calculations, tower loading trees, tower analysis, foundation loads, tower spotting, etc. The Bidder shall quote for this item in the relevant schedule separately. | We understand that the ‘Tower Loading Trees’ are usually made in CAD software manually. Should we have to provide the AutoCAD or any other CAD software. No such item is present in the BOQ. ERS structure being proposed by us can be designed using PLS-Pole software. KINDLY CLARIFY. | Different softwares may be used for preparing Tower loading trees such as Microsoft excel, auto cad etc. it is clarified that providing these softwares are not covered under the scope of bidder. |
| 18 | TS Section II – Clause # 1.14 Clause # 1.14.4 After Purchaser's approval and successful completion of all type tests, the Supplier shall within three weeks, submit 10 prints, one set of good quality reproducible, one set of colour drawings in AutoCAD stored in CDs & one set of micro films of the approved drawings for Purchaser's use. | Colour Drawings in PDF format can only be provided in CD/Soft copy for components as being provided by the Vendors / Suppliers. Micro Films are not in general use being an old technology. KINDLY CLARIFY. | Refer amendment-I |
| 19 | TS Section II – Clause # 2.4 (2.4.1, 2.4.2 & 2.4.3) Performance Tests | The IEEE:1070 Standard consists of below tests. Part 1: Strength Tests and Gimbal Test Part 2: Production Test. Part-1 is Design Tests which shall be carried out once only on our manufactured modules in the third party accredited laboratory and certificates of the same would be provided. Part-2 i.e. Production Tests are performed on each module before dispatching at our works in witness of the Purchaser. KINDLY CLARIFY. | Performance tests are to be carried out as per clause 2.4, Section-II of the technical specification and IEEE 1070. |
| Sr. No. | Clause No. and Details | Request for Clarification (From M/s Madhav Engineers vide letter ref MADHAV/ERS/2022-23/3006 dated 30.06.2022 ) | Reply from POWERGRID |
| 1. | Clause 1.2, Section-II of TS and Annexure-A (BDS) | We refer to Technical Specification section II, Clause 1.2, “Modular Restoration structures and sub clause 1.2.2 Where in it is mentioned that “The Structure components shall be of light weight, made of high strength Aluminium Alloy or Hot Dip Galvanised structure steel or a combination of high strength Aluminium alloy & Hot Dip Galvanized structure steel”. However, Qualifying Requirements at Annexure-A (BDS), sub CL.No 1.1,1.2 & 1.3 under cl 1.0. “Technical Experience” seeks bidder's manufacturing & supply experience of Aluminium/Al. alloy modular structures or hardware fittings made of Aluminium/Al-extrusions for Trans lines/Substations based on technological support of the collaborator. Thus, this appears to be contradictory & needs clear cut clarification. Alternatively, it is suggested to delete use of Hot Dip Galvanised steel structure in the above mentioned clause. Please clarify. | Refer amendment-I |
| 2. | Clause 1.1,1.2 and 1.3 Section-II of TS | If a bidder has Technical experience as per Cl 1.1, 1.2 or 1.3 i.e. manufacturing & supply experience of Al. Alloy whether he can supply steel structure & other components of ERS made of the Dip Galvanised steel. Please clarify. | Refer amendment-I |
| 3. | Annexure-A (BDS) | Whether Bidder’s established manufacturing facility in India is as must condition for Technical Experience /bid qualification. Please confirm. | Yes |
| 4. | Annexure-A (BDS) | If bidder is class II local supplier without manufacturing facility but having collaboration with OEM who is fulfilling all technical experience, whether Bidder can be considered to be qualified in terms of Qualifying Requirements. | No |