| Slno | Clause Ref | Clause / Subject |  | Bidder’s Query | POWERGRID’s Reply |
| --- | --- | --- | --- | --- | --- |
|  | Appendix -2 (Price Adjustment) Section VI (Forms and Procedures) of Volume -I of Bidding Documents |  | Price Adjustment applicability of 110/22KV 25 MVA Power Transformer. | Dear Sir, With reference to the subject cited, kindly find our pre bid query/ clarification as below and request to clarify the same to prepare and submit the competitive bid for the same. As per Tender document Vol-1 Section - VI Forms and Procedures Appendix – 2, clause 1.1 & 1.2, Price adjustment applicability on Power Transformer is not mentioned as below however as per Price schedule 02 Nos. 110/22KV 25 MVA Power transformers are to be supplied. Therefore, Kindly confirm whether Price adjustment is applicable on Supply of Power Transformers or not. | As per provisions of the Bidding Document, Price Adjustment is applicable for 110/22KV 25 MVA Power transformer. |
|  | General & Model Technical Specification/ GIS technical Specification Rev5A cl.11.2, Volume -II of Bidding Documents | Insulation co-ordination and selection of surge arrestor: The contractor shall be fully responsible for complete insulation co-ordination of switchyard including GIS. Contractor shall carry out detailed studies and design calculations to evolve the required parameters locations, energy capability etc. of surge arrestors such that adequate protective margin is available between peak impulse, surge and power frequency discharge voltages and BIL of the protected requirement. |  | The subject project involves 132kV GIS LA requirement in Line bays & 132kV GIS LA has limited vendors & we are getting support from only one of the GIS LA vendors and that too lead time is 11 month from manufacturing clearance. Considering project timeline of subject project is 18 months.it seems difficult to procure & install GIS LA within existing floated project timeline as once after manufacturing clearance is received for GIS insulation coordination study further takes 2 months in finalization based on the past experience. There are two steps in receiving GIS LA manufacturing clearance as below:- - GIS LA document approval (Drawing + type test as per IEC) - Insulation coordination study & selection of surge arrester as per clause 11.2 of GIS technical specification Rev 5A. we generally don't face any issue in Sr. no. (a) above but in sr no (b), we don't get timely inputs from PGCIL to carry out insulation coordination study & then manufacturing clearance of GIS LA gets further delayed, so we are left with very little time to complete the project. We propose two solutions to resolve the above issue. 1) change GIS LA inspection level from category IV to category II to enable us with the option of procurement of GIS LA from more vendors. As in that case inspection by PGCIL shall not be mandatory at the country from which it has to be procured. 2) To increase the project timeline from 18 months to 21 months to ensure timely completion of the project. | Bidder to quote as per bidding document |