| Slno | Clause Ref | Clause / Subject | Bidder’s Query | POWERGRID’s Reply |
| --- | --- | --- | --- | --- |
|  | Model Technical Specification/ 400kV Transformer Specification (up to 400kV class) cl.3.14.3., Page no 7/185 Volume -II of Bidding Documents | Bidder / Manufacturer should have successfully carried out Dynamic Short Circuit Test on any rating of 132 kV or above voltage class transformer as on the originally scheduled date of bid opening and shall enclose the relevant Test Report / Certificate along with bid. In case bidder has not successfully tested 132 kV or above voltage class transformer for Dynamic Short Circuit Test, their bid shall be considered technically non-responsive. The offered transformer should comply the requirement of similarity clause specified in IS 2026 (PART 5) / IEC 60076-5 with respect to short circuit tested transformer. Further, design review of offered transformer shall be carried out based on the design of short circuit tested transformer. | As per PGCIL tender document, Dynamic short circuit test report of similar design is required having validity of 5 years. With reference to letter no. “File No. CEA-PS-14-169/2/2019-PSETD Division dated 26.06.2023 received from Director, Power System Engineering & Technology Development Division, CEA, Ministry of Power, Govt. of India” having clause no. iii) “ the Validity of DSC test for transformer shall remain till the design is changed. For this project, xx is proposing with available DSC test report of 31.5 MVA 132/33 kV for one PGCIL project conducted in year 2018. Detailed report is also attached for your reference and review purpose. Accordingly, repetition of Dynamic short circuit test for Power Transformer shall not be envisaged as there is not any change in design. In view of above you are requested to kindly provide confirmation on above point for subject tender for further proceed to prepare and submit competitive bid for the same. | Kindly refer to Cl. 3.14.3 of TS section Transformer (Upto 400kv Class) wherein it is clearly mentioned that ” The offered transformer should comply the requirement of similarity clause specified in IS 2026 (PART 5) / IEC 60076-5 with respect to short circuit tested transformer. Further, design review of offered transformer shall be carried out based on the design of short circuit tested transformer.” There is no requirement of 5 years validity of Dynamic short circuit test of similar design. Dynamic type test conducted on similar design shall remain valid till the design is changed. Bidder to quote as per bidding document. |