| Slno | Clause Ref | Clause / Subject | Bidder’s Query | POWERGRID’s Reply |
| --- | --- | --- | --- | --- |
| Volume-II Technical Specifications |  |  |  |  |
|  | GIS Rev-5A 5.36 | Indicators shall be provided on all circuit breakers, isolators and earth-switches, which shall clearly show whether the switches are open or closed. | Indicators shall be provided on Drive Box/ Equipment. Request for your acceptance. | Position Indicators on drive box is acceptable. The indicators shall be mechanically coupled directly to the main contact operating drive rod or linkages and shall be mounted in a position where they are clearly visible from the floor or the platform in the vicinity of the equipment as specified in referred clause |
|  | GIS Rev-5A 6.4.6 | Withstanding all dielectric stresses imposed on it in open condition at lock out pressure continuously (i.e. shall be designed for 2 p.u. across the breaker continuously, for validation of which a power frequency withstand test conducted for a duration of at least 15 minutes is acceptable). | We wish to clarify that subject clause requirement is not in line to IEC 62271-203 standards requirement. We confirm to offer GIS type tested as per IEC 62271-203. We do not envisage any test to be conducted against clause 6.4.6. | Bidder to quote as per bidding document. |
|  | GIS Rev-5A 6.7.1 e | An operation counter shall also be provided . | The operation counter shall be in LCC where it is easier to monitor / note along with other indications. | Noted |
|  | GIS Rev-5A 6.7.3 k | Separate MCBs shall be provided for each spring charging motor and the rating of MCBs shall be suitably selected to match the starting, running and stalling time. | Offered HMB drive is Spring-hydralic type, and is already accepted in PGCIL. For MCB requirement, If needed MCB will be provided in LCC, same is not feasible to be provided in Drives due to compactness and design constraints. | Noted. |
|  | GIS Rev-5A 6.7.3 I | An overload relay shall be provided for protection of the spring charging motor. | If needed relay will be provided in LCC, same is not feasible to be provided in Drives due to compactness and design constraints. | Noted. |
|  | GIS Rev-5A 7.2 | 7.2.13. The disconnectors and safety grounding switches shall have mechanical/electrical inter-locks to prevent closing of the grounding switches when isolator switches are in the losedposition and to prevent closing of the disconnectors when the grounding switch is in the closed position. | In our offered designed in 145KV GIS , there is a mechanical & electrical interlock between Disconnector & Earthing Switch i.e common drive for the disconnector and earthing switch in a . Hope the same is acceptable. | Common drive for DS and ES meeting other requirements of TS is acceptable. |
|  | GIS Rev-5A 8.8 | All portions of the grounding switch and operating mechanism required for grounding shall be connected together utilizing flexible copper conductors having a minimum cross-sectional area of 100 sq. mm. | In our offered GIS design, Earthing switches and its mechanism are connected via the enclosure i.e they make a continuous earthing path via enclosure itself and so is the case for all the componets. Further, the complete GIS is earthed / grounded at multiple points utilizing flat CU / GI bars. Hope the same is acceptable | Bidder to quote as per bidding document. |
|  | GIS Rev-5A 15.3.6 | All instrument transformer connections shall be hard wired to terminal block via ring type connection. | We understand this requirement is at LCC side only considering the reliability of latest design of Pin Type terminals, request to please accept the Pin type terminations as well. | Bidder to quote as per bidding document. |
|  | GIS Rev-5A 5.42 (9) | GIS manufacturer as per their design shall preferably use maximum three standard straight horizontal outdoor bus duct lengths for entire GIS installation to optimize the spare requirement. | Its not possible to built the GIS Layout using 3 lengths of busduct only. Request to accept more than 3 lengths of busduct. | Kindly refer cl. No.-5.41 of Specific requirement REV10 where it is clearly mentioned that “GIS manufacturer as per their design shall preferably use maximum Fifteen standard straight horizontal outdoor bus duct lengths for entire GIS installation to optimize the spare requirement." |
|  | GIS Rev-5A 8.13 | Mechanical position indication shall be provided locally at each switch and Electrical indication at each Local Control Cabinet (LCC) / SAS. | Shall be provided on drives. | Noted. Electrical indications shall be provided in LCC and SAS |
|  | GIS Rev-5A 7.2.10 | Each disconnector shall be supplied with auxiliary switch having additional 8 NO (Normally Open) and 8 NC (Normally Closed) contacts for future use over and above those required for switchgear interlocking and automation purposes. These spare NO and NC contacts shall be wired up to the local control cabinet | Shall be subject to space left during execution. However, to fulfil the requirement CMR may be used. | Bidder to quote as per bidding document. |
|  | BPS TS SAS TS Process Bus | SAS Process interface & Trafo DIT/MU panel required for process bus system is not mentioned in BOQ | we understand that SAS Process interface & Trafo DIT/MU panels required for process bus system and to be included. Kindly confirm in which item of BPS we should consider the SAS Process interface & Trafo DIT/MU panels. | The said SAS Process interface &Tranfo DIT/MU panel may be considered in BOQ item "complete Substation automation for 132 kV bays." |
|  | Section Project | As mentioned in section project, Siemens 7SD52 to be provided for Line differential relay of both 132kV feeder to match remote end. | Kindly note that we will provide GE make relays (L90 or P54x) and replace the remote end relays. Kindly confirm and provide Remote end details required for retrofit and integration if applicable | Bidder may replace remote end relays matching with relays provided at Lawspet end. However same is acceptable without any additional cost implication to POWERGRID and at risk of cost of bidder. The testing, commissioning and integration of the relays at remote end shall be done by the bidder in this case. Further bidder shall provide additional 1 nos. of line differential relay as spare without any additional cost implication to POWERGRID over and above the mandatory spare requirement for the package. The relevant drawings shall be shared with the bidder during detailed engineering. |
|  | SLD Section project | Centralised low impedance Busbar considered for present scope of bays 6 Nos as per SLD. | Kindly note that Centralised low impedance Busbar considered for present scope of bays 6 Nos as per SLD. Busbar for future bays not considered. Kindly confirm | Confirmed |
|  | CSP SAS | general | Since this is GIS system CRP & SGC/MU panels will be placed in GIS/control room. Outdoor panel with IP65 protection applicable only for DIT/MU panel for transformer | Confirmed |
|  | CSP SAS | general | SGC and MU clubbed in one IED. DIT and MU Functionality also clubbed in a single IED. Kindly confirm | DIT and MU Functionality for may be clubbed in a single IED as specified in cl. 7.0 iv) of Annexure VIII of TS section project |
|  | 9. Annexure-VIII_Process Bus-based SAS Sl.No 19.2 | Two instances of LBB function shall run in one standalone LBB IED subscribing sample value from redundant Merging units provided for the bay | Please clarify the term “Two instances of LBB function shall run in one standalone LBB IED subscribing sample value from redundant Merging units provided for the bay” | Two LBB functions shall run in single IED. The two LBB functions shall subcribe to Sample values from different Merging unit to ensure redundancy in case of failure of merging unit. In case two LBB functions are not available in single IED, bidder may offer separate IED for each LBB function. |
|  | Annexure-A5 | Separate process bus Engineering/Testing PC as per architecture | Since the Merging units are already connected to SBUS through separate port for MMS reporting, the configuration shall be possible though SBUS engineering PC. Please clarify the requirement for Separate process bus Engineering/Testing PC as per architecture | Bidder to quote as per bidding document |
|  | BPS 11KV SLD | SLD | As per BPS there is only 1 Set BUS PT mentioned against two bus PTs mentioned in the SLD. kindly confirm whether BUS PT are to be consider as per SLD i.e 02 Nos. or BPS. | The item : 24kV Indoor panel for Bus PTs - 1 set consists of 2 nos. PT, one no. for each bus section. Bidder to quote accordingly |
|  | 11KV Panel TS 8 of 25 | a) All busbar and jumper connections shall be of high conductivity aluminium alloy / Copper of adequate size and bus bar size calculation / supporting type test report shall be submitted for approval. They shall be adequately supported on insulators to withstand electrical and mechanical stresses due to specified short circuit currents. | As per specification both options are mentioned for Bus bar material copper as well as aluminium hence we request you to kindly confirm the requirement of Bus bar material Copper or Aluminium. | Bidder may offer either Aluminium alloy or copper conductor meeting the ampacity requirements of the panels. Type test reports for conductor used shall be submitted during detailed engineering to validate the capacity of the conductor. |
|  | TS 16 of 25 | 8.01 Type Test A. Switchgear Panel (with Circuit Breaker installed) a. Short circuit duty test | Kindly note that Duty test is applicable for CB truck only and not panel. We have type tested offered VCB standalone for duty test and not by installing CB in panel. | CB short circuit duty test conducted on standalone VCB is acceptable |
|  | i. Annexure-II_Specific Requirement Rev10-part1 B. Section GIS Rev 5A ii. SLD iii. GA | As per project-specific requirement: Sr. No. 13: For 220 kV and below voltage level GIS bay module, CT on one side of the circuit breaker is also acceptable. SLD: | As per the project-specific requirements, the placement of the current transformer (CT) on one side of the breaker is acceptable. However, the Single Line Diagram (SLD) and layout indicate CTs on both sides of the breaker. Kindly confirm which configuration should be followed for both the bus coupler bay and feeder bays | Bidder to comply with the requirement of Cl. 2.2a. i) of Technical specification section project wherein it is clearly specified that The 5 Core CT shall be distributed on both sides of the breaker. |
|  | GIS BOQ | Sr. No. 137 MANDATORY SPARES- GIS CT 145KV GIS- CURRENT TRANSFORMER (5 CORES) WITH ASSOCIATED ENCLOSURE ANDPRIMARY CONDUCTOR COMPLETE IN ALL RESPECT: 1 EA | Please confirm the total quantity of current transformers required as spare ie. 1 EA =1 No CT. whether you need a breakdown for each type individually or a single total count. If it's single total count then kindly confirm which CT is required as a spare. | Since 5 core CT is distributed on either side of CB, 1 no.5 core CT specified in mandatory spares shall consist of 1 no. 02 core CT and 1 no. 3 core CT |
|  | Annexure - IV GTP Transformer | Claue No. 1.21 Maximum Permissible Losses of Transformers | Kindly clarify that the Maximum Permissible Losses of Transformers are on which KV class rating of LV side i.e either on 22KV or on 11KV | The maximum permissible losses specified are for 22kV LV |
| Volume-III Price Schedule |  |  |  |  |
|  | BOQ | 145KV, 1250A, 40KA SF6 TO AIR BUSHING(1-PHASE) ALONG WITH SUPPORTSTRUCTURE : 9 SET | Single phase bushing is not applicable for our type tested design. We shall provide three phase bushing 3 nos SF6 to Air bushing. | Kindly refer pt. no.-27 of clarification-02. |