| Slno | Clause Ref | Clause / Subject | Bidder’s Query | POWERGRID’s Reply |
| --- | --- | --- | --- | --- |
| Volume-II Technical Specifications |  |  |  |  |
|  | General | Surge Arrester data | Please note that all the Data regarding insulation coordination, etc, which can affect the LA parameters, shall be provided along with the NOA or within a month from the NOA for GIS LA finalization. Kindly accept the same. | noted |
|  | General | Additional LA requirement or changes in LA rating | Please note that no data is provided for the Insulation co-ordination study during the tender stage, and without the study, we cannot decide the additional LA quantity requirement or changes in rating. Therefore, if any additional LA or different rating LA is required during detailed engineering, it shall be supplied by the customer without any cost implication to HYOSUNG. Kindly accept the same. | Bidder to quote as per bidding document. |
|  | General | Requirement of additional Online monitoring system. | Please note that, as this substation is a digital substation, please let us know if there are any special requirements of online monitoring systems for GIS. | Portable partial discharge monitoring system is envisaged under present scope. Online monitoring of PD is not envisaged |
|  | General | LCC Size | We would like to inform you that, as this Puducherry substation is a digital substation, the MU/SGC, along with hardwiring for interlocking, is required to be placed in the LCC panel. Thus, for Puducherry GIS, LCCs of bigger sizes than the usual are considered. The usual LCC sizes are as follows: Bus coupler bay LCC - 1200mm x 850mm other bay LCC - 800mm X 850mm The sizes of LCC considered for Puducherry GIS are as follows: Bus coupler bay LCC - 1600mm x 850mm other bay LCC - 1600mm x 850mm Therefore, the cost of these LCCs is higher than that of a usual standard 145kV LCC. Kindly confirm the same. | LCC size shall be finalised during detailed engineering based on requirement |
|  | Annexure-II_Specific Requirement Rev10-part1 | Type Test validity For GIS LA and SF^ to Air bushing | Please note that from the reference clause, we are not able to understand whether the LA validity of 10 years is applicable to AIS or GIS type. However, for the Puducherry project, LA is part of indoor GIS, thus, we are considering the same TTR validity of 15 years for LA. Also, as SF6 to Air Bushings (GIS bushings) are required, the type test validity of the bushings shall be 15 years same as GIS for Puducherry GIS. Also, our understanding is in line with CEA guidelines. Kindly confirm our understanding. | Being GIS components, Validity of GIS LA and SF6 to Air bushing shall be considered as 15years as per TS |
|  | Model Technical Specification/ 400kV Transformer Specification (up to 400kV class) cl.3.14.3., Page no 7/185 Volume -II of Bidding Documents | Bidder / Manufacturer should have successfully carried out Dynamic Short Circuit Test on any rating of 132 kV or above voltage class transformer as on the originally scheduled date of bid opening and shall enclose the relevant Test Report / Certificate along with bid. In case bidder has not successfully tested 132 kV or above voltage class transformer for Dynamic Short Circuit Test, their bid shall be considered technically non-responsive. The offered transformer should comply the requirement of similarity clause specified in IS 2026 (PART 5) / IEC 60076-5 with respect to short circuit tested transformer. Further, design review of offered transformer shall be carried out based on the design of short circuit tested transformer. | Kindly note that we have Dynamic short circuit test report of 31.5 MVA 132/33 kV for PGCIL project conducted in year 2018 and 100% compliance on the above DSC test report as per similarity clause specified in IEC 60076-5 will not be met as per enclosed compliance report for your reference. Further the DSC on offered transformer is not envisaged as most of the parameters are similar. Kindly accept and confirm. | Bidder to quote as per bidding document. |