POWER GRID CORPORATION OF INDIA LTD.

(A Government of India Enterprise)

CONTENTS

| SECTION-I A | SCOPE |  |
| --- | --- | --- |
| SECTION-I B | GENERAL INFORMATION |  |
| SECTION-II | GENERAL TECHNICAL CONDITIONS |  |
| SECTION-III | SURVEY AND SOIL INVESTIGATION |  |
| SECTION-IV C | ERECTION AND STRINGING |  |
| SECTION-IV E | FOUNDATION (EMPLOYER DESIGN) |  |
| SECTION-V | GALVANISED STEEL EARTHWIRE |  |
| SECTION-VI A | HARDWARE FITTINGS & ACCESSORIES |  |
| SECTION-VII A | CONDUCTOR |  |
| SECTION-VIII | COMPOSITE LONGROD INSULATOR |  |
| SECTION-XI | DRAWINGS |  |
| SECTION-XII | FAQ |  |
| (This document is meant for the exclusive purpose of bidding against this specification and shall not be transferred, reproduced or otherwise used for purposes other than that for which it is specifically issued). |  |

SECTION-I A

SCOPE & TECHNICAL SPECS

| Clause No. | Description |  |
| --- | --- | --- |
| 1.0 | Scope |  |
| 2.0 | Transmission towers & line data |  |
| 3.0 | Different Sections to Technical Specification |  |
| 4.0 | Service Condition |  |

# TECHNICAL SPECIFICATIONS

# SECTION- I A

SCOPE

  - Scope

  - The following transmission lines are  included in the scope of the Contractor under  supply and erection packages:

  - Diversion of 400kV Vijayawada -Nellore  line  Ckt 1&2 at Locations543-548,553-557,635-639,737-740,744-749,764-768,(2) 400kV Vijayawada -Nellore  line  Ckt 3&4 at locs 640-643,794-798, (3) 400kV D/C quad Nellore PS -Gooty  line  at locs 123-127 and (4) 765 Kv D/c Nellore PS -Kurnool at locs 134-138    at KanigirI ,Obulayapalle ,Venkatapuram Prakasham  dist & Nellore Dist ,Andhrapradesh  which are infringing due to construction of Nadikudi -Srikalahasti Railway BG line being done by South Central Railways,Vijayawada.

This Specification covers the following scope of works:

          - Detailed survey including route alignment, profiling, tower spotting, optimization of tower locations, soil resistivity measurement & geotechnical investigation (including special foundation locations viz. pile/well foundation locations, whenever applicable & covered under BPS);

          - Check survey;

          - Fabrication and supply of all type of transmission line Towers as per Employer’s design/drawings including River crossing towers (wherever applicable) including fasteners, step bolts, hangers, D-shackles etc.;(POWERGRID SCOPE )

          - Supply of all types of tower accessories like phase plate, circuit plate (where ever applicable), number plate, pole plate (where ever applicable), danger plate, anti-climbing device, Bird guard, (where ever applicable);

          - Supply of

- Earth wire

- Hardware Fittings and accessories for Conductor, Earth wire &OPGW

- Conductor-ACSR Moose for 400kv lines  & ACSR  zeebra for 765 KV line

- Insulators—Composite long rod insulators

Classification of foundations for different type of towers and Casting of Foundations for tower structure footings as per Employer’s foundation design/ drawing;

          - Supply & Installation of Tower structure Earthing.

          - For transmission lines, to promote mechanization and safe working conditions, use of crane is being promoted.  Erection of towers by using crane (wherever feasible), tack welding of bolts and nuts including supply and application of zinc rich paint, fixing of insulator strings, stringing of conductors and earth wires along with all necessary line accessories. However, where usage of crane is not possible, erection of towers has to be carried out by conventional method i.e using Gin pole, Derrick, Centre mast etc. through usage of Power Operated Winch Machines. No tractor shall be allowed for tower structure erection.

          - Destringing & dismantling of existing  400kV Vijayawada -Nellore  line  Ckt 1&2 at Locations543-548,553-557,635-639,737-740,744-749,764-768 ,(2) 400kV Vijayawada -Nellore  line  Ckt 3&4 at locs 640-643,794-798, (3) 400kVd/c quad Nellore PS -Gooty  line  at locs 123-127 and (4) 765 Kv D/c Nellore NPS-Kurnool at locs 134-138 which are infringing for the construction of Nadikudi -Sikalahasti Railway BG line  by  SC Railways.

          - Stringing of Power line crossing section under Live Line Condition (where ever applicable & covered under BPS)

          - Painting of tower structures & supply and erection of span markers, obstruction lights(wherever applicable)for aviation requirements(as required)

          - Testing and commissioning of the erected transmission lines and

          - Other items not specifically mentioned in this Specification and/or BPS but are required for the successful commissioning of the transmission line, unless specifically excluded in the Specification.

  - The installation/stringing of GI Earth wire & OPGW  along with associated fittings & accessories shall be carried out by the contractor.

  - The scope of the package shall inter-alia include supervision of stringing works at site as per the approved procedure during the entire period of stringing.

  - Destringing/ Dismantling

    - The scope of works includes destringing of conductor,earthwire,opgw, removal of hardware fittings, insulators, conductor,earthwire accessories,etc and dismantling of tower from some sections of existing 400kV Vijayawada -Nellore  line  Ckt 1&2 at Locations 543-548,553-557,635-639,737-740,744-749,764-768 ,(2) 400kV Vijayawada -Nellore  line  Ckt 3&4 at locs 640-643,794-798, (3) 400kV D/C quad Nellore PS-Gooty  line  at locs 123-127 and (4) 765 Kv D/c Nellore PS -Kurnool at locs 134-138 and transporting of dismantled materials to designated  POWERGRID stores. The Employer shall arrange shut down of charged sections of existing transmission lines, if required, before carrying out destringing & dismantling works as per program finalized in co-ordination with site. Appropriate safety measures along with necessary safety tools and equipments to carry out destringing and stringing operations under the above conditions including mechanical/ structural safety of the towers shall be the responsibility of the contractor. The entire quantity of dismantled line materials viz. tower parts, conductor, earthwire, OPGW , hardware fittings, insulators and conductor, earthwire & OPGW   accessories removed from the existing line shall be transported to the designated POWERGRID stores by the contractor at his own cost. The Bidder shall submit his offer taking into consideration transportation cost of the dismantled material.

    - The contractor shall inspect the affected stretch of transmission lines and shall accordingly devise appropriate methodology/procedure of carrying out the destringing/restringing works during detailed engineering & execution stage in consultation with the site-in-charge.

    - The conductor removed from the existing line is envisaged for re-use/ utilization by the employer in other projects. Proper handling and safety of the conductor during de-stringing, storage at site, measurement of conductor lengths, rewinding on drums at site and safe transportation to employers designated  Substation stores along the transmission line shall be included in the scope of work.

    - The materials covered here under this specification shall be supplied complete in all respects, including all components, fittings and accessories which are necessary or are usual for their efficient performance and satisfactory maintenance under the various operating and atmospheric conditions.

  - Details of Transmission Line Routes and Terrain

The detailed survey shall be carried out using Total stations along the approved route alignment. As an alternative, the contractor may also use ALTM (Airborne Laser Terrain Modeling) techniques of equal or better accuracy for the detailed survey.

Quantity of detailed survey including route alignment, profiling, tower structure spotting, optimization of tower structure locations, soil resistivity measurement & geotechnical investigation etc. of lines have been indicated in the BPS.

    - Bidders may visit the line route to acquaint themselves with terrain conditions and associated details of the proposed transmission lines. For this purpose they are requested to contact the following address:

K.P RAO ,GM-STATION I/C

POWER GRID CORPORATION OF INDIA LTD.

Southern Region Transmission System-1

NELLORE SS,MANUBOLU,

Sri POTTI SRIRAMULU Dist. ,

Andhrapradesh

Qualification Requirements : Separate QR for transmission line diversion works

are prepared and it is enclosed.

- Transmission towers and Line data

  - General Description of the Tower:

    - The transmission towers covered under the package are of self-supporting hot dip galvanized lattice steel type, designed to carry the line conductors with necessary insulators, earth wire and all fittings under all loading conditions.  Outline diagram of towers are enclosed with the Specification.

    - The towers shall have mild steel or/and high tensile steel sections and shall be fully galvanized as specified in relevant clauses in section-IV. Bolts and nuts with spring washer are to be used for connections.

    - The towers are of the following types:

A)	Single Circuit*

B) 	Double Circuit*

C)	Multi Circuit*

D)	Special towers*

  - Classification of Towers

| Type of Tower | Deviation Limit | Typical Use |
| --- | --- | --- |
| A/DA/QA* | 0 – 2 deg. | To be used as Tangent tower. |
| B/DB/QB* | 0 deg. | To be used as Section Tower. |
|  | 0 - 15 deg. | - Angle towers with tension Insulator string. |
|  |  | - Also to be used for uplift force resulting from an uplift span up to 200m under broken wire conditions. |
|  |  | - Also to be used for Anti Cascading Condition. |
| C/DC/QC* | 0 deg. | To be used as Section Tower. |
|  | 15-30 deg. | - Angle tower with tension insulator string. |
|  |  | - Also to be used for uplift forces resulting from an uplift span up to 200m under broken wire condition. |
|  |  | - Also to be used for anti-cascading condition. |
| D45/DD45/ QD45* | 30 - 45 deg. | - Angle tower with tension insulator string. |
|  |  | - Also to be used for uplift forces resulting from an uplift span up to 300m under broken wire condition. |
| D60/DD60/ QD60* | 45 - 60 deg. | - Angle tower with tension insulator string. |
|  |  | - Also to be used for uplift forces resulting from an uplift span up to 300m under broken wire condition. |
|  |  | Dead end with 0 deg to 15 deg deviation both on line side and sub-station side (slack span) |
|  | 0 deg. | - Complete Dead end |
|  |  | - For river crossing anchoring with longer wind span. |

1.	The above towers can also be used for longer span with smaller angle of 	deviations without infringement of ground clearance.

2.  	The above table provides indicative classification of Towers. Tower spotting data for various towers to be used in the transmission lines under the specific package shall be given to the contractor during execution stage.

Electrical Clearances:

    - Ground Clearances:

The minimum ground clearance from the bottom conductor shall not be less than *18000 mm for 765 KV, *18000mm for +800kV HVDC, *12500mm for +500kV HVDC, *8840 mm for 400KV, *7015 mm for 220KV and *6100 mm for 132KV lines at the maximum sag conditions i.e. at max temperature as indicated in tower spotting data and still air.

a) 	An allowance of 150mm shall be provided to account for errors in stringing.

b) 	Conductor creep shall be compensated by over tensioning the conductor at a temperature as mentioned in section IV of this specification.

3.4	Details of Line Materials shall be as per the  following:-

Details of conductor & Earthwire/

| 1 | Conductor | 2nos ACSR Moose conductor per phase with sub-conductor spacing of 450 mm for 400 KV line Vijayawada-Nellore CKT 1,2 & 3,4 & 4 Nos ACSR Moose for each phase 400 KV Nellore-Gooty quad D/C line , 6Nos per phase ACSR Zeebra for 765 kv Nellore PS -Kurnool D/C line. |
| --- | --- | --- |
| 2 | Earthwire &OPGW | One ACSR Earthwire & one no OPGW with mechanical & electrical properties equivalent to existing E/W may be used as indicated in Section-IA. |

        - Details of Insulator Strings with composite long rod insulators

insulator strings with composite long rod insulators shall be used in the transmission line covered under the package. All other requirement of composite long rod insulators and insulator strings shall be as per Section-VIII of this specification shall be within the limits as  specified in the drawing.

- Different Sections to Technical Specification

  - For the purpose of present scope of work, technical specification shall consist of following parts and they should be read in conjunction with each other: -

| Sl. No. | Section Number | Name of Section | Rev No. |
| --- | --- | --- | --- |
| 1 | Section-IA | Scope | Rev-6 (Feb’2023) |
| 2 | Section-IB | General Information | Rev-7 (May’2023) |
| 3 | Section-II | General Technical Conditions | Rev-2 (Feb’2022) |
| 4 | Section-III | Survey and Soil Investigation | Rev-3 (Mar’2023) |
| 5 | Section-IVB | Tower Testing | Rev-2 (Mar’2023) |
| 6 | Section-IVC | Fabrication, Erection and Stringing | Rev-6 (Apr’2023) |
| 7 | Section-IV E | Foundation (Employer Design) | Rev-4 (Mar’2023) |
| 8 | Section-V | Galvanised Steel Earthwire | Rev-0 (June’2021) |
| 9 | Section-VIA | Hardware Fittings and Accessories for Conductor & Earthwire | Rev-2 (Jan’2022) |
| 10 | Section-VIIA | Conductor | Rev-2 (Jan’2022) |
| 11 | Section-VIII | Composite Longrod Insulators | Rev-2 (Jan’2022) |
| 12 | Section-XI | Drawings | Rev-0 (June’2021) |
| 13 | Section-XII | FAQ | Rev 0 (June’2021) |

(to be modified as applicable for the package)

  - In case of any discrepancy between Section-IA (Scope) and Section-IB (General Information) and other technical specifications on scope of works, Section-IA (Scope) shall prevail over all other sections.

  - In case of any discrepancy between Section-IB (General Information) and individual sections for various equipment, requirement of individual equipment section shall prevail.

- Service Conditions:

Equipment/material to be supplied against this specification shall be suitable for satisfactory continuous operation under tropical conditions as specified below:

| Maximum ambient temperature (oC) | 50* |
| --- | --- |
| Minimum ambient temperature (oC) | 0* |
| Relative humidity (% range) | 10-100** |
| Wind zone (as per NBC) | 1/2/3/4/5/6* |
| Terrain Category | 1/2/3* |
| Maximum wind velocity (m/sec.) | 33/39/44/47/50/55 |
| Maximum altitude above mean sea level (Meters) | Below 1000m* |
| Isokeraunic level (days/years) | 60* |