## PGCIL_KPS-I & 3Pre-bid Clarific
Clarification-III dated 26.11.2024 to the Bidding Documents for STATCOM Package - ST-01T for (a) STATCOM Station at Khavda Pooling Station 1 (KPS1) and (b) STATCOM Station at Khavda Pooling Station 3 (KPS3) associated with “Provision of Dynamic Reactive Compensation at Khavda Pooling Station 1 (KPS1) and Khavda Pooling Station 3 (KPS3)”; Spec. No: CC/T/W-STAT/DOM/A06/24/14931
Sl.No. | Name of the Document | Clause No. and Existing Provision | Clarification Required | POWERGRID Reply
1 | 1.0 Sections_Project_Final | C.9.7 Software simulation & Model Ammendment c) Harmonic Model. Bidder should provide a harmonic model of STATCOM in PSCAD software. The model detail should be appropriate and complete for the harmonic distortion evaluation of the STATCOM system. All appropriate control features for such analysis will be modeled, and necessary documentation on the theory and use of model should be provided. The harmonic model shall be benchmarked against actual performance (or as per tests) Both UDM (PSCAD and PSS/E) and Generic model (PSSE) shall be provided by OEMs to CEA/CTU/GRID-INDIA without any NDA (Non-Disclosure Agreement) | Harmonic model of STATCOM is not possible to be submitted in PSCAD. As per specification the harmonic calculation and harmonic distortion evaluation has been done as per CIGRE Publication 139. The results of the calculation showing the THD within the limits are already decribed in details in the basic design report. Please confirm bidder understanding. | Bidder's understanding is generally in order.