| Sl. No. | # Volume/ Section/ Description | # Clauses | # Bidder’s Query | # POWERGRID Reply |  |
| --- | --- | --- | --- | --- | --- |
| Volume-I: Condition of Contracts |  |  |  |  |  |
|  | Annexure-A (BDS), Route-4, Qualification Requirements | Route-4 1.4 In case, the bidder is not a GIS manufacturer, he shall also be considered provided: - The bidder must have erected and commissioned at least two (02) nos. GIS circuit breaker bays of 220kV or above voltage class in one (01) new GIS substation or switchyard during last seven (07) years and these bays must be in satisfactory operation# for at least two (02) years as on the originally scheduled date of bid opening mentioned above. - The GIS must be offered from Indian manufacturer, who meets the requirement mentioned at Route-1 or Route-2 or Route-3 above. - A legally enforceable undertaking (jointly with the GIS Manufacturer) (as per enclosed format in Section-VI, Volume-I of bidding document) to guarantee quality, timely supply, performance and warranty obligations as specified for the equipment(s) is submitted along with the bid stating that GIS Manufacturer shall furnish performance guarantee for an amount of two (2) % of the total contract price. This performance guarantee shall be in addition to the Contract Performance security to be submitted by the Bidder. | We understand that bidder who are qualifying through the Qualification requirement clause NO. 1.4(iii), ROUTE-4, OF ANNEXURE-A (BDS) need to obtain JDU only for 220 kV GIS Manufacture. Kindly confirm | Provisions of the Bidding Documents are amply clear. |  |
|  |  |  | We understand that bidder who are qualifying through the Qualification requirement clause NO. 1.4 (iii), ROUTE-4, OF ANNEXURE-A (BDS) can obtain JDU from multiple manufacturers and similarly, eligible 220 KV GIS manufacturer can support to multiple bidders, during execution stage bidder can finalize GIS manufacture to meeting their timeline and suitability. Kindly confirm. | The Bidder qualifying through Route-4 may propose more than one GIS manufacturer meeting the specified Qualification Requirements in their bid. Further, the Bidder has to submit the JDU with each of the proposed manufacturer(s) as per Clause 1.4(iii) of Annexure-A(BDS). However, one of the GIS manufacturers who is determined to be qualified as per the Qualification Requirements (QR) shall be suitably tied up with the Bidder qualifying through Route-4 prior to award of Contract. |  |
|  |  |  | We understand that bidder can propose separate make of 220 kV & 33 kV GIS rating. Kindly confirm. | Provisions of the Bidding Documents are amply clear. |  |
|  |  |  | We understand that bidder can submit the 3% additional PBG requirement against 220KV GIS on behalf of manufacturer. Kindly confirm. | The additional performance guarantee indicated in route-4 (1.4) shall be two (2) % of the total contract price from GIS Manufacturer. This performance guarantee shall be in addition to the Contract Performance security to be submitted by the bidder. Provisions of the Bidding Documents are amply clear. |  |
|  | ITB Clause 9.3 (c), ITB, Section-II | Declaration for anticipated change in legal structure/ ownership, if any. | Kindly share the blank format regarding declaration. | Provisions of the Bidding Documents are amply clear. |  |
|  | GCC Clause 6.1, GCC, Section-IV | 6. Employer’s Responsibilities 6.1 The Employer shall ensure the accuracy of all information and/or data to be supplied by the Employer as described in the corresponding Appendix - 6 (Scope of Works and Supply by the Employer) to the Contract, except when otherwise expressly stated in the Contract. ……………. | Please confirm on availability of land by Employer for construction of stores by contractor. | Provisions of the Bidding Documents are amply clear. Further, Bidder is also advised to refer Clause 6 of GCC of the Bidding Documents in this regard. |  |
|  |  |  | We presume that space shall be provided at site for storage & site office construction at free of cost. Please confirm. |  |  |
|  | GCC Clause 6.2, GCC, Section-IV | The Employer shall be responsible for acquiring and providing legal and physical possession of the Site and access thereto, and for providing possession of and access to all other areas reasonably required for the proper execution of the Contract, including all requisite rights of way, as specified in the corresponding Appendix – 6 (Scope of Works and Supply by the Employer) to the Contract Agreement. The Employer shall give full possession of and accord all rights of access thereto on or before the date(s) specified in that Appendix. | Please confirm upon availability of encumbrance free land with award of LOA/NOA. | Provisions of the Bidding Documents are amply clear. Bidder is advised to kindly refer GCC Clause 6.2 in this regard |  |
|  | GCC Clause 6.3, GCC, Section-IV | The Employer shall acquire and pay for all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the country where the Site is located which such authorities or undertakings require the Employer to obtain them in the Employer's name, are necessary for the execution of the Contract (they include those required for the performance by both the Contractor and the Employer of their respective obligations under the Contract), including those specified in Appendix 6 (Scope of Works and Supply by the Employer) to the Contract Agreement. | Please provide clarity on liability of obtaining Environment clearance for the Project. | Provisions of the Bidding Documents are amply clear. Bidder may please refer Clause 5, 6 & 18 of GCC of the Bidding Documents. |  |
|  | GCC Clause 6, GCC, Section-IV and General |  | We understand that trees cutting and clearance if any is excluded from bid scope. Please confirm. | The provisions of bidding documents are amply clear. Further, Bidder is also advised to refer Clause 5 & 6 of GCC of the Bidding Documents in this regard. |  |
|  | GCC Clause 6, GCC, Section-IV and General | Approach road to proposed site | Any strengthening / modification required in the existing culverts, road, bridges etc. for transportation of material / Items / equipment up to proposed site shall be carried out by the PGCIL. Please confirm. | The provisions of bidding documents are amply clear. Further, Bidder is also advised to refer Clause 5 & 6 of GCC of the Bidding Documents in this regard. |  |
|  | GCC Clause 6, GCC, Section-IV and General | Schedule 3 >> Erection BOQ Sl. NO. 102 >> Blasting | We presume that permissions for blasting will be arranged by employer. Please confirm. | The provisions of bidding documents are amply clear. Further, Bidder is also advised to refer Clause 5 & 6 of GCC of the Bidding Documents in this regard. |  |
|  | General and GCC Clause 6, GCC, Section-IV and |  | Construction Power & Water Kindly confirm availability of the sources for 415V constructional power and water near the boundary of proposed site. | The provisions of bidding documents are amply clear. Further, Bidder is also advised to refer Clause 5 & 6 of GCC of the Bidding Documents in this regard. |  |
|  | GCC Clause 9.3.3, SCC, Section-V | Reduction in the security pro rata to the Contract Price of any part of the Facilities is not admissible. However, if the Defects Liability Period has been extended on any part of the Facilities pursuant to GCC Sub-Clause 22.8 hereof, the Contractor shall issue an additional security in an amount proportionate to the Contract Price of that part. The security shall be returned to the Contractor immediately after its expiration, provided, however, that if the Contractor pursuant to GCC Sub-Clause 22, is liable for an extended warranty obligation, the performance security shall be reduced to three percent (3%) of the value of the component covered by the extended warranty. | Please allow for proportionate reduction of PBG based on completion of facilities. | The provisions of the Bidding Documents shall remain unchanged. |  |
|  | GCC Clause 22.8.1, GCC, Section-IV | 22.8.1 At the end of the Defect Liability Period, the Contractor's Liability ceases except for latent defects. The Contractor's liability for latent defects warranty shall be limited to period of ten (10) years from the end of Defect Liability Period. For the purpose of this clause, the latent defects shall be the defects inherently lying within the material or arising out of design deficiency, which do not manifest themselves during the Defect Liability Period defined in this GCC Clause 22, but later. | We understand that latent defect warranty of GIS is not required, kindly confirm our understanding. | Provisions of the Bidding Documents are amply clear. |  |
|  | GCC Clause 22.8.1, SCC, Section-V | Supplementing Sub-Clause GCC 22.8.1 The Contractor's liability for latent defects warranty for 132kV/ 145kV/220KV/245kV/400kV/765kV Capacitive Voltage Transformer/ Current Transformer/Circuit Breaker/Transformer shall be limited to period of five (05) years from the end of Defect Liability Period. | We request you to delete this clause. |  |  |
|  | GCC Clause 31.1, GCC, Section-IV | If, after the date seven (07) days prior to the date of Bid Opening, any law, regulation, ordinance, order or by-law having the force of law is enacted, promulgated, abrogated or changed in India (which shall be deemed to include any change in interpretation or application by the competent authorities) that subsequently affects the costs and expenses of the Contractor and/or the Time for Completion, the Contract Price shall be correspondingly increased or decreased, and/or the Time for Completion shall be reasonably adjusted to the extent that the Contractor has thereby been affected in the performance of any of its obligations under the Contract. These adjustments shall be applicable for all transactions between the Employer and the Contractor for supply of goods and services under the Contract but shall not be applicable on procurement of raw materials, intermediary components etc. by the Contractor for which the Employer shall be the sole judge. Notwithstanding the foregoing, such additional or reduced costs shall not be separately paid or credited if the same has already been accounted for in the price adjustment provisions where applicable, in accordance with the Appendix-2 to the Contract Agreement. | We understand that, if any new law or regulation imposed social responsibility on Contractor which hamper the progress of work with financial burden out of Contract, the same shall be borne by Employer. Please Confirm. | Provisions of the Bidding Documents are amply clear. |  |
|  | GCC Clause 32.1, GCC, Section-IV | “Force Majeure” shall mean any event beyond the reasonable control of the Employer or of the Contractor, as the case may be, and which is unavoidable notwithstanding the reasonable care of the party affected, and shall include, without limitation, the following: (a) war, hostilities or warlike operations (whether war be declared or not), invasion, act of foreign enemy and civil war, (b) rebellion, revolution, insurrection, mutiny, usurpation of government, conspiracy, riot and civil commotion, (c) earthquake, landslide, volcanic activity, flood or cyclone, or other inclement weather condition, nuclear and pressure waves or other natural or physical disaster, | We understand that Epidemics/Pandemic such as Novel Coronavirus (e.g. COVID 19) etc., Terrorism, Bandhs, Infrastructure failures and Shortage of certain components required for the performance of the scope of work are covered under force majeure. Please Confirm. | “Force Majeure” shall be governed by the provisions stipulated in the Bidding Documents which are amply clear. |  |
|  | GCC Clause 34.1, SCC, Section-V | The Time(s) for Completion specified in the SCC shall be extended if the Contractor is delayed or impeded in the performance of any of its obligations under the Contract by reason of any of the following: (a) any Change in the Facilities as provided in GCC Clause 33 (b) any occurrence of Force Majeure as provided in GCC Clause 32 (c) any suspension order given by the Employer under GCC Clause 35 hereof or reduction in the rate of progress pursuant to GCC Sub-Clause 35.2 or (d) any changes in laws and regulations as provided in GCC Clause 31 or (e) any other matter specifically mentioned in the Contract by such period as shall be fair and reasonable in all the circumstances and as shall fairly reflect the delay or impediment sustained by the Contractor. | Please include the below mentioned provision in stated clause: (f) Any delay caused due to delay/failure in fulfilment of Employer's obligations. The contractor is entitled for extension of time along with reimbursement of additional cost incurred. | The provisions of the Bidding Documents shall remain unchanged. |  |
|  | Clause 1.1 & 1.4 in Appendix-1 (TERMS AND PROCEDURES OF PAYMENT), Sample Forms and Procedures, Section-VI | - Supply of Goods Portion: (I) FOR SUBSTATION PORTION: C Final Payment Balance 10% (Ten percent) of the Ex-works price component of Main Equipment/Materials (excluding Mandatory Spares) shall be paid as per the following: - 5% (Five percent) on Successful completion of erection, testing and commissioning of individual bays. - 5% (Five percent) on proof of submission of required number of reproducibles, O&M Manuals, approved drawings, data sheets, test report, pamphlets and manuals of mandatory spares, maintenance & testing equipment and on successful completion of erection, testing and commissioning of all bays and issuance of Taking Over Certificate. However, in case of delay in testing and commissioning & issuance of taking over certificate by Employer beyond six (6) months from the date of receipt of equipment at site, the last 10% of Ex-Works price of respective equipment shall be paid after issuance of a certificate by Employer’s representative that the equipment have been received in good condition and on submission of a bank guarantee of equivalent amount, which shall be kept valid initially for a period of twelve (12) months or until three (3) months after the expected date of commissioning (in case it is possible to anticipate the same), whichever is earlier, provided all other conditions as per above are complied with by the Contractor. If the commissioning does not take place within the validity period of BG, the validity of BG shall be extended from time to time. The bank guarantee shall, however, be released within one month of successful commissioning of the respective equipment by the Employer. ………………… | Please rephrase this clause as under: In case of delay in testing and commissioning & issuance of taking over certificate by Employer beyond One (1) month from the date of receipt of equipment at site, the last 10% of Ex-Works price of respective equipment shall be paid after issuance of a certificate by Employer’s representative that the equipment have been received in good condition and on submission of a bank guarantee of equivalent amount, which shall be kept valid initially for a period of twelve (12) months or until three (3) months after the expected date of commissioning (in case it is possible to anticipate the same), whichever is earlier, provided all other conditions as per above are complied with by the Contractor. If the commissioning does not take place within the validity period of BG, the validity of BG shall be extended from time to time. The bank guarantee shall, however, be released within one month of successful commissioning of the respective equipment by the Employer." | The provisions of the Bidding Documents shall remain unchanged. |  |
|  |  |  | Please include provision of interest on delayed payments by Employer @ SBI PLR for the prevailing year. | The provisions of the Bidding Documents shall remain unchanged. |  |
|  | General | TCS | W.e.f. 01/10/2020, TCS is implemented. The seller is required to collect the TCS from buyer TCS @ .1% of sales consideration on sale of goods when Seller receives amount Rs 50 lakh from any single buyer in current financial year. In current tender, bidder will have to collect TCS on sale of goods @ 0.1% on value of goods excluding GST. Bidder will issue certificate to client and the same will be subject to credit to client However on service invoice no TCS will be applicable. Please confirm our understanding. |  | Payment of taxes and Duties shall be done as per the provisions of Bidding Documents / applicable laws/guidelines of GoI. The issue raised by Bidder pertains to collection of TCS under Income Tax Act. The deduction of TDS by Employer or TCS by the Contractor, as applicable, on the transactions shall be made in accordance with the applicable laws/guidelines of GoI in vogue. |
|  | Clause 39 of GCC (SCC), Vol-I of the Bidding Documents | 39. Arbitration 39.1 All disputes or differences in respect of which the decision, if any, of the Project Manager and/or the Head of the Implementing Authority has not become final or binding as aforesaid shall be settled by arbitration in the manner provided herein below: 39.2 The arbitration shall be conducted by a sole arbitrator in case the amount of claim is less than Rs. 25 Crore and by three member arbitral tribunal in case the amount of claim is greater than Rs. 25 Crore. | We request for settlement of disputes arising out of contract or in connection with the contract, to be settled with panel of three arbitrators, one from each party and a presiding arbitrator. Also the claim amount shall not be the basis to decide the number of arbitrators. |  | The provisions of the Bidding Documents are amply clear and shall remain unchanged. |
| Volume-II: Technical Specifications |  |  |  |  |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 2.3 | The equipment offered shall be protected against all types of voltage surges and any equipment necessary to satisfy this requirement shall deemed to be included. | We understand that surge arrestors are required to cater the requirement and are of AIS type. | In addition to 216kV AIS type LA specified in BPS if Bidder may require to provide additional AIS or GIS type LA to meet the requirement stipulated in the referred clause and clause no. 11.2 of Section-GIS (Rev-05A), the cost of the same shall be built up by bidder under GIS equipment itself. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 5.8. | The material and thickness of the enclosures shall be such as to withstand an internal flash over without burns through for a period of 300 ms at rated short time withstand current. The material shall be such that it has no effect of environment as well as from the by-products of SF6 breakdown under arcing condition. This shall be validated with Type Test. | The Value shall be in line with the requirement of IEC 62271-203. Request a concurrence on the same. | Requirement of Technical Specification shall prevail. Bidder shall quote accordingly. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 5.9 | Inspection windows (View Ports) shall be provided for Disconnect Switch and both type of earth switches i.e. Maintenance and fast operating. | Inspection windows shall be provided for Disconnector enclosures. Provision of Observation windows for Earth switches is not envisaged as such. | Requirement of Technical Specification shall prevail. Bidder shall quote accordingly. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 5.21. | The GIS shall be designed, so as to take care of the VFT over voltages generated as a result of pre-strikes and re-strikes during isolator operation. Maximum VFT over voltages peak shall not be higher than rated lightning impulse withstand voltage (LIWV) of the equipment. Necessary measures shall be under taken by GIS manufacture to restrict maximum VFT over voltages lower than the LIWV. Manufacturer shall submit the study report of VFTO generated for GIS installation. | For a 220 kV GIS system, we do not envisage VFTO studies. Hence, the same shall be excluded from GIS OEM scope of supply. | VFTO study report need not be submitted for present scope of 220kV GIS System. However, GIS manufacturer shall ensure compliance of other requirements of Cl. 5.21 of Section: GIS, Rev-5A. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 5.26 | The switchgear shall have provision for connection with ground mat risers through copper connections. This provision shall consist of grounding pads to be connected to the ground mat riser in the vicinity of the equipment. | Earthing details shall be provided during detailed engineering stage. However, supply of earthing materials shall be excluded from GIS OEM scope of supply. | The description referred to corresponds to Cl. 5.25. However, in response to the query, requirement of Technical Specification shall prevail. Further refer to Cl. 5.39.2 of Section: GIS, Rev.5A for further clarity. Bidder shall quote accordingly. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 5.28 | In addition to above suitable portable scissor lift shall be provided for access of distant portion of GIS installation. | We do not envisage this requirement. Walkways if required and portable ladder shall be provided. | The description referred to corresponds to Cl. 5.27. However, in response to the query, requirement of Technical Specification shall prevail. Bidder shall quote accordingly. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 5.32. | ii) Any other alarm necessary to indicate deterioration of the gas insulating system. | Not Applicable for the offered GIS | The description referred to corresponds to Cl. 5.31. However, in response to the query: confirmed. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 5.39 | Grounding | Earthing details shall be provided during detailed engineering stage. However, supply of earthing materials shall be excluded from GIS OEM scope of supply. | Requirement of Technical Specification shall prevail. Further refer to Cl. 5.39.2 of Section: GIS, Rev.5A for further clarity. Bidder shall quote accordingly. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 5.42. Gas Insulated Bus (GIB) layout : | The horizontal clearance between GIB and GIS building /any other building wall shall be preferably three (3) meters. | The space/area utilization for such a configuration is very high and request customer to accept the standard spacing's between circuits considering the fact that the Bus-ducts are passive and requires almost no maintenance. Request PGCIL to accept the same. | The description referred to corresponds to Cl. 5.41. However, in response to the query, requirement of Technical Specification shall prevail. Bidder shall quote accordingly. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 5.39.3 | The enclosure of the GIS may be grounded at several points so that there shall be grounded cage around all the live parts. A minimum of two nos. of grounding connections should be provided for each of circuit breaker, cable terminals, surge arrestors, earth switches and at each end of the bus bars. The grounding continuity between each enclosure shall be effectively interconnected externally with Copper /Aluminum bonds of suitable size to bridge the flanges. | The GIS design is such, the proper bonding is ensured by direct metal to metal flange connections and 2 nos. earthing provisions given for grounding. | Requirement of Technical Specification shall prevail. Bidder shall quote accordingly. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 5.45. | xviii. Study report of VFTO generated for GIS installation for 400 kV and above. | For an 220 kV GIS system, we do not envisage VFTO studies. Hence, the same shall be excluded from GIS OEM scope of supply. | The description referred to corresponds to Cl. 5.44. However, in response to the query, VFTO study report need not be submitted for present scope of 220kV GIS System. However, GIS manufacturer shall ensure compliance of other requirements of Cl. 5.21 of Section: GIS, Rev-5A. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 6.6.7 | Provisions shall be made for attaching an operational analyzer to record travel, speed and making measurement of operating timings etc. after installation at site. The contractor shall supply three set of transducer for each substation covered under the scope. | The supply of transducers is excluded GIS OEM Scope of supply | Requirement of Technical Specification shall prevail. Bidder shall quote accordingly. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 6.6.8. | Circuit Breaker shall be supplied with auxiliary switch having additional 8 NO( normally open) and 8 NC ( normally closed) contacts for future use over and above those required for switchgear interlocking and other control and protection function. These spare NO and NC contacts shall be wired upto the local control cubicle. | Auxiliary switches are of standard design/size suitably designed for the available space. Hence the required additional 8 NO (Normally open) and 8 NC (normally closed) contacts shall be provided to customer through contact multiplication relays at LCC. | Noted. However, these contact multiplication relays shall be energized directly through Auxiliary Switches of CB. Detail shall be finalized during detailed engineering. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 6.7.2. Control | The breaker shall normally be operated by remote electrical control. Electrical tripping shall be performed by shunt trip coils. However, provisions shall be made for local electrical control. For this purpose a local/remote selector switch and close and trip control switch/push buttons shall be provided in the breaker control cabinet. | As per our standard practice the Local/Remote switches will be provided in the Local Control Cubicle (LCC). | Noted. However, detail shall be finalized during detailed engineering meeting the requirements of Technical Specifications. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 7.2.5 | For motor-operated disconnect switches, the control should be electrically and/or mechanically uncoupled from the drive shaft when the switch is operated manually to prevent coincident power operation of the switch and the drive mechanism(s). | Only electrical inter-locks possible between DS & ES. We do not envisage providing any mechanical interlocks. Request customer to kindly accept the same. | Acceptable in case other requirement of Technical Specifications are fulfilled for offered design of GIS. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 7.2.10 | Each disconnector shall be supplied with auxiliary switch having additional 8 NO (Normally Open) and 8 NC (Normally Closed) contacts for future use over and above those required for switchgear interlocking and automation purposes. These spare NO and NC contacts shall be wired up to the local control cabinet. | Auxiliary switches are of standard design/size suitably designed for the available space. Hence the required additional 8 NO (Normally open) and 8 NC (normally closed) contacts shall be provided to customer through contact multiplication relays at LCC. | Noted. However, these contact multiplication relays shall be energized directly through Auxiliary Switches of Disconnector. Detail shall be finalized during detailed engineering. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 7.2.13 | The disconnectors and safety grounding switches shall have a mechanical and electrical inter-locks to prevent closing of the grounding switches when isolator switches are in the closed position and to prevent closing of the disconnectors when the grounding switch is in the closed position. Integrally mounted lock when provided shall be equipped with a unique key for such three phase group. Master key is not permitted. | The disconnectors and the safety grounding switches are separate modules in GIS design and shall have only electrical inter-locks between them. However the required padlocking facility shall be provided for the manual interlocking for additional protection. | Acceptable in case other requirements of Technical Specifications are fulfilled for offered design of GIS. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 8.3 | Each safety grounding switch shall be electrically interlocked with its associated disconnectors and circuit breaker such that it can only be closed if both the circuit breaker and disconnectors are in open position. Safety grounding switch shall also be mechanically key interlocked with its associated disconnectors. | The disconnectors and the safety grounding switches are separate modules in GIS design and shall have only electrical inter-locks between them. However the required padlocking facility shall be provided for the manual interlocking for additional protection. | The description referred to corresponds to Cl. 8.2. However, in response to the query, Acceptable in case other requirements of Technical Specifications are fulfilled for offered design of GIS. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 8.6 | Each ground switch shall be fitted with auxiliary switches having 4 NO (Normally Open) and 4 NC (Normally Closed) contacts for use by others over and above those required for local interlocking and position indication purposes. | Auxiliary switches are of standard design/size suitably designed for the available space. Hence the required additional 4 NO (Normally open) and 4 NC (normally closed) contacts shall be provided to customer through contact multiplication relays at LCC. | Noted. However, these contact multiplication relays shall be energized directly through Auxiliary Switches of Disconnector. Detail shall be finalized during detailed engineering. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 11.2. | Insulation co-ordination and selection of surge arrestor: | The same shall be excluded from GIS OEM scope of supply. | Insulation coordination and selection of Surge Arrestors is included under present scope of contract. Bidder to quote as per requirement of Technical Specification. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 15.2.1 | It shall comprise structural frames completely enclosed with specially selected smooth finished, cold rolled sheet steel of thickness not less than 3 mm for weight bearing members of the panels such as base frame, front sheet and door frames, and 2.0mm for sides, door, top and bottom portions. | As per the standard practice, for the weight bearing members a sheet thickness of 2.5 mm is more than sufficient and as a GIS manufacturer we recommended the same and for non weight bearing members the same is 2 mm thick. We request customer to kindly confirm the same. | Requirement of Technical Specification shall prevail. Bidder shall quote accordingly. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 22 | All transport packages containing critical units viz Circuit breakers and Voltage transformers shall be provided with sufficient number of impact recorders (on returnable basis) during transportation to measure the magnitude and duration of the impact in all three directions. | VTs being an critical equipment only impact recorders shall be provided for VTs. We request customer to kindly accept the same. | Requirement of Technical Specification shall prevail. Bidder shall quote accordingly. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 23.9. | Cost of the raised platform for temporary storage is deemed to be included in overall cost. The raised platform needs to be made ready before arrival of GIS equipment at site. The contractor may use the available storage areas at site with permission of site in charge. | The Cost of any specific requirements with regards to Platform or civil works are excluded from GIS OEM Scope. | Requirement of Technical Specification shall prevail. Bidder shall quote accordingly. |  |
|  | Technical specification for GIS (GIS-REV 5A) Cl. 27 | TESTING & MAINTENACE EQUIPMENT SF6 Gas leakage detector. Gas filling and evacuating plant : (Gas Processing unit) SF6 gas analyzer: Portable Partial Discharge (PD) monitoring system (Shall generally applicable for 220kV&132 kV) Online Partial Discharge Monitoring System (Applicable for 765kV& 400 kV GIS) | The same shall be excluded from GIS OEM scope of supply. | Bidder shall quote as per requirement of bidding documents. |  |
|  | General Arrangement Electrical Layout | Dimension of GIS Hall | Kindly specify the space available for GIS in the allocated hall | Design of GIS Building is in scope of Bidder. Refer to Cl. 3.1 (III) ii. c) of Section: Project. Accordingly, size of GIS Hall shall be decided during detailed engineering. Bidder shall quote accordingly. |  |
|  | General Arrangement Electrical Layout | Requirement of Wall Mount Bushings | Kindly specify the mechanical Load anticipated at the terminal load points of the SF6/Air Bushings | In addition to requirement of Cl. 12.3 of Technical Specification Section: GIS, Rev.5A Mechanical load of SF6/Air Bushing shall be designed including the effect of bushing self-load & Snow load. However, minimum cantilever strength shall however be as per Annexure-6 of Technical Specification Section: GIS, Rev.5A. Bidder shall quote accordingly. |  |
|  | Price_Schedule | Air Bushing Quantity for 220kV GIS | There is no item mentioned in BPS for Air Bushing for 220kV GIS. Please confirm whether this item, is required or not and specify quantity if required. | SF6 to Air Bushing (Wall Bushing) is included in the BPS item for respective 220kV GIS module. Refer Cl. II. ii) vii & Cl. II. iii) v. of Annexure-VIII to Section: Project. |  |
|  | 1.0 Section-Project (Part-A) V2 R0 | Technical Specifications | Technical Specifications for below mentioned items are not in Tender documents – - Section Switchgear_ISO - Testing & Maintenance equipments - EOT Crane - Scissor Lift Without Technical Specification of the above-mentioned items, we are unable to get offer from manufacturers/OEMs. Please provide the same. | - Please refer Errata No-02. - Testing & Maintenance equipment’s: Refer Cl. 27 of Technical Specification Section: GIS, Rev.5A - EOT Crane: Refer Cl. 17 of Technical Specification Section: GIS, Rev.5A - Scissor Lift: As per requirement and shall be decided during detailed engineering. Bidder shall quote accordingly. |  |
|  | 33kV Bay control unit |  | We understand bidder may opt BCU or BCPU for each bay or one BCU/BCPU for two bays of 33kV Switchgear. Please confirm. | BCPU is not envisaged in 33 kV system for subject package. As per Cl. 3.1 (I) (B) f) of TS, Section: Project, BCU based Substation Automation of 33kV bays is envisaged under present scope. Bidder shall quote accordingly. |  |
|  | 33kV Bay control unit |  | We understand bidder may offer 33kV BCU/BCPU mounted on 33kV switchgear panels or on separate panel in SAS room or in 33kV switchgear room. Please confirm | BCPU is not envisaged in 33 kV system for subject package. Bidder may provide BCU in 33 kV Switchgear panel if there is no space constraint or in separate panels in the 33 kV switchgear room. Bidder shall quote accordingly. |  |
|  | Creepage |  | We understand as per tender documents required creepage is 25mm/kV. Please confirm | Confirmed. |  |
|  | Remote end |  | We understand there is no supply services scope at remote ends except DPC. Please confirm | Bidder to quote as per requirements of Bidding documents. |  |
|  | Remote end |  | Please confirm, there is no interface/integration scope is envisaged under present scope of bidder. | Bidder to quote as per requirements of Bidding documents. |  |
|  | Remote end DPC |  | We understand DPC Re-erected or placed at existing panel only. No control power wiring or connection is considered at 220kV line connecting subststaion. Please confirm. | DPC dismantled at Drass S/S shall be re-erected at Nilgrar S/S. Further, details of placement & integration of new DPC panel to be supplied at Drass S/S shall be finalized during engineering. |  |
|  | Dispatch centers |  | Please confirm, there is no interface/integration/supply/service scope is envisaged under present scope of bidder. | Bidder shall quote as per requirements of Bidding documents. |  |
|  | Earthing |  | Please share earth resistivity value for proposed scope site. | As per Cl.3.1.(I) (B) r) of Section: Project; design of Main Earthmat is under Bidder’s scope. Therefore, measurement of soil resistivity is also under Bidder’s scope. Bidder shall quote accordingly. |  |
|  | Earthing |  | Please confirm main earthmat is required for present+future scope bays at nilgrar GIS subststation within fence area only as per tender "general arrangement & electrical plan layout". Eartmat for complete area shown under X and Y cor-ordinates is not required. | Extent of earthmat to be laid in Switchyard shall be decided during detailed engineering. Bidder shall quote accordingly. |  |
|  | Tension String |  | We understand 220kV/33kV line side tension sring and long rod insulator is not required under subststaion supply / services scope. Please confirm. | Bidder to quote as per requirements of Bidding documents. |  |
|  | TL |  | Please confirm the both connecting substation line length for 220 kV side. | Bidders may refer Clause 1.3.1, Section-IA, Volume-II (Technical specifications) wherein following contact details/ address has been indicated: Chief General Manager (Projects) POWER GRID CORPORATION OF INDIA LTD. Northern Region Transmission System-II Regional Headquarter OB-26, "GRID BHAWAN", RAIL HEAD COMPLEX JAMMU-180012. Bidder shall quote accordingly. |  |
|  | CRP |  | Please confirm whether simplex or duplex type CRP required under present scope. | Simplex type panel as per Section: CRP, Rev.9 shall be supplied under present scope. Bidder shall quote accordingly. |  |
|  | 220kV EOT Crane |  | We understand EOT crane capacity and type is acceptable as per OEM recommendation. Please confirm. | Refer Cl. 17 of Section: GIS, Rev.5A for requirements of EOT Crane. Bidder shall quote accordingly. |  |
|  | 33kV EOT Crane |  | We understand that EOT crane for 33kV GIS switchgear is not required. | Confirmed. |  |
|  | Relay test kit |  | We understand BPS line item "39" is normal tool kit. No numerical reay test kit is envisaged under presnet scope of supply. Please confirm. | The BPS line item referred to corresponds to S. No. 35. However, in reply to query, Refer Cl. 36 of Section: CRP, Rev.9 for requirement of Relay Test Kit. Bidder shall quote accordingly. |  |
|  | Telecommunication - Joint Box |  | We understand "OPGW joint box" supply/erection at substation line dead entry gantry shall be part of transmission line scope . So same is not required under substation supply/services scope. Please confirm. | Bidder to quote as per requirements of Bidding documents. |  |
|  | Telecommunication |  | Please confirm there is no requirement of repeater hub. | Confirmed. |  |
|  | SAS |  | We understand substation SAS is required as per tender single line diagram. | Bidder’s understanding is correct. |  |
|  | Bus bar protection |  | We understand bidder may offer centralised/distributed bus bar protection. No future bays envisaged under present scope. | Centralised/distributed bus bar protection scheme as per Cl. 26 of Section: CRP, Rev.9. Further, refer Cl. 26.3 (o) & (p) for bus bar protection for future bays. Bidder shall quote accordingly. |  |
|  | Relay setting calculations |  | We understand relay setting calculations shall be provided by client. Kindly confirm. | Bidder to quote as per requirements of Bidding documents. |  |
|  | Lightening arrester |  | We understand that 220 kV & 33 kV LA with polymer or porcelain insulator are acceptable. Kindly confirm. | Confirmed. |  |
|  | Order of Prevail |  | In case of any discrepancy in between price schedule, section project & tender drawing & tech. Specification. Kindly confirm the Order of precedence. | The order of precedence shall be as mentioned at Cl. No. 22.3 of ITB and Cl. No. 8 of Section: Project. The order of precedence amongst the specifically mentioned documents is as follows: a) Price Schedule b) Section Project & Tender drawings c) Technical Specifications |  |
|  | Land |  | We understand hurdle free , levelled land shall be provided by client. Kindly confirm. | Tentative land coordinates are already provided in Cl. 11.16 of Section: Project. Further, Contouring & site-levelling is also in bidder’s scope. Bidder shall quote as per requirement of Bidding documents. |  |
|  | SBC |  | Please share tender stage tentative Soil investigation report (SBC, ERT contour etc.) for estimation of foundations. | Soil investigation is in bidder's scope. Bidder to quote as per BPS. |  |
|  | Basic Wind Speed |  | 39m/Sec as per Latest Wind Map of India. Kindly confirm. | Confirmed |  |
|  | Requirement Of Grade C Structural Steel |  | Kindly confirm whether Grade C Structural Steel is required to be provided as per IS:2062 due to extreme low temperature. | Confirmed |  |
|  | Requirement Of Snow Loading |  | Snow Loading is applicable as per IS: 875 Part IV. Please confirm. | Confirmed |  |
|  | Site Visit Time And Facility Location |  | Please provide the store location for estimation of hydrant pipe location | Location of store shall be decided during detailed engineering. Bidder shall quite accordingly |  |
|  | Schedule 1 >> Supply BOQ Sl. NO. 199 >> Non standard structure |  | As per supply BOQ sl. No. 199, Towers, Beams & Equipments shall be Lattice type. However as per Section project page no. 6 of 16, same may either be Lattice or Pipe. Please clarify. | Bidder to Quote as per BPS. |  |
|  | Schedule 3 >> Erection BOQ Sl. NO. 137 >> CRB |  | We presume that CRB will be double storied. Please confirm. | Design and drawing of Control Room building is in bidder’s scope. It can be either single or double storey and the same shall be decided during detail engineering. |  |
|  | Section Project > > Page 7 of 16 |  | We believe that piles, if required during execution shall be paid extra. Please confirm. | Pile is not envisaged. If encountered during detail engineering it shall be dealt with clause no 20.22.2 of technical specification for substation -civil works -Rev 11A |  |
|  | Building Measurement |  | We propose that internal cable trenches in Gis Building & CRB shall be measured & paid in similar way of outdoor trenches. Please accept. | Internal cable trenches in GIS Building & CRB shall be measured & paid for excavation, concrete, reinforcement steel. However structural steel shall be deemed to be included in the plinth area rate. |  |
|  | PEB suppliers |  | Please share project specific list of approved PEB suppliers. | Please refer compendium of vendor available on POWERGRID website |  |
|  | 220 kV & 33 kV GIS |  | We understand that bidder can propose seprate make of 220 kV & 33 kV GIS rating. Kindly confirm. | Bidder’s understanding is correct. Further, refer Cl. 11.13 of Section: Project for Technical Requirements of 33kV Indoor Switchgear (GIS Type). |  |
|  | Approach road to proposed site |  | 1). As per section project the construction of approach road leading to allotted site is included in bidders scope, however seperate BOQ item is not available for the same. So we presume that its drawing and specification will be same as that of switchyard internal road and payament will be made in same line item. Any RCC or Pipe culverts shall be payable extra. Please confirm. | 1) Confirmed |  |
|  | Construction Power & Water |  | Kindly confirm availability of the sources for 415V constructional power and water near the boundary of proposed site. | Refer Cl. 14.3.2 of Section: GTR, Rev.15 for facilities to be provided by Employer. Bidder shall quote accordingly. |  |