| Sl. No. | # Volume/ Section/ Description | # Clauses | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- |
| Volume-I: Condition of Contracts |  |  |  |  |
|  | ITB Clause 9.3(c)(iv), ITB, Section-II | …………….. (iv) The leader shall be authorized to incur liabilities and receive instructions for and on behalf of any and all partners of the joint venture, and the entire execution of the contract, including payment, shall be done exclusively with the leader, provided otherwise requested by the joint venture and agreed between the Employer and the leader. ………………. | As per clause, we understand that in case of JV / Consortium bid, each Consortium Partner can raise separate direct Invoice and receive separate direct payment for their respective scope of work. Please confirm our understanding. | Provisions of the Bidding Documents are amply clear. |
|  | GCC Clause 9.3.1, SCC, Section-V | …………………. The Contractor shall also arrange additional Performance Security (ies), if applicable as per stipulated QR/Clause no. 5 of Joint Deed of Undertaking mentioned at Sl. No. 20, 22 of Section – VI: Sample Forms and Procedures. The said security(ies) shall be required to be extended time to time till ninety (90) days beyond the actual Defect Liability Period, as may be required under the Contract …………………. 1.4 (iii) (Route-IV) of Annexure-A (BDS) (iii)A legally enforceable undertaking (jointly with the GIS Manufacturer) (as per enclosed format in Section-VI, Volume-I of bidding document) to guarantee quality, timely supply, performance and warranty obligations as specified for the equipment(s) is submitted along with the bid stating that GIS Manufacturer shall furnish performance guarantee for an amount of two (2) % of the total contract price. This performance guarantee shall be in addition to the Contract Performance security to be submitted by the Bidder. | In the case of participation via Route-4 by JDU support from a GIS OEM. GIS OEM has to submit 2% CPBG corresponding to entire substation value. Currently GIS OEM is submitting multiple CPBGs against this requirement with different validities as per SCC-Clause no. 39. Our request is that GIS OEM should be allowed to submit only 1 CPBG with validity equivalent to GIS equipment Defect Liablity Period +90 days. Kindly accept the same. | Provisions of the Bidding Documents are amply clear. |
| Volume-II: Technical Specifications |  |  |  |  |
|  | 1.0 Section-Project (Part-A) V2 R0 Cl. 11.2 CT data | Requirements of 245kV, 2500A, 120% extended rating current transformer shall be as follows: a) Primary ratio taps: 2500-1600-800/1-1-1A b) Class: PX, 0.2S, PX, PX c) Core: 4 d) Min. Knee point voltage Vk: 2500-1600-800V for 2500/1600/800 A tapping in all cores except metering. e) Burden: 20VA (For Metering core) f) Max. CT sec. winding resistance Rct (ohms): 12.5/8/4 for 2500/1600/800 tapping g) Max. excitation current at Vk (Imax in mA): 16/25/50 for 2500/1600/800 tapping | We would like to inform you that, the Bus coupler bay is having rating of 2500A, hence the adjacent CT data mentioned in Cl. 11.2 shall be only applicable for Bus coupler bay and not for ICT bay & Transmission line bay. For TL bay & ICT bay we understand to consider the CT data as per GIS Specification Rev5A Table 3C. Please confirm. | Confirmed. |
|  | Tender Layout | Tender Layout | Please let us know whether Control cum 33KV switchgear building is single storey building OR more than one storey building. Pls clarify. | Design and drawing of Control Room Building cum 33kV Indoor Switchgear Room is in bidder’s scope. It can be either single or double storey and the same shall be decided during detail engineering. |
|  | Tender Layout | One Nos. 220KV Future transformer bay | As per tender layout, We understand that the bidder has to freeze the Size of 220KV GIS PEB building considering only space provisions for One Nos. 220KV Future transformer bays (Supply of GIS module for the same is not under our scope) along with space required for maintenance bay. Pls confirm our understanding. | The size of 220kV GIS PEB building has to freeze considering all 220kV bays in present scope as per Clause 2.A. of TS, Section: Project along with space required for maintenance bay. Space provision for future 220kV GIS Transformer Bay module in the present scope GIS building is not envisaged. Bidder shall quote accordingly. |
|  | Tender Layout | Future Interface module | As per the tender layout, we understand that at only one end, Future interface module is required for extension of future bays. Pls confirm our understanding. | Please refer to Clause II. i) v. of Annexure-VIII to TS, Section: Project. Interface module (with isolating test link) for future extension is required on both ends of Bus bar. Bidder shall quote accordingly. |
|  | Tender Layout | Connection Philosophy between 220KV Line overhead conductor to 220KV GIS building | As per the tender layout, we understand that the 220KV line bays overhead conductor terminates to 220KV GIS building through Horizontal SF6/AIR bushing but the quantity of horizontal SF6/AIR bushing is not mentioned in bid price schedule. Pls clarify. | Please refer Clause II. ii) vii of Annexure-VIII to TS, Section: Project, wherein the SF6 to Air Bushings (Wall Bushings) are already included/covered in the detailed description of 245kV GIS line bay module and similarly included/covered in 245kV GIS ICT bay module description for ICT bay termination. Accordingly, no separate item envisaged for SF6 to Air Bushings (Wall Bushings) in BPS. Bidder shall quote accordingly. |
|  | Bid price schedule / SS98-220/33KV NILGRAR GIS SS / Sr No.- 19 & 20 | "Sr.No. -19 - 33KV, 1CX630 SQ.MM XLPE AL. ARMOURED CABLE Sr.No. - 20 - 33KV ,3CX95 SQ.MM XLPE AL. ARMOURED CABLE " | As per the bid price schedule we understand that the 33KV HT cable size shall be as per the bid price schedule. 33KV HT cable sizing is not under bidder scope of work. Pls confirm our understanding. | Confirmed. |