Section 3

TELECOMMUNICATIONS MANAGEMENT NETWORK

The Contractor shall provide a Telecommunications Management Network (TMN) System for operational support of the Equipment (MPLS-TP, Optical Amplifiers etc.) and associated subsystems. The contractor shall provide a centralized TMN System to monitor, configure and control all the Network Elements, supplied under this Package. This TMN system shall assist the Employer in the overall management, operations and maintenance of the telecommunication resources including detection of degraded circuits and system performance, diagnosis of problems, implementation of remedial actions and the allocation or reallocation of telecommunications resources.

  - Applicable Standards

The TMN design concept, functional and informational architecture, and physical architecture, shall be in compliance with ITU-T Recommendation M.3010.

  - TMN Architecture

    - The bidder will propose single TMN system in the Employer’s network such that all the management functions are available seamlessly across all the network elements (MPLS-TP, Optical Amplifiers etc.) supplied by the bidder under this package.

    - If the bidder has existing TMN system in Employer’s network, the bidder shall be required to upgrade existing TMN system such that all the management functions are available seamlessly across all the network elements supplied by the bidder under this package and earlier package(s). In such case, the bidder shall quote the cost of all required hardware/ software/replacement/ update for up gradation against TMN system item in price schedules. The TMN architecture envisaged under the subject package is described below:

    - The main Control Centre (DC) for all the network elements being procured under this package will be located at New Delhi and the backup Control Centre (DR) will be located at Bangalore, however PowerTel reserves the right to change the location of DC and/ or DR as per requirement. The operation of main and backup Control Centre will be co-ordinated in such a way that the database in both the Control Centres are in synchronism. The synchronisation of database shall be done automatically and periodicity of synchronisation shall not be more than three (3) hours under any circumstances. The management functions of the network elements under this subject procurement encompasses from any to any and the operation and maintenance of all the network elements shall be seamless. In case of failure of main Control centre, the control function shall be fully taken care of by backup Control Centre by manual take-over and/ or automatic mechanism, as per requirement. Restoration of main Control Centre shall be done after synchronism of database is achieved and after proper validation, which should be done automatically. Similar methodology shall be adopted for restoration of back up Control centre from a failover situation.

    - It should be possible to configure at least ten (10) remote Work Stations located at across India other than DC & DR. The bidders shall propose the scheme in the bid along with exact hardwares that will be required for this purpose. The TMN shall provide-

- Collection of Management data from all Network Elements (NEs) supplied under this package. The minimum monitoring and control requirements for the communication equipment shall be as per Section 2.

- Processing of above management data by using a processor(s) located at Control Centres and additional intermediate station processors, wherever required.

- Invoking the TMN functions through local Work Stations (DC & DR) and remote work Stations.

- PowerTel may like to extend the environmental/ auxiliary alarm of associated devices at locations where Telecom equipment are installed, if required. SO necessary provision of Supervisory monitoring of following alarms will be available:

    - Intrusion Detection Alarms

    - Power Failure

    - Fire and Smoke Detection

    - Environmental Control (Temperature, Humidity etc.)

- Communication channel support as specified in Section 3.4.

- The TMN system shall be redundant as defined in Section 3.6.

- The contractor must ensure that TMN has north bound CORBA/XML/ Q3/ SNMP or any other acceptable open standard interface and shall ready to partake any information required by other vendors for ensuring the integration with other vendors’ systems as well as operations support system (OSS). The north bound interface shall be compliant to Tele Management Forum (TMF 814) or any other internationally accepted standard for integration. The interface shall accommodate all required functionalities to implement OSS but not limited to the following:

- Real time forwarding and synchronization

- Provisioning of circuits

- Upload of network topology

- Monitoring of events for topology and circuit changes

- Alarm handling

The details shall be finalised and discussed during detailed engineering and the Contractor shall be obliged to provide/share all necessary information and co-ordinate with the implementation vendor of OSS without any cost implication to Employer.

- The supplied TMN system shall be capable of handling all management functions for at least 200% of the final network elements supplied under this package, also the TMN system shall be capable of handling the fully expanded equipment. If the bidder is upgrading existing TMN system, the upgraded TMN system shall be capable of handling all management functions of fully expended equipment for at least additional 200% of the final network elements supplied under this package. The cost of license to meet these requirements shall be included in the network element cost. The TMN shall be equipped to connect at least 10 local work stations at main control centre (DC), at least 10 local work stations at back-up control centre (DR) and 20 remote work stations. The Contractor shall submit for Employer’s approval, the TMN architecture describing in detail the following subsystems/features:

- Database used in TMN.

- Server/workstation, LAN, Peripherals, and hardware (Refer Section 3.7)

- Software and operating system (Refer Section 3.8)

- Local / Remote Operator Consoles (Refer Section 3.7)

- Craft Terminals (Refer Section 3.5.)

- Data communication between NEs, Remote/Local Consoles and TMN Processor(s) (Refer Section 3.4)

- Routers/ Switches

- Expansion Capabilities

- Redundancy Provisions (Refer Section 3.6)

- Response time details (Refer Section 3.2.1)

- Detail Breakup of BOQ listing all Hardware components, Physical architecture, Software(s) and licences included in the TMN, the Bidder shall indicate separate prices for each item along with the bid.

- Compliance with DoT condition w.r.t. storage of logs & necessary provision for their Online as well as offline both storage

- In case any of the proprietary interface, protocol, system architecture etc supplied with TMN/ NMS etc, the contractor shall have to provide full support including manpower resources, licenses, documents etc for integration of network with third party orchestrator or OSS, GIS, whenever required during project execution, DLP or AMC.

    - General Operational and Functional Requirements

- The TMN system shall be multi-user system and based on Graphical User Interface.

- It should be possible to have a view of selected sub-networks/rings controlled by the TMN system as per requirement. By zooming-in, it shall be possible to drill down to module-level in each NE for configuration and fault management. The same shall be provided through user-friendly GUI commands.

- The TMN system shall provide the complete view of the network elements and the interconnecting links. The TMN system shall have the ability to include the network elements and the links in the visual/graphical map of the domain. The visual maps shall display the elements and the links in different colour depending upon the status of the links. For example, green colour for healthy and amber/yellow colour for degraded condition and red for unhealthy condition may be used.

- It shall provide the ability to drill down to the individual element, then to subsystem, then to card and then to port level configuration template from the domain-map by clicking on the icon of the network element.

- It shall be possible to generate customized reports for various types of faults, performance history, security management etc. It shall be possible to generate reports at various client levels to facilitate monitoring of performance statistics in a pre-defined/ customized format. It shall be possible to generate and define the formats at any time, based on network needs.

- The TMN shall support correlation (filtering and suppression) to avoid multiple alarms from a single source of failure within the sub-network. Single Alarm shall be provided for the events that are correlated and are due to a common cause.

- It shall be possible to execute any schedulable administrative command i.e. NE backup, software download, performance, operator log-in/ log-out etc., at any time by attaching a time tag to the command and it shall be executed when the Network real time matches the time tag. It shall be possible to define both time and date. If no date is mentioned, the command shall be executed daily at the time mentioned.

- The response time for query/command on any operator terminal, local or remote shall be indicated by the vendor. For update on topological information on the terminals, the response time shall be indicated by the vendor. The response time shall however, be reviewed depending upon total NE load and topology by Employer during testing.

  - Management Functions

The TMN shall support and provide the following Management functions:

- Configuration Management

- Fault Management

- Performance Management

- Security Management

- Inventory Management

- Software Management

- Network planning

The equipment shall support the generic requirement of fault, configuration and performance requirements as per clause 6.1 of ITU-T G.872. The equipment shall support the management aspect of the optical network as specified in ITU-T G.874 and G.874.1. The functions mentioned below shall be available across the entire network on a seamless end-to-end basis comprising of all the network elements (MPLS-TPOptical amplifiers etc.) being procured under this package.

    - Configuration Management

Configuration management is concerned with management, display, configuration, provisioning and control of the network configuration and shall be implemented in accordance with ITU-T Rec. G.874. Minimum specific requirements that shall be satisfied include the following:

- Provide tools to establish, maintain, update, delete and retrieve the topology and configuration information and provide graphical maps depicting the configurations. It shall be possible to inspect and configure all the appropriate parameters of the Network Elements through the Graphical User Interface.

- Gather descriptive information about the current configuration of the equipment, provide operator displays, and prepare reports.

- Provide tools for planning, establishing, and changing the static equipment configuration. Provide for changes to the equipment configuration in response to equipment failures, planned upgrades, and operator requests to take equipment offline for testing.

- Provide verification testing to support new equipment installation.

- Provide tools & support for configuring end to end and to configure protection for each of them individually.

- Provide tools for downloading software upgrades from remote using TMN.

    - Fault Management

Fault management is concerned with detecting, diagnosing, bypassing, directing service restoral and reporting on all the network equipment, systems, and links and shall be implemented in accordance with latest and relevant ITU-T standards.  Minimum specific requirements that shall be satisfied include the following:

- Display equipment status in a consistent fashion regardless of the source of the data on a graphical topological, map-type display.  Status shall be displayed through the use of colours on links and nodes as well as through text. Alarm notification shall include type, occurrence, severity, probable cause and clearing.

- Obtain status and detect faults through periodic polling, processing of unsolicited alarms and error events, and periodic testing for connectivity. Each failure and clearance shall be time-stamped.

- Maintain an alarm summary of unacknowledged alarm events on the management station display and maintain a log of all received alarms.  The operator shall be able to acknowledge and clear alarms individually and as a group.  The use of alarm correlation techniques is required to minimize the proliferation of alarms caused by a single, common event.

- Bypass failures through the use of automatic failover to redundant equipment where possible and through operator-initiated actions where automatic failover is not possible.  The criteria for failover shall be configurable.

- Storing and processing of historical alarm information for 35 days minimum. Retrieving functions with filtering capabilities for historical alarms and events shall be provided. FCS errors for Ethernet clients shall be provided.

- Assigning alarm severity i.e. Critical, Major, Minor & Deferred.

- Provision to create a customised entity under fault management window to monitor alarms of specific set of customers, set of links, geographical area etc.

    - Performance Management

Performance management is concerned with evaluation of the use of network equipment’s and their capability to meet performance objectives and shall be implemented in accordance with latest and relevant ITU-T standards. Performance monitoring shall conform to ITU-T Rec. M-2100, M-2101, M-2120, G.821, G.826, G.828, G.829 and RFC 2544.  The equipment shall support / OTU-k related performance requirements specified in ITU-T G.8113, G.8113.2, G.709, G.8201 and G.7710. The minimum specific requirements that shall be satisfied include the following:

- Provide support for an operator to initiate, collect, and terminate performance metrics under both normal and degraded conditions.  For example, The BER of each link, together with other data measured at each node, shall be available on operator request. A suitable user interface shall be provided for generating report. The details for report format shall be finalised during detailed engineering. Performance history for minimum 35 days shall be supported with configurable launch time and performance evaluation/integration period. It shall be possible to set the performance thresholds from 1x10-5 to 1x10-15 through the TMN/LCT in a continuous manner in the specified BER range as above.

- Provide tools for measuring the uptime of link/ location/ circuit trail end to end.

- Provide end to end latency of Ethernet links at circuit level.

- There shall be provision for both, near end performance monitoring and far end performance monitoring at lambda level and circuit level.

- Monitor point to point & end to end signal quality and history at individual wavelength level. Provide operator controls to monitor performance of specified events, measures, and resources.  Specifically provide displays to permit the operator to:

- A suitable user interface shall be provided for generating above reports. The details for report format shall be finalised during detailed engineering. Select/deselect network equipment, events, and threshold parameters to monitor

- Set monitoring start time and duration or end time

- Set monitoring sampling frequency

- Set/change threshold values on selected performance parameters

- Generate alarm events when thresholds are exceeded.

- Monitor optical parameters (signal levels) of all optical interfaces and generate alarms. Set multiple thresholds on certain performance parameters of electrical and optical signals.  Alarm categories include as a minimum a warning and a failure.

- Calculate selected statistical data to measure performance on selected equipment based on both current and historical performance data maintained in performance logs.  Performance data provided is limited to what is available from the equipment Contractors.

- Provide graphical displays of point to point and end to end current performance parameter values.  Provide tabular displays of current, peak, and average values for performance parameters.

- Generate reports on a daily, weekly, monthly, and yearly basis containing system statistics

    - Security Management

The TMN system shall provide adequate security to the data and for the access to the system as per the following details:

- The TMN shall have the capability of supporting the management of Network through local and remote Operators. The authorizations and the privileges of the operators (Remote and Local) shall depend upon the Login and Password.

  - Low level protection for read only access to faults and performance information.

  - Medium level protection for access to configuration status and features.

  - High level protection for control of access to change in the configuration and control parameters.

- Network management security features shall include operator authentication, command, menu-restriction and operator privileges. The TMN shall support multi-level passwords as below-

  - TMN shall allow the System Administrator to define the level of access to the network capabilities or feature for each assigned password. TMN shall block the access to the operator in case of unauthorized commands being tried for five consecutive times. TMN shall also not allow the entry into the system in case wrong password is provided more than five consecutive times during the login.

  - The system administrator shall be able to monitor and log all operator activities in the TMN and Local Craft Terminal.

  - The dynamic password facility shall be provided in which the operator may change his password at any time.

- All log-in and log-out attempts shall be logged in the security log file of the TMN system.

- The network and the management system shall be protected against intentional or accidental abuse, unauthorized access and loss of communication.

- The man-machine communication programs shall have the facility of restricting the use of certain commands or procedures to certain passwords and terminals.

- The LCTs shall normally operate through the centralized TMN. Only in the case of failure of link between the LCT location and the TMN, the LCT should be able to supervise/monitor the local assigned to it.

- It should be mandatory for the system to have a record of all log-ins, operation and maintenance command logs which shall include the actual command given, who gave the command, when was it given with date and time and from where for a period of at least twelve months after which a backup should be possible under system administrator command.

- It shall be possible to define multiple domains for purposes of monitoring and control. It shall also be possible to make domain based on the circuit(s) of a particular customer. Means shall be provided to ensure only one authorized operator has access to change in the configuration and control parameters for a selected domain of the network.

- The system shall be able to back up programmes and data and restore the same to and from external storage media (e.g. tape, CD etc.). Anti-virus packages, if required, shall also be provided.

- The DCN network shall transmit all management data encrypted. Encryption shall be done by 128-bit encryption key.

- System shall also fully comply with DoT requirement on security & remote access.

    - Inventory Management

Under inventory management functionality, the following shall be supported:

- It shall indicate complete view of the network elements and interconnecting links. It shall indicate absence or presence of any physical module in hardware elements. It shall also indicate the usage of module i.e. how many ports are in use, which interface is in use, and which are free to be used etc.

- TMN shall be able to discover and keep the device information.

- The inventory information shall be provided to Network Management Layer (NML) / Service Management Layer (SML) so that SML is able to create and activate a service to the customer automatically. This shall also assist SML in providing the network inventory to which SML shall add the customer identification and maintain this information in the database.

- Generate report based on query e.g. module type, network element location etc. A suitable user interface shall be provided for generating report. The details for report format shall be finalised during detailed engineering.

    - Software Management

It shall be possible to carry out the following tasks under the software management function:

- Loading of new system software.

- Manage different versions of software.

- Shall have the capability of managing multiple versions of software for individual elements. In this case, one software version shall remain active and other versions shall be passive.

- Installation of software patches.

- Examine contents of all system memory and disk memory.

- At the time of downloading the software, the message shall be displayed that the software has been downloaded successfully or failed and at what stage.

- The operator terminals (local & remote) shall not allow loading of any software without the terminal administrator's authorization.

- It shall support FTP/TFTP for downloading of Software, configuration, patches etc. to the Network Element.

- It shall enable operations like changing the system configuration, reconfiguration of input and output devices, loading a new software package, etc. Both automatic and manual reconfiguration capabilities shall be available.

- All commands which are executed over the TMN program or data shall be logged in a file (read only) and it shall be possible to retrieve the same on demand whenever required using Man-Machine Commands. The file usage of up to 50%, 75% and 90% shall generate alerts in the server platform, of suitable category prompting the operator to initiate the backup operation.

- It shall be possible through a single Man-Machine Command to obtain a list and the total number of equipment of a particular domain in a state (e.g. in-service, blocked etc.).

- While working on system level commands, it shall be possible to log recent user operations and display the same through the GUI.

- Local & remote software download via management system to NEs and LCT shall be possible, including the means of identification of software module versions. No loss of data/traffic and connection-map shall take place during the software downloading process.

  - Data/ Communication Channel Requirement and Integration

Communication channel requirements for TMN system have not been considered in BoQ and the Contractor shall provide these as a part of TMN system and/or as part of network element) supply. The Contractor shall provide all required Equipment, interface cards / devices, LAN, routers/ bridges, channel routing, cabling, wiring etc. and interfacing required for TMN data transport for all the supplied equipment and transport of data shall be in protected configuration.

The data transport network shall be designed with full protected configuration and with 100% hardware redundancy. The Data Communication Network shall be designed to ensure proper and effective use of encryption techniques/devices to protect confidentiality, authenticity and/integrity of information in line with DoT guidelines.

The bidders shall optimise the use of communication channels for TMN. It is preferable that the capacity required for all sorts of communication needs be restricted to a 100 Mbps (or a part of it) throughout the network. The bidders shall use appropriate technology to achieve this.

The bidders shall describe in the proposal the TMN data transport proposed to be used by the bidder in detail including capacity requirements and various components/equipment proposed to be used. The bidders shall also indicate the response times envisaged.

  - Craft Terminal

Each node on the network shall include provision for connecting a Local Craft Terminal, i.e. a portable (laptop) IBM-compatible personal computer (PC) to support local commissioning and maintenance activities. It shall also be possible to perform maintenance activities on remote stations. Through the use of this Local Craft terminal, the operator shall be able to:

a.	Change the configuration of the station

b.	Perform tests

c.	Get detailed fault information

d.	Download configuration data, software upgrades

e.	Upload alarm data and other system related data from the network element

f.	Monitor performance parameter of optical ports.

The laptop computer shall be connected to a V.24/V.28 interface, Ethernet interface, USB etc available at network element. Laptop computers, each complete with necessary system & application software to support the functions listed below, shall be supplied to the Employer.

- There shall be a provision at each network element for connecting to a Local Craft Terminal (LCT). This feature shall be available for all network element equipment proposed by the Bidder. The Local Craft Terminal shall be connected through a serial V.24/V.28, Ethernet interface, USB etc.

- The Local Craft Terminal software shall be executable on a laptop PC equipped with latest supported Microsoft Windows or Linux (or its variant) operating systems.

- It shall be possible, once connected to one Network Element, to access other network elements by way of addressing.

- It is desired that the Local Craft Terminal and TMN shall have the same Graphical User Interfaces and they shall behave in the same manner regardless of whether they are executing on a Local Craft Terminal or on TMN.

- The Local Craft Terminal shall provide Graphical User Interfaces that enables the user to interact with the embedded software in the network element in such a way that the user can:

  - Inspect all data residing in the network element, being registers, files or database elements;

  - Set all the appropriate data elements, as appropriate, within the network element.

- The Bidder shall state if there are any functionalities (or registers, files or database elements) for which the Graphical User Interface of the Local Craft terminal cannot be used and the means by which such functionalities are then reached.

  - Redundancy Requirements

TMN system hardware shall be so designed that failure of a component shall not inhibit any of the functionality of the TMN Server at any of the control centres. Redundancy of TMN servers shall be accomplished between Main (DC) and Backup (DR) centres. If required each network element may report to two masters. The hard disk and power supply for each server shall be in redundant configuration.

  - Hardware Requirements

    - Server, Workstation and Craft Terminal

The TMN hardware should be based on either UNIX/LINUX/SOLARIS or the latest supported windows server platform with Sun/HP/Siemens/IBM or any other equivalent make Servers and Workstations. The software should be user friendly. The sizing of the server/processor, RAM, number & type of interfaces, RAID/HDD etc. shall be commensurate with the network size, number of con-current users, response time etc. The bidder shall provide details of hardware, software and server sizing calculations along with the bid. Servers and workstations shall have the necessary Disk drives for data backup and restoration. Servers along with associated hardware shall be rack mounted.

- Work station CPU enclosures shall be desktop type (Preferably All-in-one PC suitable for 24x7 NOC operations) and shall include available expansion slots except for the Craft Terminal which shall be a laptop. All the VDUs including that of server and Workstations shall be not less than 23.8” Full HD colour LED panels. Tentative quantities of workstations given in BoQ, although PowerTel reserve the right to increase/ decrease quantity based on requirement. The minimum requirement for Desktop PC/ Terminal shall be as follows:

    - Intel 13th Generation Core-i7 processor or higher

    - Licensed MS Window with Anti-Virus provisioning

    - 16GB DDR-4 1333 MHz SDRAM or higher

    - 512 GB SSD

    - Min 23.8-inch Full HD LED monitor

    - Ethernet 10/100 adapter with RJ-45 connector

- Craft Terminal (Hardware & Software) shall be supplied along with associated items like: cable, connectors, licensed software etc.  The Craft Terminal (hardware) shall be a professional grade device complying with MIL-STD-810G reliability & stability, from a prominent Laptop/ Computer manufacturer (like: HP, DELL, Lenovo etc) and shall be supplied along with latest licensed operating system (OS). The minimum requirement of each Craft Terminal shall be as follows:

    - Intel 13th Generation Core-i7 processor

    - Licensed MS Window with Anti-Virus provisioning

    - 16GB DDR-4 1333 MHz SDRAM

    - 512 GB SSD

    - 14-inch Full HD LED (or Higher resolution)

    - Ethernet 10/100 adapter with RJ-45 connector

    - Minimum 6 hours Battery Life

    - Local / Remote Operator Consoles

The Contractor shall provide operator consoles sized and equipped to support the subsystem(s) furnished and in compliance with the specification. The console shall provide hardware interfacing for the TMN users to the software operating support systems. At a minimum, a console shall include a work station (refer Section 3.7.1 above) and suitable interfaces to the TMN as stated above.

    - Power Supplies

The TMN system shall use 230-volt 50 Hz AC or -48volt DC for its operation.

  - General Software/ Firmware Requirements

Due to various alternative design approaches, it is neither intended nor possible to specify all software and firmware characteristics. It is the intent herein to provide design boundaries and guidelines that help to ensure a demonstrated, integrated program package that is maintainable and meets both hardware systems requirements and the customer's operational requirements.

The Contractor shall provide software upgrades and patches if any for the proposed TMN. The Contractor shall also provide detail procedure to execute the upgrades.

    - Operating System Software

Operating system software shall be provided to control the execution of system programs, application programs, management devices, to allocate system resources, and manage communications among the system processors. The Contractor shall make no modifications to the OEM's operating system, except as provided as USER installation parameters.

    - Applications Software

All applications software shall be written in a high-level programming language unless developed using industry proven application programs and development tools provided with the system. The Contractor shall make no modifications to the applications program except as provided as USER development tools.

    - Software Utilities

A utility shall be provided to convert all reports into standard PC application formats i.e. dbase, dxf, excel, ascii etc. as applicable.

    - Revisions, Upgrades, Maintainability

Software revisions, upgrades and maintainability is specified as follows:

      - Versions

All firmware and software delivered under this specification shall be the latest field proven.

      - Program Rewrites

All firmware provided shall support its fully equipped intended functional requirements without additional rewrite or programming.

      - Maintainability

Contractor shall supply a copy of installation version of software(s) including final database in External SSD Drive, if requested by Employer.

      - Standards Compliance

Software provided shall be compliant with national and international industry standards such as IEEE, ISO and OSF.

    - Database(s)

The contractor shall develop all the databases for final wideband network following the global acronyms for all stations. Database(s) shall comply with the following:

      - Structure and Inclusions

A database shall be provided that contains all structure definitions and data for the integrated functional requirements of TMN system.

TMN operator Groups shall share the same virtual database. This means that they shall share the same database and database manager, whether or not physically separate databases are maintained.

  - Help

All applications shall be supported by USER accessible HELP commands that shall assist the USER in the performance of its tasks. HELP commands for an application shall be available to the USER from within the active application and shall not interfere with the activities of the application.