Section 4

ENVIRONMENT, EMI, POWER SUPPLY, CABLING AND EARTHING

The purpose of this section is to describe the minimum general equipment characteristics for telecommunication equipment and specifications for environmental conditions, source power conditioning and backup, equipment construction, and installation.

  - Environmental Requirements

Equipment and their components provided under this specification, shall operate reliably under the following environmental conditions.

    - Temperature and Humidity

The equipment shall operate in accordance with the limits shown in Table 4.1

| Table 4-1 Environmental Operating Limits |  |
| --- | --- |
| All Equipment Operation meeting all Specifications Operation without damage Shipping/ storage | Temperature Range (Controlled Environment) 0 to +50C -5 to +55C -5 to +60C |
| Relative Humidity, non-condensing | Up to 90% |
| Elevation: Operating Non-operating | to 3,000 m to 10,000 m |

For each location, the Contractor is required to assess the environmental conditions for the equipment to be installed under this specification. The Contractor is responsible for all necessary enclosure, rack or equipment upgrades to ensure the proper operation of the installed equipment.

    - Noise:

## The offered equipment’s Maximum acoustic noise emission levels for telecommunication equipment must be in accordance to ETSI 300 753, Acoustic noise emitted from telecommunication.

Procedures for measuring and reporting the noise emission of offered telecommunications equipment must be as per ISO 7779-2010; (Measurement of airborne noise emitted by information technology and telecommunications equipment.

    - EMI and Electrostatic Interference

The emission, immunity and resistibility requirements for the offered equipment must be as per the latest MTCTE essential requirements. For the individual tests to be carried out at the different interfaces, references are made to the relevant IEC and ITU-T recommendations or equivalent Indian Standard (IS).

    - Vibration and Shock Resistance

As per testing requirements indicated in Section 5.

    - Tropicalization

Communications equipment will often be stored and operated in uncontrolled environment areas and will be subject to mold, growth of fungus, corrosion, and oxidation. The equipment and components shall be suitably tropicalized during manufacture through commissioning, as necessary.

  - Primary Source AC/ DC Power Requirements

Facilities will be required to support both AC and DC power load requirements of telecommunications equipment as specified below:

    - Primary Source AC Power

It will be the Employer's responsibility to provide the required Primary AC Power support, if needed for communications equipment under this specification. The Primary AC Power supplied will be 240 VAC ± 10%, 50Hz with a frequency variance between 46 and 55 Hz. Harmonic distortion will not exceed five (5) percent.

All equipment and components provided under this specification requiring Primary AC Power shall be designed for normal operation under the above stated tolerances for 240 V AC supply.

The Contractor is responsible for providing in the survey report the Employer with projected 240 V AC Primary Power load requirement per equipment and totals, by location, for equipment provided under this specification.

    - Primary -48V DC Power

Power supplies/ converters for communications equipment (Except Computer Systems supplied as part of TMN which shall use 240 VAC) provided under this specification, shall use -48V DC uninterrupted primary source power. It is Contractor's responsibility to provide the Employer with -48 Vdc load requirement at each location. The Employer will provide -48 Vdc battery plant sized to support the maximum projected load requirement. The equipment shall be able to operate normally within the DC voltage range -42V to -60V.

    - Power Distribution and Protection

      - The Employer shall provide power sources of primary 240 VAC and -48 VDC power in each building. If two separate DC power sources are provided, the contractor shall connect the equipment from the both DC power sources. It shall be the Contractor's responsibility for the connection and distribution of all Primary AC and -48Vdc source power, in full compliance with all local and national electrical codes.

      - There are DC cable of four (04) different ratings identified in BoQ and shall be ordered along with Equipment. The contractor has to assess & recommend the rating (as per the ultimate load requirement of finalized equipment(s)) of Power Cable  to connect their Equipment(s) with DC Power Source, as per site requirement..

      - In case Rack is also ordered along with Equipment, the rack shall have a DCDB with sufficient number of MCBs to support installation of minimum of 3 equipment’s/Sub-racks and tapping power from Two (02). All MCBs required for connectivity shall be supply by contractor as part of Equipment or Rack accessories, assuming there shall be two (02) Power Sources.

      - There following cases to be considered as per site:

        - Case-1: Only Equipment is supplied. The DC Power will be tapped from PowerTel DCPS. So, DC Cable as per BoQ and a minimum of two (02) no of MCBs will be required.

        - Case-2: Equipment with Rack is ordered, and DC Power will be tapped from PowerTel DCPS. So, DC Cable as per BoQ to connect the PowerTel DCPS with the DCDB in the Rack, and minimum four (4) no of MCBs will be required in DCDB and minimum two (2) for PowerTel DCPS.

        - Case-3: DCPS is also ordered along with Equipment and Rack. AC cable as per BoQ will be supplied to extend input AC power to DCPS and the DCPS have sufficient number of MCBs (DCDB) to feed the equipment.

      - The DC Cables & Rack (equipped with DCDB) will be also supplied by contractor as per BoQ. DC Power will be distributed from this DCDB (Source-1 & 2) to the DCDB(PDP) available in each of the equipment Racks/ cabinets. Distribution of power among internal Sub-racks in a rack/ cabinet shall be done from the DCDB, wherever Rack/ Cabinet is supplied & bidder must supply the power cable along with Sub-racks as part of equipment accessories...

      - The Contractor is responsible for all inter-rack (enclosure) and intra-rack (enclosure) power distribution required to support equipment supplied under this specification. The Contractor shall provide all cabling, fusing, switching and circuit breaker and surge protection required.

      - Partially equipped subsystems shall be installed with provision for expansion. Equipment power supplies provided under this specification shall be sized to support fully equipped subsystems. Primary power distribution protection shall be sized to support and protect maximum operating load potential whether or not the actual projected load shall meet that maximum load potential.

      - The Contractor shall provide equipment and rack safety earthing in compliance with paragraph 4.3.4 of this specification.

  - Equipment Construction, Assembly and Installation

All equipment supplied under this specification shall be constructed, assembled and installed in accordance with the following requirements:

    - Identification

All cabling, racks/enclosures, equipment, modules and materials shall be uniquely identifiable as per the following:

    - Equipment

## Each equipment component to the level of printed circuit card shall be clearly marked with the manufacturer's part number, serial number, month/year of manufacture and revision level. The Contractor shall be responsible for maintaining the master revision level list until the Contractor has complied with all requirements of this specification.

Equipment chassis and printed circuit card cages having wired backplanes, shall be clearly marked with the manufacturer's part number, serial number, month/year of manufacture, revision level and an additional identifier corresponding directly to the applicable backplane wiring diagram/list.

      - Power Distribution

Power distribution panels shall be clearly marked with their unique identifier, source feed information, and remote source feed emergency disconnect location and identity.

Power distribution panel "MAIN Disconnect" and circuit breakers shall be clearly marked with a unique identifier. Circuit breaker feed lists shall be clear, accurate and the feed list information shall be posted inside each distribution panel door.

Inter-rack and intra-rack (enclosure) power distribution shall be clearly identified with source feed, voltage and power rating information. All power feed cabling shall be clearly identified near the point of termination.

All power distribution identification shall utilize heat-resistant permanent marking techniques such as stamped non-metallic tags, embossed labels, etc. Marking techniques are subject to approval by the Employer. Power distribution identifiers and information shall agree with the Contractor's power cable plant drawings.

      - Signal Cabling

Connectorized signal cabling/ wiring requires marking with a unique identifier at each connectorized end. The signal cable/wire identifier shall include a cable identifier and the location of both terminations. Signal cable/wiring installed on terminal blocks requires marking with the cable identifier and distant end location. The cable tag shall be clearly visible at the cable fanout point.

All signal cable, wiring and terminations shall be clearly labeled/ tagged with identifiers consistent with Contractor supplied cable plant records. Marking techniques are subject to approval by the   Employer.

      - Equipment Racks and Enclosures

All equipment racks, enclosures and equipment, including distribution frames, shall be clearly labeled with unique identifiers inscribing/ printing the name of the Employer (viz. “PowerTel”) on metal/ PVC sheets or thin metal/ plastic film, consistent with Contractor’s standard practice.

    - Installation Hardware

Equipment racks, enclosures, cable raceways and installation hardware shall, at a minimum shall comply with the following requirements:

      - Equipment Racks and Enclosures

All equipment provided under this specification shall be suitable for physically mounting in racks or enclosures (cabinet). The BoQ indicates the tentative quantities of equipment enclosure (cabinet) wherever required. In addition to cabinet requirements for telecom equipment being supplied under this package, the contractor may also be required to provide few cabinets for mounting Employer’s existing equipment at various locations after suitable modification in cabinet to meet existing equipment requirements. The size of the Cabinet will preferably be 2200mmx600mmx600mm, however cabinets with smaller size as per site requirement can also be ordered without any financial implication to PowerTel.

Selection of equipment racks and enclosures shall meet the following requirements:

        - Equipment Sub Rack Construction

Equipment Sub Racks provided for installation in environmentally controlled facilities, shall meet the following minimum requirements:

          - Equipment Sub Racks shall be steel/ aluminum fabricated and finished on all surfaces. All metal and welds shall be   thoroughly cleaned and sanded to obtain a smooth finish. All surfaces shall be treated for rust and primed to form a bond between metal and the finish coats of paint.

          - Equipment covers shall be provided for exposed components mounted in equipment sub-Racks.

          - Dust and moisture protection shall meet or exceed IP20 standards.

        - Equipment Cabinet (Enclosure) Construction

          - The tentative quantity of Cabinets has been identified in BoQ and shall be ordered as per requirement.

          - Equipment cabinets shall be steel/ steel & Aluminum extrusion fabricated and finished on all surfaces. All metal and welds shall be thoroughly cleaned and sanded to obtain a smooth finish. All surfaces shall be treated for rust and primed to form a bond between metal and the finish coats of paint.

          - Equipment cabinets shall be designed free-standing but shall be mounted to the floor. Cabinets shall have secured fittings, lockable, full-length front and back doors for access to hardware and wiring. Equipment covers for exposed components mounted inside cabinets are not required unless specifically recommended.

          - All doors and removable panels shall be fitted with long-life rubber beading. All panels shall be fabricated from minimum 2.0mm thickness steel sheet. However, for racks with load bearing Aluminum extrusion frame, door panels and side panels may be fabricated from minimum 1.6mm thickness steel sheet and the top & bottom panels shall be fabricated from minimum 2.0mm thickness steel sheet.

          - Dust and moisture protection shall meet or exceed IP20 standards.

          - Depending upon the thermal engineering of the enclosure (cabinet) and heat load generated from the equipment inside the cabinet, -48V DC powered fan should be provided for cooling. Such fans should be serviceable and replaceable, if required, without disturbing the installed equipment inside the cabinet.

      - Cable Raceways

- The Contractor is required to provide and install all additional necessary cable raceways wherever the same is not available or is not suitable for use. The cable raceways shall be fabricated from construction grade aluminum, galvanized iron or anodized sheet metal or any other suitable material with suitable anti-corrosion measures.  All cable raceways shall be sized to support full loading requirements plus at least a 200% safety loading factor.

    - Inside Plant

For purposes of this specification, Inside Plant is defined to include all fixed earth cable plant and equipment extending inward from. It shall be the Contractor's responsibility to provide all inside plant cable support required for equipment and shall be in accordance with communications industry standard inside plant practices and the requirements below:

      - Inside Plant Cabling

All Contractor supplied inside plant cabling and cable assemblies shall be compliant to relevant IS/IEC standards and shall be constructed from fire/smoke resistant materials as per IEC 332-part 3 or equivalent Indian Standard. All inter-cabinet and intra-cabinet signal cable assemblies shall be shielded from electromagnetic interference. Earth connections to shields shall be kept short or shall be bonded to the connector shell with 360-degree terminations.

      - Signaling Distribution

The Contractor shall be responsible for all signal wiring associated with furnished equipment in accordance with the following:

          - All signal wiring connections to the communications equipment shall be via electrical/ optical cable of appropriate length equipped with necessary connectors.

          - The Contractor shall provide subscriber level wiring and patching wherever required.

    - Station Safety Earthing and Signal Grounding

For each facility, the Contractor is responsible for meeting the following station and equipment earthing requirements:

          - All safety earthing and signal grounding shall be in full compliance with EMI/ EMC requirements as per relevant international/ Indian standards.

          - Each enclosure (rack) or enclosure group shall include suitable signal ground and safety earth networks. The signal ground network shall terminate at a separate signal ground stud connection isolated from safety earth.

          - Each earth/ground network shall utilize copper bus bars, copper braids and/or 16 sqmm or bigger earth cable. All equipment earth/ground connections shall be made directly to the equipment chassis utilizing grounding lugs and secured metal-to-metal with star washers. Use of the enclosure frame, skin or chassis mounting hardware as part of the earthing/ grounding networks, is not acceptable.

          - The safety earth network shall be connected to "earth ground" at the safety earth stud. The earth stud connection shall be sized for an external earthing cable equipped with a 2/0 solid copper lug secured metal-to-metal with star washers. Primary AC feeds and distribution within enclosures, requires earthing wire connection to the safety earth stud.

          - The safety earth and signal ground networks shall be inter-connected only at the safety earth stud and signal ground stud.

At each location, the Employer shall extend the existing station earth to the equipment room.  The Contractor shall be responsible for determining the suitability of existing station earth for the equipment to be supplied under this contract.

The Contractor is responsible for providing all required earthing/grounding cable and installation. Enclosure/rack and equipment safety earthing and signal grounding shall be subject to the Employer’s approval.

    - Interconnections

All power and signal cabling between component units of the communications systems shall be supplied and installed by the Contractor and shall be shown on contractor-supplied as-built drawings.

The Contractor shall supply and install all primary power cords, power strips, receptacles, circuit breakers, fuse panels, switches, surge protectors, distribution cabling, and power connectors required to support all equipment enclosures and system components furnished and installed under this specification, except as specifically excluded.

Plug-type power connectors with captive fastening (such as "Twist-Lock") shall be used for interconnection of source power to the equipment enclosures or racks.

Plug-type connectors with captive fasteners (i.e. DB-25, etc) shall be used for the interconnection of all inter and intra-enclosure signaling cable.

    - Finish Colors

Unless otherwise specified, finish colors for enclosures shall be gloss white enamel on the inside, and semi-gloss medium grey enamel on the outside. However, the Employer reserves the right to approve the proposed color scheme, and bidder has to take prior approval for the coloring scheme before supply of racks. Only brushed aluminum trim shall be used.

  - Location of Equipment, Cable Routes and Associated Civil Works

During the Site Surveys, the Contractor shall determine and propose locations for equipment to be supplied under this contract.  Further, the Contractor shall locate and identify proposed routing for all cabling between all equipment locations including existing and planned equipment not provided under this contract but required to be connected under the scope of this contract. This subsection defines the requirements and clarifies the responsibilities of the Employer and the Contractor regarding equipment sitting, intra and inter facility interconnectivity and necessary associated civil works.

    - Locations for Supplied Equipment

All transmission equipment, the TMN and associated hardware shall be collocated in the same communications room whenever possible.

    - Associated Civil Works

The Contractor shall provide all required minor civil works necessary for full connectivity as required in the Contractor’s scope of work as follows:

All drilling, mounting (including mounting structure for false flooring etc. as per site requirement) and grouting etc. as required for proper installation.

All wall and floor penetrations necessary for the installation of all cabling to be performed in accordance with the requirements of this specification.

Installation of racks, cabinets, cable raceways, and cabling supplied as part of this contract. However, extension of trenches etc. if required for installation of rack shall be carried out by Employer.