Section 5

INSPECTION, TEST and AVAILABILITY

All materials furnished and all work performed under this Contract shall be inspected and tested. Deliverables shall not be shipped until all required inspections and tests have been completed, and all deficiencies have been corrected to comply with this Specification and approved for shipment by the Employer.

Except where otherwise specified, the Contractor shall provide all manpower and materials for tests, including testing facilities, logistics, power and instrumentation, and replacement of damaged parts. The costs shall be borne by the Contractor and shall be deemed to be included in the contract price.

The entire cost of testing for type, factory & site acceptance, functional tests, routine tests, production tests and other test during manufacture & site activities specified herein shall be treated as included in the quoted unit price of materials, except for the expenses of Inspector/Employer’s representative.

Acceptance or waiver of tests shall not relieve the Contractor from the responsibility to furnish material in accordance with the specifications.

All tests shall be witnessed by the Employer and/or its authorized representative (hereinafter referred to as the Employer) unless the Employer authorizes testing to proceed without witness. The Employer representative shall sign the test form indicating approval of successful tests.

Should any inspections or tests indicate that specific item does not meet Specification requirements, the appropriate items shall be replaced, upgraded, or added by the Contractor as necessary to correct the noted deficiencies at no cost to the Employer. After correction of a deficiency, all necessary retests shall be performed to verify the effectiveness of the corrective action.

The Employer reserves the right to require the Contractor to perform, at the Employer's expense, any other reasonable test(s) at the Contractor's premises, on site, or elsewhere in addition to the specified Type, Acceptance, Routine, or Manufacturing tests to assure the Employer of specification compliance.

The Employer also reserves the right to require any retesting of previously approved tests at the Employer's expense.  However, if the retest(s) reveal noncompliance to the specification, the Contractor shall bear the expense for the retesting and remedial action.

  - Inspection

    - Access to the Contractor's facilities during system manufacturing and testing and to any facility where systems/ equipment is being produced/ tested/ integrated for the fibre optic communication network, shall be available to the Employer. At all times the Employer shall have full facilities for unrestricted inspection of such materials or equipment. To facilitate this, the Contractor shall submit for the Employer approval, a comprehensive Quality Assurance Plan using ISO 9000 as a general guideline. In addition, the Quality Assurance Plan shall satisfy the following:

        - Sufficient office facilities, equipment, and documentation necessary to complete all inspections and to verify that the equipment is being fabricated and maintained in accordance with the Specification shall be provided by the Contractor to the Employer.

        - Inspections to be performed by the Employer will include visual examination of hardware, cable dressings, and labeling. The contractor’s documentation will also be examined to verify that it adequately identifies and describes all offered items.

        - Access to inspect the Contractor's standards, procedures, and records that are applicable to the supplied equipment shall be provided to the Employer. Documents will be inspected to verify that the Contractor has performed the required quality assurance activities.

        - The inspection rights described above shall also apply to subcontractors who are responsible for supplying major components described in this Specification.  These items shall be inspected and tested at the subcontractor’s factory by the Employer's representatives prior to shipping this equipment to the Contractor's facility or directly to the Employer.

        - The above inspection rights shall also apply to subcontractors supplying assemblies, subassemblies and components. However, such items will normally be inspected and tested by the Employer's representatives at the Contractor's site before acceptance.

    - Contractor has to procure bought out items from sub-vendors as per the list in “Compendium of Vendors” available on POWERGRID web-site www.powergrid.in after ensuring compliance to the requirements/conditions mentioned therein.  The contractor has to explore first the possibilities of procuring the bought-out items from POWERGRID approved existing vendors. In case of their unavailability / non-response, Contractor may approach PowerTel for additional sub-vendor. In that case, the assessment report of proposed sub vendor by Contractor along with the enclosures as per Annexure-I shall be submitted within 60 days of the award. The proposal shall be reviewed, and approval will be accorded based on the verification of the document submitted and/or after the physical assessment of the works as the case may be. The physical assessment conducted by PowerTel, if required, shall be on a chargeable basis. Charges shall be as per the PowerTel norms prevailing at that time, which shall be intimated by PowerTel separately. If a proposal for sub-vendor is submitted after 60 days, the contractor’s proposal normally will not be considered for subject NOA/LOA. However, PowerTel may process the case for developing more vendors for referred items, if found relevant. In all cases, the contractor shall ensure that Project activities do not suffer on account of delay in approval/non approval of a new sub-vendor.

    - Annexure II indicates the requirement of approval of MQP (Manufacturing Quality Plan) by PowerTel and Level of inspection envisaged against each item. In this regard PowerTel explained the following: -

Manufacturing Quality Plan (MQP): The Manufacturing Quality Plan (MQP) shall relate to the specific & objective manufacturing practices followed by manufacturer, right from procurement of raw material till final inspection & testing and shall be broadly subdivided as under:

- Raw material / bought out items and components.

- In process inspection and test/checks to establish successful completion/accomplishment of the process.

- Final test/checks in accordance with relevant national / international standards / specifications.

The MQP shall also include process flow chart and list of component manufacturers and shall be generally as per PowerTel format enclosed at Annexure – III and also in line with PowerTel standard MQP

Inspection Levels: For implementation of projects in a time bound manner and to avoid any delay in deputation of PowerTel or its authorized representative, involvement of PowerTel for inspection of various items / equipment will be based on the level below:

Level –I:   Contractor has to raise all inspection calls and review the report of tests carried out by the manufacturer, on his own, as per applicable standards / specification, and submit to concerned PowerTel inspection office. CIP / MICC will be issued by PowerTel based on review of test reports / certificates of manufacturers.

Level – II:  Contractor has to raise all inspection calls and carry out the inspection on behalf of PowerTel on the proposed date of inspection. However, in case PowerTel wishes to associate itself during inspection, the same would be intimated to Contractor and CIP/MICC will be issued by PowerTel. Else, Contractor would submit their witnessed test report / certificates to PowerTel. CIP/MICC will be issued by PowerTel based on review of these test reports / certificates.

Level – III:  Contractor has to raise inspection calls for both, stage (as applicable) & final inspection and carry out the stage inspections on behalf of PowerTel on the proposed date of inspection. However, in case PowerTel wishes to associate itself during stage inspection, the same would be intimated to Contractor and CIP will be issued by PowerTel. Else, Contractor would submit their witnessed test report / certificates of stage inspection after their own review and CIP will be issued by PowerTel based on review of these test reports / certificates. Final inspection will be carried out by PowerTel and CIP/MICC will be issued by PowerTel.

Level – IV:  PowerTel will carry out the inspection for both stage & final inspection and CIP/MICC will be issued by PowerTel.

In case of off-shore supply items/equipment, the inspection & test plan (ITP) is to be submitted for PowerTel’s approval.

    - The procedure for giving inspection call, organization structure, deviation-disposal and documentation requirement as explained above, shall be followed by contractor and submit inspection calls over internet through POWERGRID/ PowerTel website. The required vendor code and password to enable raising inspection call will be furnished to the Contractor within 30 days of award of contract. After raising the inspection calls on the ICMS, Contractor shall then proceed as per the message of that particular call which is available on the message board of ICMS. All inspection calls for overseas material shall be given at least six (6) weeks in advance and for indigenous materials at least four (4) weeks in advance.

    - Contractor has to implement the above inspection levels, particularly for the quality control and inspection at their sub-vendor’s works, they would depute their sufficiently qualified & experienced manpower in their Quality Control and inspection department. Further, to assure quality of construction of Project, Contractor has a separate workforce having appropriate qualification and experience for maintaining quality requirement during construction with applicable FQP (Field Quality Plan).

    - Contractor shall ensure that order for items where MQP is required will be placed only on vendors having valid Manufacturing Quality Plan and where the supplier’s MQP is either not valid or has not been approved by PowerTel, the same shall be generally submitted as per PowerTel format No.MR/QA&I/02 (copy enclosed as Annexure – III) within 60 days from date of LOA. Manufacturing, however, shall be taken up only after approval of MQP by PowerTel.

    - Items not covered under MQPs shall be offered for inspection as per PowerTel LOA/ Technical Specifications/ PowerTel approved data sheets/ PowerTel approved drawings and relevant Indian / International standards. For offshore items, Contractor has to offer the internal test reports of the equipment for review during PowerTel inspection.

    - PowerTel, his duly authorized representative and/or outside   inspection  agency  acting on  behalf  of  the PowerTel  shall have at all reasonable times  access  to   Contractor’s  premises or manufacturer works and shall  have  the power  at all reasonable  times to ensure that proper Quality Management practices / norms are adhered to,  inspect  and  examine the  materials & workmanship of the Works, to carry out Quality/Surveillance  Audit during  manufacture  or erection and if part of  the  Works  is being  manufactured  or assembled at other  premises or works.  Contractor shall obtain permission for the PowerTel and for his duly authorized representative to inspect  as if the items were manufactured or  assembled on  Contractor’s own premises or works.  The item/equipment, if found unsatisfactory with respect to workmanship or material, is liable to be rejected.  The observations for improvements during product/ process inspection by PowerTel shall be recorded in Quality Improvement Register (available & maintained at works) for review & timely compliance of observations.

    - Contractor shall be supplying various items as per requirements of technical specifications and that they have not taken any deviation regarding quality matters, routine and acceptance tests as per specifications except those already discussed and agreed with PowerTel Engineering during post-bid discussions.  Any other deviations regarding Quality matters, routine and acceptance tests, explicit or implicit stand withdrawn.

    - PowerTel reserves the right to witness any or all type tests, acceptance and routine tests specified for which Contractor shall give PowerTel Seven (7)   days written notice of any material being ready for  testing for each stage of testing as   identified  in the approved quality plan as customer inspection  point(CIP) for indigenous  inspections.  All inspection calls for overseas material shall be given at least six (6) weeks in advance. Such tests shall be to Contractor’s account except for the expenses of the Inspection Engineer.  PowerTel, unless witnessing of the tests is waived by PowerTel, will attend such tests within Twenty one (21) days of  the date  of which the equipment is notified as being  ready for  test/inspection, failing which  Contractor  may proceed with the test which shall be deemed to have been made in the Inspector’s presence and he shall  forthwith forward  to  the  Inspector six copies  of  tests,  duly certified. Contractor shall ensure, before   giving notice for type test, that all drawings and quality plans have been got approved.  The equipment shall be dispatched to site only after approval of Routine and Acceptance test results and Issuance of Dispatch Clearance in writing by the PowerTel. CIP/Material Inspection clearance certificate (MICC) shall be issued by PowerTel after inspection of the equipment or review of test reports as applicable.  PowerTel may waive off the presence of PowerTel’s inspecting engineer.  In that case test will be carried out as per approved QP/ITP and test certificate will be furnished by the supplier for approval.  CIP/MICC will be issued only after review and approval of the test reports.

    - Contractor shall generally offer material for inspection as per L2 network approved by PowerTel and not before 30 days from schedule indicated in the L2 network. In case Contractor offers material(s) for inspection prior to 30 days from the scheduled date with necessary approval of PowerTel, PowerTel shall inspect the material and issue CIP only.  However, in such an exceptional case, MICC shall be issued only as per provision of original / revised approved supply schedule.

    - The contractor shall maintain a separate register for all CIP and MICC issued by PowerTel.  For each issue of CIP/MICC a serial number will be given and it shall be recorded by the inspection engineer on CIP clearance/MICC.

    - Contractor shall inspect the material themselves and only after they are fully convinced about the Quality, they shall offer the material for PowerTel inspection and shall also ensure that relevant portion of LOA, approved drawing and data sheets along with applicable Quality Plans, Standards etc. are available at the works of Contractor or their Sub-vendor before the material is offered for inspection.  The contractor shall also ensure availability of Type test approval wherever applicable as per specification/contract.

    - Rework/ Re-engineering, if any, on any equipment shall be carried out only after mutual discussions and in accordance with mutually agreed procedure.   Contractor shall submit Joint Inspection Report of equipment under Re-Work/Re-Engineering along with Procedure for the same to PowerTel for approval, before taking up the Re-Work/Re-Engineering, failing which PowerTel reserves the right to reject the equipment.

    - Contractor has to minimize the number of inspection calls by offering optimum quantities in each inspection call at the respective manufacturer’s works.

    - Contractor shall follow PowerTel approved Field Quality Plan for applicable site activities.

    - Contractor’s onshore material which has been cleared for dispatch after inspection, will be dispatched within 30 days from the date of issuance of CIP and for off shore dispatch of inspected material to be done within 60 days of CIP. Material which is not dispatched within 30 days for onshore and 60 days for offshore will be reoffered for PowerTel inspection. All Test Reports and documents to be submitted in English during final inspection of equipment by PowerTel or as and when required for submission.

    - When the factory tests have been completed at Contractor’s works or  Contractor’s Sub-vendor works,    PowerTel Inspection Engineer(IE) shall issue a certificate to this effect  within fifteen  (15) days after completion of tests but if  the tests  are not witnessed by  PowerTel,  the certificate shall be issued within fifteen (15) days  of receipt  of  Contractor’s  Test  certificate  by  PowerTel.  Failure of PowerTel to issue such a certificate shall not prevent Contractor from proceeding with the Works.  The completion of these tests or the issue of the certificate shall not bind PowerTel to accept the equipment should, it, on further tests after erection, is found not to comply with the Contract.

    - In  all  cases,  where the Contract  provides  for  tests whether at the premises or works of   Contractor or of any  Contractor’s Sub-vendor works,  Contractor, except where  otherwise  specified, shall provide free of charge such  items as labour, materials, electricity, fuel, water,  stores, apparatus and instruments as may be reasonably  demanded by the PowerTel/Inspector or his authorized  representative  to carry out effectively such tests of the  equipment  in  accordance with the Contract  and  shall  give facilities  to the PowerTel or to  his  authorized representative to accomplish testing.

    - The inspection and acceptance by PowerTel and issue of Inspection Certificate thereon shall in no way limit the liabilities and responsibilities of Contractor in respect of the agreed quality assurance program forming a  part of the Contract, or if  such  equipment  is found to be defective at a later stage.

    - PowerTel will have the right of having at his own expenses any other test(s) of reasonable nature carried out at Contractor’s premises or at site or in any  other place  in addition of aforesaid type and routine  tests, to satisfy that the material comply with the  specification.

    - PowerTel reserves the right for getting any field tests conducted on the completely assembled equipment at site.

    - PowerTel reserves the right to increase or decrease their involvement in inspections at Contractor’s Works or at his Sub-vendor’s premises or at PowerTel’s site or at any other place of work based on performance of Contractor/sub vendor.

    - Contractor shall supply all equipment under this package from PowerTel approved manufacturers.

    - Contractor will take all possible steps to avoid transport, storage and erection damages of equipment supplied.

    - Contractor wherever specified in TS commissioning of equipment’s will be carried out by/under the supervision of equipment supplier.

    - In certain cases, where delivery locations are required to be changed during/ after inspection of material due to Telecom Business/ Customer requirement, the dispatch clearance shall be given over email along with the addresses of new delivery locations and contractor shall dispatch the material accordingly. The CIP/ MICC shall be issued subsequently after necessary amendment in CA (changes in ERP) incorporating the changes in quantity of material in PO as per requirement.

  - Test Classifications

    - Type Tests

## Type Tests shall be defined as those tests which are to be carried out to prove the design, process of manufacture and general conformity of the materials to this specification with regard to Environmental and Immunity/Emission perspective. Detailed requirement of Type Testing and equipment on which Type Testing shall be carried out is defined in clause 5.4.

    - Functional Tests (Qualification Tests):

## Functional Tests shall be defined as those tests which are to be carried out to prove the design and functions/ features of the equipment offered in conformity to this specification. Detailed requirement of Functional Testing is provided in clause 5.5.  Functional Testing shall be carried out on all types of equipment to be supplied under the package.

    - Factory Acceptance Tests (FAT):

## Factory Acceptance Tests shall demonstrate the equipment parameters in relation to this specification and approved drawings and documents. Detail requirement of Testing is provided at clause 5.6. Factory Acceptance Testing shall be carried out on all the deliverable items.

    - Site Acceptance Tests (SAT):

## Site Acceptance Tests shall demonstrate that the equipment at site has been installed as per technical specifications, with proper markings etc. to meet the intended performance of the equipment supplied and installed as per Contract including quality of installation and integration with network is satisfactory. Detail requirement of SAT is provided at clause 5.7.

    - Network Security Audit cum Vulnerability Assessment Test

#### Network Security Audit or Vulnerability Assessment (VA) of the completed Network (All equipment, amplifiers, DCN Network, TMN/ NMS etc) shall be done after completion of SAT (SATI, II & III) in line with DoT prevailing policies of Network Security. Further, an adequate solution/ scheme shall be implemented in consultation with PowerTel, to mitigate the vulnerabilities reported in the vulnerability Assessment/ Audit. Brief requirement is provided at clause 5.9, and details shall be finalized during detailed Engineering and/ or before testing.

#### Taking over of Network shall be done by PowerTel after implementation of mitigation plan & Taking Over Certificate (TOC) to be issued to contractor.

  - Test Plans and Procedures

Test plans and test procedures for type, functional, factory and site acceptance tests shall be provided by the Contractor. The Contractor shall submit a Test Schedule for the Employer's approval after the award of contract for Type Tests, Functional Tests Factory Acceptance Tests and Site Acceptance Tests as specified at Appendix-A. The test schedule shall list the tests to be carried out, and the approximate test duration.

The Contractor shall give the Employer twenty-one (21) days written notice of any material being ready for testing.

    - Test Procedures

Type Test Procedure and Functional Test Procedure shall be submitted within three (3) weeks of contract award. Testing shall not commence without approved test procedures.

All test equipment and/or instruments shall bear calibration stickers indicating valid calibration on and beyond the testing date.

The Contractor shall ensure that all testing will be performed by qualified testing personnel well experienced in performing such tests.

    - Test Records

Complete and indexed records of all type tests, functional, factory and site acceptance tests results shall be maintained and provided to the Employer by the Contractor in Softcopy/ hardcopy. The records shall be keyed to the steps enumerated in the test procedures.

All principal test records, test certificates and performance curves shall be supplied for all tests carried out as proof of compliance with the specifications and/or each and every specified test. These test certificates, records and performance curves shall be supplied for all tests, whether or not they have been witnessed by the Employer.

    - Rejection of Elements

Any item or component which fails to comply with the requirements of this Specification in any respect, at any stage of manufacture, test, erection or on completion at site may be rejected by the Employer either in whole or part as considered necessary.

Material or components with defects of such a nature that do not meet the requirements of the Specification by adjustment or modification shall be replaced by the Contractor at his own expense. After adjustment or modification, the Contractor shall submit the items to the Employer for further inspection and/or tests.

    - Test Periods Defined

The terminology used in Volume I, General Conditions of Contract and their correlation with the tests requirements described within this section is as follows:

Pre-Commissioning & Commissioning Period - The Site Acceptance Test (SAT)

Operational Acceptance - Successful completion of Site Acceptance Test (SAT-I, II and III) would be considered for operational acceptance.

  - Type Testing

"Type Tests" shall be defined as those tests which are to be carried out to prove the design, process of manufacture and general conformity of the materials to this Specification. Type Testing shall comply with the following:

        - The Contractor shall submit, within one (1) week of Contract Award, copies of test reports and certificates for all of the Type Tests for all types of offered MPLS-TP Equipment, DCPS & Optical amplifiers etc. Type testing requirement have been specified in clause 5.4.2.

        - The type tests must have previously been performed in the last five years on the equipment which is required to be type tested. These certificates may be accepted by the Employer only if they apply to materials and equipment that are essentially identical to those due to be delivered under the Contract and only if test procedures and parameter values are identical to those specified in this specifications. Further, earlier type tests must have been carried out in third party accredited laboratories and/or witnessed by third party/ customer. MTCTE certificate is also acceptable for EMI/EMC type testing requirements of offered telecom Equipment. However, the bidder has to submit the certificate for environmental & mechanical tests are per the requirement mentioned in this document. For DCPS bidder must submit the Type Test certificate as per the TEC GR TEC/GR/FA/SMP-001/07/MAR-17 and latest release and amendments.

        - Type Tests shall be performed by the contractor at no additional cost to Employer for equipment types as identified above for which certification is not provided as required in (a) above, or if it is determined by the Employer that the certification provided is not acceptable.

        - Type Tests shall be certified or performed by internationally reputed laboratories using material and equipment data sheets and test procedures that have been approved by the Employer. The test procedures shall include a complete list of the applicable reference standards.

        - The Contractor shall provide a detailed schedule for performing all specified type tests. These tests shall be performed in the presence of a representative of the Employer, if desired so.

The Contractor shall ensure that all type tests can be completed within the time schedule offered in their Technical Proposal.

In case of failure during any type test, the Supplier is either required to manufacture a fresh sample lot and repeat all type tests successfully or repeat that particular type tests at least three times successfully on the samples selected from the already manufactured lot at their own expenses. In case a fresh lot is manufactured for testing then the lot already manufactured shall be rejected.

In order to expedite equipment delivery in stipulated time schedule, the equipment may require to be shipped and installed at site before the completion of type testing.  However, if the type testing does not pass successfully, the required modification shall be done by the Contractor in already delivered equipment at no additional cost to Employer.

    - Type Test Samples

The Contractor shall supply equipment/material for sample selection only after the Quality Assurance Plan has been approved by the Employer. The sample material shall be manufactured strictly in accordance with the approved Quality Assurance Plan. The Contractor shall submit for Employer approval, the type test sample selection procedure. The selection process for conducting the type tests shall ensure that samples are selected at random. At least three samples of the proposed equipment shall be offered for selection, of which one sample shall be selected.

    - List of Type Tests

| ### Type test | ### MPLS-TP and Optical Amplifiers | ### DCPS |
| --- | --- | --- |
| ### EMI/EMC | ### As per MTCTE Essential Requirement: ER No. TEC37942403 or latest if any | ### TEC GR TEC/GR/FA/SMP-001/07/MAR-17 and latest release and amendments if any |
| ### Environmental | ### QM-333 March 2010 latest release and amendments if any ### Category B2 | ### QM-333 March 2010 latest release and amendments if any ### Category B2 |
| ### Mechanical | ### Vibration: 60068-2-6 ### Shock: 60068-2-27 ### Free Fall: 60068-2-32 ### Bump Test: 60068-2-29 | ### Not Applicable |

  - Functional Tests

## Functional Tests shall be required to be conducted on all types of Equipment offered under the Package. The comprehensive test plan will be finalized with the successful bidder during detailed engineering. The test plan under Functional Test shall cover all aspects of features and functions described in Chapter-2 and requirement specified in BOQ.

## PowerTel reserves the right to add new tests or modify the test(s) to check the functionality of the equipment/ system, if required.

## Necessary tests to assess the Performance of Long link amplifier solution with different Span loss as specified in BoQ shall also be demonstrated.

In order to expedite equipment delivery in stipulated time schedule, the equipment may require to be shipped and installed at site at the risk & cost of contractor before the completion of functional testing.  However, if the functional testing does not pass successfully, the required modification shall be done by the Contractor in already delivered equipment at no additional cost to Employer.

  - Factory Acceptance Tests

Factory acceptance tests shall be conducted on randomly selected final assemblies of all equipment to be supplied. Factory acceptance testing shall be carried out on Equipment and associated subsystems.

Equipment shall not be shipped to the Employer until required factory tests are completed satisfactorily, all variances are resolved, full test documentation has been delivered to the Employer, and the Employer has issued Material Inspection & Clearance Certificate (MICC). Successful completion of the factory tests and the Employer approval to ship, shall in no way constitute final acceptance of the system or any portion thereof. These tests shall be carried out in the presence of the Employer's authorized representatives.

Factory acceptance tests shall not proceed without the prior delivery to and approval of all test documentation (Section 5.3) by the Employer.

The factory acceptance test shall demonstrate the technical characteristics of the equipment in relation to these specifications and approved drawings and documents. The comprehensive test plan will be finalized with the successful bidder during detailed engineering. A list of factory acceptance tests for equipment is given in Table 5-1(Telecom equipment) and Table 5-2(DCPS). This list of factory acceptance tests shall be supplemented by the Contractor's standard FAT testing program. The factory acceptance tests for the other items shall be proposed by the Contractor in accordance with technical specifications and Contractor's (including Sub-Contractor's / supplier's) standard FAT testing program.

| Table 5-1: (Telecom Equipment): Factory Acceptance Testing |  |
| --- | --- |
| Item | Description: |
| 1. | Physical inspection for conformance to drawings and appearance of equipment including verification of identification a per Section 4.3.1 Identification |
| 2. | Optical output power |
| 3. | Transmitter light wave spectral analysis |
| 4. | Low receive level threshold |
| 5. | Measurement of residual bit error rate |
| 6. | Output and input jitter, bit error rate and line rate tolerance |
| 7. | Simulation of failure conditions and failover of each redundant unit. |
| 8. | Checks of power supply/converter voltage margins, ripple levels, noise rejection, and short circuit and overvoltage protection |
| 9. | Random inspections to verify the accuracy of documentation |
|  | -End of Table- |

TMN functions and features as per Section-3 shall be included in the FAT for TMN system.

| Table 5-2 (DCPS): Factory Acceptance Testing |  |
| --- | --- |
| Item | Description: |
| 1. | Physical inspection for conformance to drawings and appearance of equipment including verification of identification a per Section 4.3.1 Identification |
| 2. | Visual Inspection of modular based design on SMPS as per approved drawing |
| 3. | Input AC range |
| 4. | DC Output Voltage: -48V (Nominal), -48V to -56V |
| 5. | SMR Module, Hot Plug-in |
| 6. | Load and line regulation |
| 7. | Check the ripple factor |
| 8. | Efficiency |
| 9. | Short circuit protection |
| 10. | System overload test |
| 11. | Output voltage, load current |
| 12. | Checking of LED for SMR fail, Mains healthy |
| 13. | Lord sharing on the DCPS |
|  | -End of Table- |

    - Sampling for FAT

From each Lot of equipment presented by the Contractor for Factory acceptance testing, the Employer shall select random sample(s) to be tested for acceptance. Unless otherwise agreed, all required FAT tests in the approved FAT procedures shall be performed on all samples. The Sampling rate for the Factory acceptance tests shall be 10% of the Lot size (minimum 1) for all items.  In case any of the selected samples fail, the failed sample is rejected and an additional 20% samples shall be selected randomly and tested.  In case any sample from the additional 20% also fails the entire Lot may be rejected.

Since FAT testing provides a measure of assurance that the Quality Control objectives are being met during all phases of production, the Employer reserves the right to require the Contractor to investigate and report on the cause of FAT failures and to suspend further testing/ approvals until such a report is made and remedial actions taken, as applicable.

  - Site Acceptance Tests for Telecom equipment

The Contractor shall be responsible for the submission of all equipment supplied in this contract for site tests and inspection as required by the Employer. All equipment shall be tested on site under the conditions in which it will normally operate.

The tests shall demonstrate that the overall performance of the contract works satisfies every requirement specified. A minimum Site Acceptance Testing requirement for equipment is outlined in the following section. This testing shall be supplemented by the Contractor's standard installation testing program, which shall be in accordance with their quality plan(s) for equipment installation.

During the course of installation, the Employer shall have full access for inspection and verification of the progress of the work and for checking workmanship and accuracy, as may be required. On completion of the work prior to commissioning, all equipment shall be tested to the satisfaction of the Employer to demonstrate that it is entirely suitable for commercial operation.

    - Phases of Site Acceptance Testing

The SAT shall be completed in following phases:

      - Installation Testing (SAT-I)

The field installation test shall be performed for all equipment at each location. If any equipment has been damaged or for any reason does not comply with this Specification, the Contractor shall provide and install replacement parts at its own cost and expense. The minimal installation testing requirements for the Equipment are provided in Table 5-3.

| Table 5-3: Installation Testing (SAT-I) |  |
| --- | --- |
| Item | Description: |
| 1. | Physical Inspection for conformance to drawings, rack elevations and appearance of equipment and cabling. |
| 2. | Taping/ connection of Equipment with Power Source |
| 3. | Power ON of all modules |
| 4. | Correct configuration, level setting & adjustments and termination of Input/ output interfaces |
| 5. | Proper establishment of Safety and signalling earthing system and resistance to ground to be checked. |
|  | End of Table |

In case, a link is handed over to customer without conducting/ witnessing Installation test to meet urgent requirement of customer and link/ service configured/ passing through that equipment is accepted by customer (Commercial acceptance by customer), the ‘Installation testing (SAT-I)’ deemed to be considered completed and no separate testing will be required.

The minimal installation testing requirements for TMN are provided in Table 5-4.

| Table 5-4 TMN Installation Testing |  |
| --- | --- |
| Item | Description: |
| 1. | Physical inspection for rack elevations and appearance of equipment and cabling |
| 2. | Power supply/converter/UPS connections |
| 3. | Workstation hardware inventory, configuration, and characteristics |
| 4. | Demonstration of proper operation of all hardware, including workstations peripherals |
| --End of Table-- |  |

      - Link Commissioning Tests (SAT-II)

The commissioning tests shall verify that communication can be performed over the fiber optic link under test. During this test, BER Test, RFC2544, Y.1564, Switching test etc shall be made on the fibre optic to verify compliance with designed link performance as per Sec-2 (Link Performance). PowerTel reserves the right to include test(s) to check the performance of link(s) in field to its satisfaction or satisfy customer’s expectations.

Each link (Backbone as well as access) shall be tested for 24 hours covering the equipment(s) under test. In case any link does not meet the performance requirements during 24 hours, then the cause of failure shall be investigated and the test shall be repeated after rectifying the defects. The outages or errors resulting from faults in Fibre Optic Cabling system, or any other equipment not provided by the Contractor shall not be included in the availability calculations. In case, a link is handed over to customer without conducting ‘Link Commissioning test’ to meet urgent requirement of customer and link/ service configured/ passing through that route/ link accepted by customer (Commercial acceptance by customer), ‘Link Commissioning test’ deemed to be considered completed and no separate testing will be required.

This phase of testing shall be conducted by the Contractor and witnessed by the Employer. Field adjustments shall be made to meet established standards, however, if the field adjustments fail to correct the defects the equipment(s) may be returned to the Contractor for replacement at his own expense. In case any adjustments are required to be made during the interval of the test then the test shall be repeated.

      - Integrated Testing (SAT-III)

The intent of integrated testing is to demonstrate that the equipment is operational end to end under actual conditions, that all variances identified during factory and field installation and communications testing have been corrected, and that the communication equipment is compatible with other equipment at all locations. The Integrated System Test shall include all equipment and the network management system. Conditional Taking over Certificate (TOC) will be issued by PowerTel pending Network Security audit.

At a minimum the following tests shall be included in the integrated testing:

          - Installation testing for TMN as per tables 5-3.

          - End to End testing of all channels provided for TMN systems to demonstrate proper operation of channels over the network. Operation shall be checked in terms of monitoring of BER.

          - Testing of TMN to demonstrate proper operation of all functions: Configuration Management, Performance Management, Fault Management, Inventory Management, Software Management and Security management. All the standard features of the TMN including DCN network shall be demonstrated for proper functioning.

          - DCN Failover testing.

          - DC failover and DR takeover testing

          - Testing of Automatic syncing of Network Database

          - Measurement of response time for TMN operations.

          - Equipment configuration shall be checked.

          - End to End testing of all types of configured Circuits at E1/ STM-1/GbE/10GbE/100GbElevel. Operation shall be checked in terms of monitoring of BER and Packet loss, throughput, latency for Ethernet.

          - Demonstration of Protection switching.

  - Site Acceptance Test for DCPS

The field installation test shall be performed for all DCPS in each location. If any equipment has been damaged or for any reason does not comply with this Specification, the Contractor shall provide and install replacement parts at its own cost and expense. The minimal installation testing requirements for the Equipment are provided in Table 5-5.

| Table 5-5(DCPS-SAT) |  |  |
| --- | --- | --- |
| 1.Site Installation |  |  |
| 1.1 | DCPS installation, commissioning & integration as per approved site layout |  |
| 1.2 | Cable Routing & connection | …… Mtr (Specify length) |
| 1.3 | Labelling done at all end points of cable |  |
| 1.4 | Alarm indication and verification |  |
| 2.SWITCH ON TEST |  |  |
| 2.1 | Make all external connections to the system including load, battery, mains inputs etc. |  |
| 2.2 | Plug in controller Module |  |
| 2.3 | System shall turn ON; Alarm Module shall also turn ON. Panel meter on Alarm shall read the System voltage. | System controller should turn ON |
| 2.4 | Insert Rectifier modules and turn on the system's main MCB. |  |
| 2.5 | Configure the system settings by Controller |  |
| 2.6 | All component of System works smoothly |  |
| ---END OF TABLE--- |  |  |

  - Network Security Audit cum Vulnerability Assessment Test

#### Network Security Audit or Vulnerability Assessment (VA) of the whole Network (All equipment, amplifiers, DCN Network, TMN/ NMS etc) shall be done after completion of SAT-III. The report of the Audit/ Test along with mitigation plan shall be submitted to PowerTel. Further, an adequate solution/ scheme shall be implemented in consultation with PowerTel, to mitigate the vulnerabilities reported in the vulnerability Assessment/ Audit. The network shall be accepted by PowerTel after implementation of mitigation plan & Taking Over Certificate (TOC) to be issued to contractor.

#### Contractor shall conduct network security audit for complete network including NOC through CERT-In (the Indian Computer Emergency Response Team) empaneled parties before final Taking over of the Network/ Project by Employer and issuance of final Taking over Certificate (TOC). If the bidder itself is a CERT empaneled vendor, it still can’t perform the audit by itself. The purpose of this audit is to assess the network vulnerability and implement corrective schemes to avoid unauthorized access or alien intrusion (broadly cyber-attacks). The network audit/ Test shall be performed satisfying the Network Security guidelines issued by DOT.

# Annexure-I

# Page 1 of 1

Assessment report from Contractor for proposed sub-vendor’s along with following enclosures (to the extent available):

- Registration / License of the works

- Organization chart with name and qualification of key persons

- List of Plant and Machinery.

- List of testing equipment with their calibration status.

- List of Raw material, bought out items with sourcing details

- List of out-sourced services with sourcing details.

- List of supply in last three years.

- Third party approval, if any (viz. ISO, BIS),

- Pollution clearance wherever applicable

- Energy Conservation & Efficiency report

(Applicable to industries having contract load more than 100 KVA)

- Formats for RM, in process and acceptance testing

- Type test approvals conducted in last 5 years, if applicable

- Performance Certificates from customers

- Photographs of factory, plant and machinery & testing facilities

Annexure-II

# Page 1 of 1

# MQP & INSPECTION LEVEL REQUIREMENT

| Sl. No. | Item / Equipment | Requirement of MQP | Inspection Level |
| --- | --- | --- | --- |
| 1 | Equipment Cabinet | Yes (PGTS) | II |
| 2 | Power Cables | Yes (PGTS) | II |
| 3 | Mux/ Demux | Yes (PGTS) | II |
| 4 | DCPS | Yes (PGTS) | II |
| 5 | MPLS-TP Equipment | Yes (FAT/ ITP) | IV |
| 6 | NMS/ TMN | Yes (FAT/ ITP) | IV |
| 7 | Optical Amplifiers | Yes (FAT/ ITP) | IV |

# Annexure – III (Page 1 of 2)

|  |  | MANUFACTURING QUALITY PLAN |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Manufacturers Details (Name, Works Address etc.) | Customer |  | Vendor's Code: | Item: | Q.P. No. |  |  |  | Valid From: |  |  |  |
|  |  | PowerTel |  |  |  | Rev. No. |  |  |  | Valid Upto: |  |  |  |
|  |  |  |  |  |  | Date: |  |  |  |  |  |  |  |
| Sr. | Components / Operations & Description of Test | Type of check | Quantum of Check / Sampling with basis | Reference document for Testing | Acceptance Norms | Format of Record | Applicable Codes |  |  |  |  |  | Remarks |
| No. |  |  |  |  |  |  | 1 | 2 | 3 | 4 | 5 | 6 |  |
| A. Section RAW MATERIAL INSPECTION |  |  |  |  |  |  |  |  |  |  |  |  |  |
| B. Section : IN PROCESS INSPECTION |  |  |  |  |  |  |  |  |  |  |  |  |  |
| C. Section: FINAL TESTING |  |  |  |  |  |  |  |  |  |  |  |  |  |

# Annexure – III ((Page 2 of 2)

| MANUFACTURING QUALITY PLAN |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Customer |  | Vendor's Code: | Item: | Q.P. No. |  |  |  | Valid From: |  |  |  |
|  |  | PowerTel |  |  |  | Rev. No. |  |  |  | Valid Upto: |  |  |  |
|  |  |  |  |  |  | Date: |  |  |  |  |  |  |  |
| Code 1 | Indicates place where testing is planned to be performed i.e. Inspection location |  |  | Code 2 | Indicates who has to perform the tests i.e. Testing Agency |  |  |  |  |  |  |  |  |
| A | At Equipment Manufacturer's works |  |  | J | The Equipment Manufacturer |  |  |  |  |  |  |  |  |
| B | At Component Manufacturer's works |  |  | K | The Component Manufacturer |  |  |  |  |  |  |  |  |
| C | At Authorized Distributor's place |  |  | L | The Third Party |  |  |  |  |  |  |  |  |
| D | At Independent Lab |  |  | M | The Turnkey Contractor |  |  |  |  |  |  |  |  |
| E | At Turnkey Contract’s location |  |  |  |  |  |  |  |  |  |  |  |  |
| F | Not specified |  |  |  |  |  |  |  |  |  |  |  |  |
| Code 3 | Indicates who shall witness the tests i.e. Witnessing Agency |  |  | Code 4 | Review of Test Reports/Certificates |  |  |  |  |  |  |  |  |
| P | Component Manufacturer itself |  |  | W | By Equipment manufacturer during raw material / bought out component inspection |  |  |  |  |  |  |  |  |
| Q | Component Manufacturer and Equipment Manufacturer |  |  | X | By Contractor during product/process inspection |  |  |  |  |  |  |  |  |
| R | Component Manufacturer, Equipment Manufacturer and Contractor |  |  | Y | By PowerTel during product/process inspection |  |  |  |  |  |  |  |  |
| S | Equipment Manufacturer itself |  |  | Z | By Contractor and/or PowerTel during product/process inspection |  |  |  |  |  |  |  |  |
| T | Equipment Manufacturer and Contractor |  |  |  |  |  |  |  |  |  |  |  |  |
| U | Equipment Manufacturer, Contractor and PowerTel |  |  |  |  |  |  |  |  |  |  |  |  |
| V | Third Party itself |  |  |  |  |  |  |  |  |  |  |  |  |
| Code 5 | Whether specific approval of sub-vendor / Component make is envisaged? |  |  | Code 6 | Whether test records required to be submitted after final inspection for issuance of CIP/MICC |  |  |  |  |  |  |  |  |
| E | Envisaged |  |  | Y | Yes |  |  |  |  |  |  |  |  |
| N | Not Envisaged |  |  | N | No |  |  |  |  |  |  |  |  |

--- End of Vol II Section 5 ---