| Sl. No | Clause Ref. No. | Existing provision | Bidder’s Query | POWERGRID Clarification |
| --- | --- | --- | --- | --- |
|  | Schedule-I & II of the BPS {Volume-III of the bidding documents} & SECTION-VIII of the Technical Specification {Volume-II of the bidding documents} | TW10B S/C on D/C Rilo - Sagalee Sl. No; Service code; Description; Unit; Qty. 18; 1000033771; 90KN COMPOSITE INSULATOR FOR 132KV WITH LENGTH 1595MM; SET; 62. Sl. No; Service code; Description; Unit; Qty. 20; 1000033771; 90KN COMPOSITE INSULATOR FOR 132KV WITH LENGTH 1595MM; SET; 1545. TW12B S/C on D/C Nahar'n - Geru'kh Section-VIII Annexure-B | Kindly clarify the applicable insulator length to be considered for bidding purposes. We request you to kindly provide the above clarifications at the earliest to enable us to submit a technically compliant bid. Thanking you in anticipation of your kind response. | Bidder to quote as per the BPS & Annexure - B of Section-VIII of the Technical Specification except nominal length which shall be as per BPS. Further, Bidder may refer to the Clause 4.1.1 of Section-VIII of the Technical Specification for type testing requirements due to elevated altitude of the line. |