## summ (hidden)
Summary for Deviation w.r.t. proposed cost
Sl. No | DSR 2023 Item no | Description of Item | Unit | Proposed Qty | Rev Quantity
12 |  | Centering and shuttering including strutting, propping etc. and removal of form work for :
i | 5.9.1 | Foundations, footings, bases for columns. | Sqm | 1056.99 | 316.1435
ii | 5.9.5 | Lintels, beams, plinth beams, girders, bressumers and cantilevers | Sqm | 0 | 292.0203
iii | 5.9.6 | Columns, Pillars, Piers, Abutments, Posts and Struts | Sqm | 0 | 448.8305
14 | 13.1.2 | 12 mm cement plaster of mix : 1:6 (1 cement: 6 fine sand) | Sqm | 336.62 | 347.931
15 | 13.2.2 | 15 mm cement plaster on the rough side of single or half brick wall of mix : 1:6 (1 cement: 6 fine sand) | Sqm | 375.3 | 407.7705
18 | 5.22.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto & above plinth level. Thermo-Mechanically Treated bars of grade Fe-500D or more. | Kg | 9967.63 | 10726.0027
19 | 10.2 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | Kg | 8038.77 | 8488.6248
20 | 13.61.1 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade : Two or more coats on new work | Sqm | 263.55 | 245.0213
21 | 13.46.1 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including priming coat of exterior primer applied @ 0.90 litre/10 sqm) | Sqm | 711.91 | 755.7015
29 | 15.19 | Dismantling steel work manually/ by mechanical means in built up sections without dismembering and stacking within 50 metres lead as per direction of Engineer-in-charge. | Kg | 0 | 179.775
30 | 10.2 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete (excluding supply). | Kg | 0 | 179.775

## BOQ
BOQ for reapiring of damaged Boundary Wall at Mathabhanga Earth Electrode Station
Sl. No | DSR 2023 Item no | Description of Item | Unit | Quantity | DSR'23 Rate | Rate Excluding GST | Amount Excluding GST | Remarks
A | B | B | C | D | F | E | F | J
1 | 14.23 | Pumping out water caused by springs, tidal or river seepage, broken water mains or drains and the like. | Kltr | 1920.5 | 231.05 | To be quoted in SRM | To be quoted in SRM
2 | 15.40.2 | Dismantling precast concrete or stone slabs in walls, partition walls etc. including stacking within 50 metres lead : Thickness above 40 mm up to 75 mm and precast column all as per direction of Engineer in Charge | Sqm | 688 | 433.55 | To be quoted in SRM | To be quoted in SRM
3 | 2.25A | Excavating, supplying and filling of local earth (including royalty) by mechanical transport up to a lead of 5 km, also including ramming and watering of the earth in layers not exceeding 20 cm in trenches, plinth, sides of foundation etc., complete. | Cum | 2857.925 | 700.5 | To be quoted in SRM | To be quoted in SRM
4 | 2.6.1 | Earth work in excavation by mechanical means (Hydraulic excavator)/ manual means over areas (exceeding 30 cm in depth, 1.5 m in width aswell as 10 sqm on plan) including getting out and disposal of excavated earth lead upto 50 m and lift upto 1.5 m, as directed by EIC. All kinds of soil | Cum | 161.0888 | 177.5 | To be quoted in SRM | To be quoted in SRM
5 | 2.10.1.3 | Excavating trenches of required width for pipes, cables, circular columns etc including excavation for sockets, and dressing of sides, ramming of bottoms, depth up to 1.5 m, including getting out the excavated soil, and then returning the soil as required, in layers not exceeding 20 cm in depth, including consolidating each deposited layer by ramming, watering, etc. and disposing of surplus excavated soil as directed, within a lead of 50 m : Pipes, cables,columns etc. exceeding 300 mm dia but not exceeding 600 mm. | Metre | 56 | 549.75 | To be quoted in SRM | To be quoted in SRM | For tilted portion
6 | 2.25 | Filling available excavated earth (excluding rock) in trenches, plinth, sides of foundations etc. in layers not exceeding 20cm in depth, consolidating each deposited layer by ramming and watering, lead up to 50 m and lift up to 1.5 m. | Cum | 54.1323 | 196 | To be quoted in SRM | To be quoted in SRM
7 | 4.1.8 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:4:8 (1 Cement : 4 coarse sand (zone-III) derived from natural sources : 8 graded stone aggregate 40 mm nominal size derived from natural sources). | Cum | 64.3195 | 6812 | To be quoted in SRM | To be quoted in SRM
8 | 4.1.3 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:2:4 (1 cement : 2 coarse sand(zone-III) derived from natural sources : 4 graded stone aggregate 20 mm nominal size derived from natural sources) | Cum | 24.0078 | 7878.5 | To be quoted in SRM | To be quoted in SRM
9 | 4.1.5 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : 1:3:6 (1 Cement : 3 coarse sand(zone-III) derived from natural sources : 6 graded stone aggregate 20 mm nominal size derived from natural sources). | Cum | 9.9106 | 7294.7 | To be quoted in SRM | To be quoted in SRM
10 | 5.1.2 | Providing and laying in position specified grade of reinforced cementconcrete, excluding the cost of centering, shuttering, finishing and reinforcement - All work up to plinth level : 1:1.5:3 (1 cement : 1.5 coarse sand (zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources) | Cum | 82.7752 | 9045.75 | To be quoted in SRM | To be quoted in SRM
11 | 5.2.2 | Reinforced cement concrete work in walls (any thickness), including attached pilasters, buttresses, plinth and string courses, fillets, columns, pillars, piers, abutments, posts and struts etc. above plinth level up to floor five level, excluding cost of centering, shuttering, finishing and reinforcement : 1:1.5:3 (1 cement : 1.5 coarse sand(zone-III) derived from natural sources : 3 graded stone aggregate 20 mm nominal size derived from natural sources) | Cum | 15.2766 | 10852.95 | To be quoted in SRM | To be quoted in SRM
12 |  | Centering and shuttering including strutting, propping etc. and removal of form work for : |  |  |  | To be quoted in SRM | To be quoted in SRM
i | 5.9.1 | Foundations, footings, bases for columns. | Sqm | 316.1435 | 392.15 | To be quoted in SRM | To be quoted in SRM | Separate item added below
ii | 5.9.5 | Lintels, beams, plinth beams, girders, bressumers and cantilevers | Sqm | 292.0203 | 736.4 | To be quoted in SRM | To be quoted in SRM
iii | 5.9.6 | Columns, Pillars, Piers, Abutments, Posts and Struts | Sqm | 554.4286 | 961.3 | To be quoted in SRM | To be quoted in SRM
iv. | 5.9.14 | Extra for shuttering in circular work (20% of respective centering and shuttering items) | Sqm | 105.5981 | 192.26 | To be quoted in SRM | To be quoted in SRM | 20% rate of above item
13 | 6.4.2 | Brick work with common burnt clay F.P.S. (non modular) bricks of class designation 7.5 in superstructure above plinth level up to floor V level in all shapes and sizes in : Cement mortar 1:6 (1 cement : 6 coarse sand) | Cum | 54.1445 | 9105.95 | To be quoted in SRM | To be quoted in SRM | item & rate revised as per dwg B/w 1:6 in place of 1:4
14 | 13.1.2 | 12 mm cement plaster of mix : 1:6 (1 cement: 6 fine sand) | Sqm | 347.931 | 333.35 | To be quoted in SRM | To be quoted in SRM
15 | 13.2.2 | 15 mm cement plaster on the rough side of single or half brick wall of mix : 1:6 (1 cement: 6 fine sand) | Sqm | 407.7705 | 383 | To be quoted in SRM | To be quoted in SRM
16 | 26.77.3 | Erection & Installation of Precast/Prestressed Concrete elements in correct & final position with proper line level and plumb at site making all arrangements (i.e cranes, push-pull jacks & all another T & P for lifting Placing & Alignment of elements, within erection tolerance as per IS 15916 as per approved shop drawings and all complete as per the direction of Engineer-in-Charge but excluding the cost of sim pads, non shrink grout and steel works i.e hangers. All work up to fifth floor. Solid concrete wall elements | Cum | 23.9117 | 2720.3 | To be quoted in SRM | To be quoted in SRM
17 | Rate Analysis | Fabrication and manufacturing of solid precast concrete element with provisions of shear keys, connecting loops, dowel tubes and proper lifting accessories for walls, beams, slabs, stairs, column etc, of various thickness, shape and size of different concrete grades manufactured in controlled factory environment with approved methodology including moulds (Pallet system, Tilts form, table moulds, battery moulds, vertical moulds, beam moulds, column moulds, staircase moulds, Facade mould, etc.), mixing, transporting and placing of concrete, vibrating, curing, finishing, making necessary cutout/holes of required sizes for services, yard handling & stacking all complete as per IS 11447:1985 and as per approved shop drawings and as per the direction of Engineer-in-Charge (Cost of reinforcement, Mechanical, Electrical and Plumbing inserts will be paid separately). Concrete grade M-20 (Cast In Situ) | Cum | 9.9617 | 19124.59 | To be quoted in SRM | To be quoted in SRM | Derived from DAR'23 Item no 26.74.1
18 | 5.22.6 | Steel reinforcement for R.C.C. work including straightening, cutting, bending, placing in position and binding all complete upto & above plinth level. Thermo-Mechanically Treated bars of grade Fe-500D or more. | Kg | 10726.0027 | 107.85 | To be quoted in SRM | To be quoted in SRM
19 | 10.2 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | Kg | 8488.6248 | 133.7 | To be quoted in SRM | To be quoted in SRM
20 | 13.61.1 | Painting with synthetic enamel paint of approved brand and manufacture to give an even shade : Two or more coats on new work | Sqm | 245.0213 | 155.9 | To be quoted in SRM | To be quoted in SRM
21 | 13.46.1 | Finishing walls with Acrylic Smooth exterior paint of required shade : New work (Two or more coat applied @ 1.67 ltr/10 sqm over and including priming coat of exterior primer applied @ 0.90 litre/10 sqm) | Sqm | 755.7015 | 160.6 | To be quoted in SRM | To be quoted in SRM
22 | 16.11 | Dry stone pitching 22.5 cm thick including supply of stones and preparing surface complete. | Sqm | 225 | 883.15 | To be quoted in SRM | To be quoted in SRM
23 | 13.33.1 | Pointing on stone work with cement mortar 1:3 (1 cement : 3 fine sand) :Flush/ Ruled pointing | Sqm | 225 | 385.4 | To be quoted in SRM | To be quoted in SRM
24 | 16.53 | Providing and fixing concertina coil fencing with punched tape concertina coil 600 mm dia 10 metre openable length ( total length 90 m), having 50 nos rounds per 6 metre length, upto 3 m height of wall with existing angle iron 'Y' shaped placed 2.4m or 3.00 m apart and with 9 horizontal R.B.T. reinforced barbed wire, stud tied with G.I. staples and G.I. clips to retain horizontal, including necessary bolts or G.I. barbed wire tied to angle iron, all complete as per direction of Engineer-in-charge, with reinforced barbed tape(R.B.T.) / Spring core (2.5mm thick) wire of high tensile strength of 165 kg/ sq.mm with tape (0.52 mm thick) and weight 43.478 gm/ metre (cost of M.S. angle, C.C. blocks shall be paid separately) | Metre | 327.5 | 375.8 | To be quoted in SRM | To be quoted in SRM
25 | 15.36 | Dismantling barbed wire or flexible wire rope in fencing including making rolls and stacking within 50 metres lead. | Kg | 54.064 | 36.8 | To be quoted in SRM | To be quoted in SRM
26 | Rate Analysis | Fixing of dismantled concertina coil fencing with punched tape concertina coil 600 mm dia 10 metre openable length ( total length 90 m), having 50 nos rounds per 6 metre length, upto 3 m height of wall with existing angle iron 'Y' shaped placed 2.4m or 3.00 m apart and with 9 horizontal R.B.T. reinforced barbed wire, stud tied with G.I. staples and G.I. clips to retain horizontal, including necessary bolts or G.I. barbed wire tied to angle iron, all complete as per direction of Engineer-in-charge, with reinforced barbed tape(R.B.T.) / Spring core (2.5mm thick) wire of high tensile strength of 165 kg/ sq.mm with tape (0.52 mm thick) and weight 43.478 gm/ metre (cost of M.S. angle, C.C. blocks shall be paid separately) | Metre | 62.5 | 102.6498 | To be quoted in SRM | To be quoted in SRM | Derived from DAR'23 Item no 16.53
27 | 5.3 | Add for plaster drip course/ groove in plastered surface or moulding to R.C.C. projections. | Metre | 1481.84 | 78.4 | To be quoted in SRM | To be quoted in SRM
28 | 15.32 | Demolishing thatch roofing including mats, bamboo, jaffari etc. complete including stacking of serviceable material and disposal of unserviceable material within 50 metres lead. | Sqm | 692.5 | 57.7 | To be quoted in SRM | To be quoted in SRM
29 | 15.19 | Dismantling steel work manually/ by mechanical means in built up sections without dismembering and stacking within 50 metres lead as per direction of Engineer-in-charge. | Kg | 179.775 | 3.85 | To be quoted in SRM | To be quoted in SRM | existing angle section may be reused
30 | 10.2 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete (excluding supply). | Kg | 179.775 | 40.11 | To be quoted in SRM | To be quoted in SRM | 30% of item no 19 considered for erection
TOTAL Excluding GST
TOTAL Including 18% GST

## Measurement Sheet (hidden)
Qty Cal Sheet for reapiring of damaged Boundary Wall at Mathabhanga Earth Electrode Station
Sl. No. | Item Description | Unit | Nos. | Length (m) | Width (m) | Height (m) | Quantity | Remarks
1 | Dewatering from constrcution site | Kltr
| Loc. 1 | Cum | 1 | 21 | 10 | 1 | 210
| Loc. 2 | Cum | 1 | 13 | 10.5 | 1 | 136.5
| Loc. 3 | Cum | 1 | 16 | 13 | 1 | 208
| Loc. 4 | Cum | 1 | 12 | 13 | 1 | 156
| Loc. 6 | Cum | 1 | 40 | 10 | 1 | 400
| Loc. 7 | Cum | 1 | 18 | 10 | 1 | 180
| Loc. 8 | Cum | 1 | 65 | 3 | 1 | 195
| Loc. 9 | Cum | 1 | 7.5 | 18 | 1 | 135
| Loc. 10 | Cum | 1 | 75 | 3 | 1 | 225
| Loc. 11 | Cum | 1 | 12.5 | 6 | 1 | 75
|  |  | Total |  |  |  | 1920.5
| Considering 1Cum =1000Ltr=1Kltr |  | Net Total in Kltr |  |  |  | 1920.5
2 | Removal of existing Precast Panels & Column….... | Sqm
| Loc. 1 |  | 1 | 20 |  | 2 | 40
| Loc. 2 |  | 1 | 12.5 |  | 2 | 25
| Loc. 3 |  | 1 | 12.5 |  | 2 | 25
| Loc. 4 |  | 1 | 10 |  | 2 | 20
| Loc. 5 |  | 1 | 2.5 |  | 2 | 5
| Loc. 6 |  | 1 | 52.5 |  | 2 | 105
| Loc. 7 |  | 1 | 22.5 |  | 2 | 45
| Loc. 8 |  | 1 | 65 |  | 2 | 130
| Loc. 9 |  | 1 | 12.5 |  | 2 | 25
| Loc. 10 |  | 1 | 75 |  | 2 | 150
| Loc. 11 |  | 1 | 12.5 |  | 2 | 25
| For providing Extra Gratings in existing portion |  | 25 | 2.325 |  | 1.6 | 93
|  |  | Total |  |  |  | 688
3 | Soil supply and filling including Compaction | Cum
| Loc. 1 |  | 1 | 21 | 10 | 1.5 | 315
| Loc. 2 |  | 1 | 13 | 10.5 | 1.25 | 170.625
| Road Filling Beside the wall |  | 1 | 20 | 2.5 | 0.3 | 15
| Loc. 3 |  | 1 | 16 | 13 | 1.85 | 384.8
| Loc. 4 |  | 1 | 12 | 13 | 1.5 | 234
| Loc. 6 |  | 1 | 40 | 10 | 1.5 | 600
| Loc. 7 |  | 1 | 18 | 10 | 1.5 | 270
| Loc. 8 |  | 1 | 65 | 3 | 1.3 | 253.5
| Loc. 9 |  | 1 | 7.5 | 18 | 1.5 | 202.5
| Loc. 10 |  | 1 | 75 | 3 | 1.5 | 337.5
| Loc. 11 |  | 1 | 12.5 | 6 | 1 | 75
|  |  | Total |  |  |  | 2857.925
4 | Earth Work in Excavation
for Cast in Situ Column Foundation
| Loc. 1 |  | 11 | 1.85 | 1.35 | 0.5 | 13.7363
| Loc. 2 |  | 8 | 1.85 | 1.35 | 0.75 | 14.985
| Loc. 3 |  | 8 | 1.85 | 1.35 | 0.15 | 2.997
| Loc. 4 |  | 7 | 1.85 | 1.35 | 0.5 | 8.7413
| Loc. 6 except tilted portion |  | 15 | 1.85 | 1.35 | 0.5 | 18.7312
| Loc. 7 |  | 12 | 1.85 | 1.35 | 0.5 | 14.985
| Loc. 8 except tilted portion |  | 19 | 1.85 | 1.35 | 0.7 | 33.2167
| Loc. 9 |  | 8 | 1.85 | 1.35 | 0.5 | 9.99
| Loc. 10 except tilted portion |  | 27 | 1.85 | 1.35 | 0.5 | 33.7163
| Loc. 11 |  | 8 | 1.85 | 1.35 | 0.5 | 9.99
|  |  | Total |  |  |  | 161.0888
5 | Excavation for Bore hole for column fixing | Metre
| For tiltet portion for loc 6, 8, 10 |  | 28 |  |  | 2 | 56
|  |  | Total |  |  |  | 56
6 | Backfilling of soil… | Cum
Footing
| P.C.C Portion |  | 123 | 0.3 | 0.3 | 0.075 | 0.83025
| R.C.C Portion |  | 123 | 0.45 | 0.45 | 0.25 | 6.2269
| Column portion below excavation |  | 123 | 1.62 | 1.05 | 0.225 | 47.0752
|  |  | Total |  |  |  | 54.1323
7 | P.C.C 1:4:8 | Cum
| Below Column Footing |  | 123 | 1.55 | 1.05 | 0.075 | 15.0137
Below Bottom Beam
| Loc. 1 |  | 1 | 17.47 | 0.45 | 0.075 | 0.58961
| Loc. 2 |  | 1 | 10.66 | 0.45 | 0.075 | 0.35978
| Loc. 3 |  | 1 | 10.66 | 0.45 | 0.075 | 0.35978
| Loc. 4 |  | 1 | 8.39 | 0.45 | 0.075 | 0.28316
| Loc. 6 |  | 1 | 26.55 | 0.45 | 0.075 | 0.89606
| Loc. 7 |  | 1 | 19.74 | 0.45 | 0.075 | 0.66622
| Loc. 8 |  | 1 | 35.63 | 0.45 | 0.075 | 1.2025
| Loc. 9 |  | 1 | 10.66 | 0.45 | 0.075 | 0.35978
| Loc. 10 |  | 1 | 53.79 | 0.45 | 0.075 | 1.8154
| Loc. 11 |  | 1 | 10.66 | 0.45 | 0.075 | 0.35978
Cast in Situ Column Foundation
| Loc. 1 |  | 11 | 1.55 | 1.05 | 0.075 | 1.3427
| Loc. 2 |  | 8 | 1.55 | 1.05 | 0.075 | 0.9765
| Loc. 3 |  | 8 | 1.55 | 1.05 | 0.075 | 0.9765
| Loc. 4 |  | 7 | 1.55 | 1.05 | 0.075 | 0.85444
| Loc. 6 |  | 15 | 1.55 | 1.05 | 0.075 | 1.8309
| Loc. 7 |  | 12 | 1.55 | 1.05 | 0.075 | 1.4647
| Loc. 8 |  | 19 | 1.55 | 1.05 | 0.075 | 2.3192
| Loc. 9 |  | 8 | 1.55 | 1.05 | 0.075 | 0.9765
| Loc. 10 |  | 27 | 1.55 | 1.05 | 0.075 | 3.2957
| Loc. 11 |  | 8 | 1.55 | 1.05 | 0.075 | 0.9765
| Near main entrance Gate |  | 1 | 17 | 6 | 0.1 | 10.2
| for approach road portion |  | 1 | 80 | 2.15 | 0.1 | 17.2
|  |  | Total |  |  |  | 64.3195
8 | P.C.C (1:2:4) | Cum
| Cement Coping on Column and Wall |  | 1 | 232.5 | 0.28 | 0.05 | 3.255
| For Fixing gratings |  | 1 | 204.21 | 0.23 | 0.1 | 4.6968
| Precast col groove filling |  | 20 | 0.08 | 0.08 | 1.8 | 0.2304
| Encasing precast columns |  | 28 | 0.2826 |  | 2 | 15.8256
|  |  | Total |  |  |  | 24.0078
9 | 1:3:6 Concrete Encasing……Precast column | Cum
| Column |  | 28 | - | 0.2826 | 2 | 15.8256
| Deduct Column |  | -28 | 0.325 | 0.325 | 2 | -5.915
|  |  | Total |  |  |  | 9.9106
10 | RCC - 1:1.5:3…....upto Plinth Lvl | Cum
| RCC Beam (Top & Bottom) | [6 empty] | span | type |  | col
| Loc. 1 |  | 1 | 17.47 | 0.23 | 0.3 | 1.2054 | 20 | Full span | considered | 11
| Loc. 2 |  | 1 | 10.66 | 0.23 | 0.3 | 0.73554 | 12.5 | Full span | considered | 8
| Loc. 3 |  | 1 | 10.66 | 0.23 | 0.3 | 0.73554 | 12.5 | Full span | considered | 8
| Loc. 4 |  | 1 | 8.39 | 0.23 | 0.3 | 0.57891 | 10 | Full span | considered | 7
| Loc. 6 |  | 1 | 26.55 | 0.23 | 0.3 | 1.832 | 30 | coll span | considered | 15
| Loc. 7 |  | 1 | 19.74 | 0.23 | 0.3 | 1.3621 | 22.5 | Full span | considered | 12
| Loc. 8 |  | 1 | 35.63 | 0.23 | 0.3 | 2.4585 | 40 | coll span | considered | 19
| Loc. 9 |  | 1 | 10.66 | 0.23 | 0.3 | 0.73554 | 12.5 | Full span | considered | 8
| Loc. 10 |  | 1 | 53.79 | 0.23 | 0.3 | 3.7115 | 60 | coll span | considered | 27
| Loc. 11 |  | 1 | 10.66 | 0.23 | 0.3 | 0.73554 | 12.5 | Full span | considered | 8
| Column Footing | [6 empty] | 232.5
| Loc. 1 |  | 11 | 1.4 | 0.9 | 0.25 | 3.465
| Loc. 2 |  | 8 | 1.4 | 0.9 | 0.25 | 2.52
| Loc. 3 |  | 8 | 1.4 | 0.9 | 0.25 | 2.52
| Loc. 4 |  | 7 | 1.4 | 0.9 | 0.25 | 2.205
| Loc. 6 |  | 15 | 1.4 | 0.9 | 0.25 | 4.725
| Loc. 7 |  | 12 | 1.4 | 0.9 | 0.25 | 3.78
| Loc. 8 |  | 19 | 1.4 | 0.9 | 0.25 | 5.985
| Loc. 9 |  | 8 | 1.4 | 0.9 | 0.25 | 2.52
| Loc. 10 |  | 27 | 1.4 | 0.9 | 0.25 | 8.505
| Loc. 11 |  | 8 | 1.4 | 0.9 | 0.25 | 2.52
Column
| Loc. 1 |  | 11 | 0.23 | 0.3 | 1.675 | 1.2713
| Loc. 2 |  | 8 | 0.23 | 0.3 | 1.675 | 0.9246
| Loc. 3 |  | 8 | 0.23 | 0.3 | 1.675 | 0.9246
| Loc. 4 |  | 7 | 0.23 | 0.3 | 1.675 | 0.80902
| Loc. 6 |  | 15 | 0.23 | 0.3 | 1.675 | 1.7336
| Loc. 7 |  | 12 | 0.23 | 0.3 | 1.675 | 1.3869
| Loc. 8 |  | 19 | 0.23 | 0.3 | 1.675 | 2.1959
| Loc. 9 |  | 8 | 0.23 | 0.3 | 1.675 | 0.9246
| Loc. 10 |  | 27 | 0.23 | 0.3 | 1.675 | 3.1205
| Loc. 11 |  | 8 | 0.23 | 0.3 | 1.175 | 0.6486
| Near main entrance Gate for approach road |  | 1 | 80 | 2 | 0.1 | 16
|  |  | Total |  |  |  | 82.7752
11 | RCC - 1:1.5:3…....above Plinth Lvl | Cum
Column
| Loc. 1 |  | 11 | 0.23 | 0.3 | 1.8 | 1.3662
| Loc. 2 |  | 8 | 0.23 | 0.3 | 1.8 | 0.9936
| Loc. 3 |  | 8 | 0.23 | 0.3 | 1.8 | 0.9936
| Loc. 4 |  | 7 | 0.23 | 0.3 | 1.8 | 0.8694
| Loc. 6 |  | 15 | 0.23 | 0.3 | 1.8 | 1.863
| Loc. 7 |  | 12 | 0.23 | 0.3 | 1.8 | 1.4904
| Loc. 8 |  | 19 | 0.23 | 0.3 | 1.8 | 2.3598
| Loc. 9 |  | 8 | 0.23 | 0.3 | 1.8 | 0.9936
| Loc. 10 |  | 27 | 0.23 | 0.3 | 1.8 | 3.3534
| Loc. 11 |  | 8 | 0.23 | 0.3 | 1.8 | 0.9936
|  |  | Total |  |  |  | 15.2766
12 | Centering and Shuttering | Sqm
Below Bottom Beam P.C.C (1:4:8)
| Loc. 1 |  | 2 | 17.47 | - | 0.075 | 2.6205
| Loc. 2 |  | 2 | 10.66 | - | 0.075 | 1.599
| Loc. 3 |  | 2 | 10.66 | - | 0.075 | 1.599
| Loc. 4 |  | 2 | 8.39 | - | 0.075 | 1.2585
| Loc. 6 |  | 2 | 26.55 | - | 0.075 | 3.9825
| Loc. 7 |  | 2 | 19.74 | - | 0.075 | 2.961
| Loc. 8 |  | 2 | 35.63 | - | 0.075 | 5.3445
| Loc. 9 |  | 2 | 10.66 | - | 0.075 | 1.599
| Loc. 10 |  | 2 | 53.79 | - | 0.075 | 8.0685
| Loc. 11 |  | 2 | 10.66 | - | 0.075 | 1.599
P.C.C (1:2:4)
| Cement Coping on Column and Wall |  | 2 | 232.5 | - | 0.05 | 23.25
| For Fixing gratings |  | 2 | 204.21 | - | 0.1 | 40.842
| Cast in Situ Column Footing P.C.C |  | 246 | 1.55 | - | 0.075 | 28.5975
|  |  | 246 | - | 1.05 | 0.075 | 19.3725
| Cast in Situ Column Footing RCC |  | 246 | 1.4 | - | 0.25 | 86.1
|  |  | 246 | - | 0.9 | 0.25 | 55.35
| Cast in Situ Column except Loc 11 |  | 230 | 0.3 | - | 3.475 | 239.775
|  |  | 230 | - | 0.23 | 3.475 | 183.8275
| Cast in Situ Column Loc 11 |  | 16 | 0.3 | - | 2.975 | 14.28
|  |  | 16 | - | 0.23 | 2.975 | 10.948
| Pre fab columns foundation |  | 28 | 1.8857 |  | 2 | 105.5981
| RCC Beam vertical (Top & Bottom of Gratings) |  | 4 | 204.21 | - | 0.3 | 245.052
| Bottom of top beam |  | 1 | 204.21 | 0.23 | - | 46.9683
| for approach road portion PCC & RCC |  | 2 | 80 | - | 0.2 | 32
|  | i | Total |  |  |  | 316.1435
|  | ii | Total |  |  |  | 292.0203
|  | iii | Total |  |  |  | 554.4286
|  | iv | Circular work |  |  |  | 105.5981
13 | Brickwork for Wall | Cum
| B/w column |  | 1 | 188.81 | 0.23 | 1.1 | 47.7689
| Connected with precast col |  | 1 | 15.4 | 0.23 | 1.8 | 6.3756
|  |  | Total |  |  |  | 54.1445
14 | Outside wall Plaster 12mm thk | Sqm
| wall Connected with precast col including coping |  | 1 | 15.4 | - | 1.85 | 28.49
| Intermediate Wall including column |  | 1 | 212.5 | - | 1.45 | 308.125
| Column from GL to top of grating |  | 123 | 0.23 | - | 0.4 | 11.316
|  |  | Total |  |  |  | 347.931
15 | Inside Wall Plaster 15mm thk | Sqm
| wall Connected with precast col including coping |  | 1 | 15.4 |  | 1.85 | 28.49
| Intermediate Wall including column |  | 1 | 212.5 | - | 1.45 | 308.125
| Column Offset |  | 246 | 0.085 |  | 1.85 | 38.6835
| Column face grating side from GL to top of grating |  | 246 | 0.215 | - | 0.4 | 21.156
| Column from GL to top of grating |  | 123 | 0.23 | - | 0.4 | 11.316
|  |  | Total |  |  |  | 407.7705
16 | RCC -1:1.5:3...Precast Panel and Column…..Erection & Installation.. | Cum
| Column |  | 28 | 0.325 | 0.325 | 3.8 | 11.2385
| Deduct Grooves |  | -56 | 0.075 | 0.08 | 3.8 | -1.2768
| Reusable Panels For Tilted area |  | 100 | 2.325 | 0.4 | 0.075 | 6.975
| For providing Extra Gratings in existing portion |  | 100 | 2.325 | 0.4 | 0.075 | 6.975
|  |  | Total |  |  |  | 23.9117
17 | Precast Fabrication and manufacturing…. | Cum
| Column |  | 28 | 0.325 | 0.325 | 3.8 | 11.2385
| Deduct Grooves |  | -56 | 0.075 | 0.08 | 3.8 | -1.2768
|  |  | Total |  |  |  | 9.9617
18 | Reinforcement | Kg
For Cast in Situ
|  |  | Nos | Nos in each |  | Unit Wt.(kg/m)
Column
| Lateral Tie 8dia@190c/c |  | 123 | 19 | 0.9 | 0.395 | 830.8035
| Vertical Bars 6nos @12dia |  | 123 | 6 | 4.095 | 0.88889 | 2686.32
R.C.C Beam (Top & Bottom) from both side of prefab col b/w 2.5m
| Horizontal Bars 4nos @12dia |  | 65 | 4 | 3.25 | 0.88889 | 751.1111
| Stirrups 8dia @200c/c |  | 65 | 14 | 1.02 | 0.39506 | 366.6963
R.C.C Beam (Top & Bottom) from both side of prefab col b/w 1.5m
| Horizontal Bars 4nos @12dia |  | 20 | 4 | 2.25 | 0.88889 | 160
| Stirrups 8dia @200c/c |  | 20 | 9 | 1.02 | 0.39506 | 72.5333
R.C.C Beam (Top & Bottom) from both side of prefab col b/w 1m
| Horizontal Bars 4nos @12dia |  | 20 | 4 | 1.75 | 0.88889 | 124.4444
| Stirrups 8dia @200c/c |  | 20 | 7 | 1.02 | 0.39506 | 56.4148
Raft
| Main bar top & bottom @12dia 200c/c |  | 123 | 12 | 1.6 | 0.89 | 2101.824 | 150 add in each side
| Distribution bar top & bottom @10dia 225c/c |  | 123 | 16 | 1.1 | 0.617 | 1335.6816 | 150 add in each side
| Chair |  | 123 | 4 | 0.75 | 0.617 | 227.673
| Lugs for fixing MS Flat in beam@ 10 dia |  | 341 | 1 | 0.62 | 0.61728 | 130.5062
| for approach road portion RCC-8dia @300c/c |  | 1 | 7 | 79.9 | 0.395 | 220.9235
| binder -8dia @300c/c |  | 1 | 267 | 1.9 | 0.395 | 200.3835
For Precast Column
| Stirrups 1 - 8dia@200c/c |  | 28 | 20 | 1.63 | 0.39506 | 360.6123
| Stirrups 2 -8dia@200c/c |  | 28 | 20 | 0.71 | 0.39506 | 157.0765
| Vertical Bars 1 - 4nos @12dia |  | 28 | 4 | 3.92 | 0.88889 | 390.2578
| Vertical Bars 2- 8nos @10dia |  | 28 | 8 | 3.92 | 0.61728 | 542.0247
| Lugs for fixing Insert plate@ 10 dia |  | 28 | 1 | 0.62 | 0.61728 | 10.716
|  |  | Total |  |  |  | 10726.0027 | checked upto this row
19 | Structural Steel | Kg |  | Nos |  | Unit Wt.(kg/m)
| M.S Angle- 50x50x6mm for barbed wire fixing on cast in setu column |  | 123 | 1 | 1.475 | 4.5 | 816.4125
| M.S Angle- 50x50x6mm for barbed wire fixing on precast column |  | 28 | 1 | 1.175 | 4.5 | 148.05
Solid Square Bar for gratings @ 20mm
| Vertical Bars @100c/c |  | 65 | 24 | 0.6 | 3.14 | 2939.04
|  |  | 20 | 14 | 0.6 | 3.14 | 527.52
| M.S Flat 75x6 for Grating in cast in setu |  | 65 | 2 | 2.27 | 3.498 | 1032.2598
|  |  | 20 | 2 | 1.27 | 3.5 | 177.8
Solid Square Bar for gratings @ 20mm for Pre cast
| Vertical Bars @100c/c |  | 25 | 23 | 0.4 | 3.14 | 722.2
| M.S Flat 75x6 for Grating |  | 25 | 2 | 2.325 | 3.498 | 406.6425
| Side |  | 25 | 2 | 0.4 | 3.5 | 70
For providing Extra Gratings in existing portion
| Vertical Bars @100c/c |  | 25 | 23 | 0.4 | 3.14 | 722.2
| M.S angle 75x75X6 for Grating |  | 25 | 2 | 2.325 | 6.8 | 790.5 | MS angle in place of 75x6 flat
| Side |  | 25 | 2 | 0.4 | 6.8 | 136
|  |  | Total |  |  |  | 8488.6248
20 | Synthetic Enamel paint | Sqm
| M.S Angle- 50x50x6mm for barbed wire fixing |  | 1 | 214.325 | 0.2 |  | 42.865
| Solid Square Bar for gratings @ 20 |  | 1 | 1564 | 0.08 |  | 125.12
| Gratings (MS Flat 75x6) |  | 1 | 482.15 | 0.075 |  | 36.1613 | exposed side only considered in place of both side
| M.S angle 75x75X6 for Grating |  | 1 | 136.25 | 0.3 |  | 40.875
|  |  | Total |  |  |  | 245.0213
21 | Finishing walls with Acrylic Smooth exterior paint | Sqm
| wall Connected with precast col including coping |  | 2 | 15.4 |  | 1.85 | 56.98
| Intermediate Wall including column |  | 2 | 212.5 | - | 1.45 | 616.25
| Column Offset |  | 246 | 0.085 |  | 1.85 | 38.6835
|  |  | Total item 14+15 |  |  |  | 755.7015
22 | Stone Pitching….. | Sqm
| slope protection outside near Loc. 10 |  | 1 | 75 | 3 |  | 225
|  |  | Total |  |  |  | 225
23 | Pointing on stone work with cement mortar 1:3 (1 cement : 3 fine sand) :Flush/ Ruled pointing | Sqm
| Loc. 10 |  | 1 | 75 | 3 |  | 225
|  |  | Total |  |  |  | 225
24 | Concertina coil fencing | Metre
| on newly constructed boundary wall |  | 1 | 297.5 | - | - | 297.5
| on stolen portion |  | 12 | 2.5 |  |  | 30
|  |  | Total |  |  |  | 327.5
25 | Dismantling barbed wire or flexible wire… | Kg
| For providing Extra Gratings in existing portion |  | 25 | 2.1626 |  |  | 54.064
|  |  | Total |  |  |  | 54.064
26 | Refixing of existing Concertina coil fencing | Metre
| For providing Extra Gratings in existing portion |  | 25 | 2.5 | - | - | 62.5
|  |  | Total |  |  |  | 62.5
27 | Making groove in plastered surface | Metre
| wall Connected with precast col |  | 8 | 15.4 |  |  | 123.2
| Intermediate Wall including column |  | 6 | 212.5 | - |  | 1275
| Column Offset |  | 984 | 0.085 |  |  | 83.64
|  |  | Total |  |  |  | 1481.84
28 | Demolishing bamboo fence | Sqm
|  |  | 1 | 277 | - | 2.5 | 692.5
|  |  | Total |  |  |  | 692.5
30 | Structural steel work … (excluding supply).
| M.S Angle- 50x50x6mm for barbed wire fixing |  | 34 | 1 | 1.175 | 4.5 | 179.775 | Qty for 34 tilted column

## Rate Analysis 16.53 (hidden)
RATE ANALYSIS: Fixing concertina coil fencing with punched tape concertina coil 600 mm dia 10 metre openable length ( total length 90 m), having 50 nos rounds per 6 metre length, upto 3 m height of wall with existing angle iron ‘Y’ shaped placed 2.4m or 3.00 m apart and with 9 horizontal R.B.T. reinforced barbed wire, stud tied with G.I. staples and G.I. clips to retain horizontal, including necessary bolts or G.I. barbed wire tied to angle iron, all complete as per direction of Engineer-in-charge, with reinforced barbed tape(R.B.T.) / Spring core (2.5mm thick) wire of high tensile strength of 165 kg/ sq.mm with tape (0.52 mm thick) and weight 43.478 gm/ metre (cost of M.S. angle, C.C. blocks shall be paid separately)
Sl.no (1) | DSR23 item no. | Description of item | UNIT | Quantity | RATE | Amount
1 | 13.63 | Details of cost for 30.00 m length
i) | 8691 | MATERIAL Punched tape concertina coil 600 mm dia 10 m openable length (Total length 90 m) (Having 50 Nos. of rounds per 6 meter = 1 bundles) Therefore, Nos. of bundles 30/10=3bundles) | bundle | 0 | 720 | 0
ii) | 8692 | RBT reinforced barbed wire 9 rounds = 9x30 = 270m | metre | 0 | 8 | 0
iii) | 8693 | Turn buckle and strengthening bolt | each set | 10 | 46 | 460
iv) | 9999 | G.I. staples clips etc. LABOUR Labour for fixing straightening cutting of tape/ coils & wire | L.S. | 49.4 | 2.27 | 112.138
v) | 0114 | Beldar 0.50x2 = 1.00 Nos (Taken double due to height) | day | 1 | 736 | 736
vi) | 0102 | Blacksmith 1st class | day | 0.5 | 897 | 448.5
vii) | 0103 | Blacksmith 2nd class | day | 0.5 | 816 | 408
viii) |  | TOTAL |  |  |  | 2164.638 | W
2 |  | Add 1 % Water charges on “W” |  |  |  | 21.6464
3 |  | TOTAL |  |  |  | 2186.2844 | X
4 |  | Add GST on “X” (multiplying factor 0.2127) |  |  |  | 465.0227
5 |  | TOTAL |  |  |  | 2651.3071 | Y
6 |  | Add 15% CPOH on “Y” |  |  |  | 397.6961
7 |  | TOTAL |  |  |  | 3049.0031 | Z
8 |  | Add Cess @ 1% on “Z” |  |  |  | 30.49
9 |  | Total including Contractor profit & GST (Cost of 30 metre) |  |  |  | 3079.4932
10 |  | Total including Contractor profit & GST (Cost of 1.00 metre) |  |  |  | 102.6498

## Rate Analysis 26.74.1 (hidden)
RATE ANALYSIS: Fabrication and manufacturing of solid precast concrete element with provisions of shear keys, connecting loops, dowel tubes and proper lifting accessories for walls, beams, slabs, stairs, column etc, of various thickness, shape and size of different concrete grades manufactured in controlled factory environment with approved methodology including moulds (Pallet system, Tilts form, table moulds, battery moulds, vertical moulds, beam moulds, column moulds, staircase moulds, Facade mould, etc.), mixing, transporting and placing of concrete, vibrating, curing, finishing, making necessary cutout/holes of required sizes for services, yard handling & stacking all complete as per IS 11447:1985 and as per approved shop drawings and design mix as per the direction of Engineer-in-Charge (Cost of reinforcement, Mechanical, Electrical and Plumbing inserts will be paid separately). Concrete Grade M20 Cast In Situ
Sl.no (1) | DSR23 item no. | Description of item | UNIT | Quantity | RATE | Amount
(1) | 26.74.1 | Detail of cost for 1.26 Cum Considers a wall 2.80 X 3.00 X 0.15 = 1.260 Cum
i) | 4.1.2 | Rate as per Item No.4.1.2 of SH: RCC M20 | Cum | 1.26 | 8340.85 | 10509.471 | A
ii) | 5.35 | Rate as per item no 5.35 of SH RCC | quintal | 0 | 733.5 | 0 | A
iii) | 9999 | Cost of hosting and fixing moulds Side Shuttering of walls ((2.8+3)x2x0.15=1.74) | L.S. | 372 | 2.27 | 844.44
iv) | 5.9.1 | Rate as per item No.5.9.1 of SH : RCC | sqm | 1.74 | 392.15 | 682.341 | A
v) | 9999 | Table buffing & oiling | L.S. | 174 | 2.27 | 394.98
vi) | 9999 | Sundries (Extra labour for Lifting, transportation, stacking of finished precast elements) | L.S. | 230 | 2.27 | 522.1
vii) | 5.41.1 | Rate as per item no 5.41.1 of SH RCC (Curing using curing compound) | sqm. | 18.54 | 69.05 | 1280.187 | A
viii) | 7929 | Shear loops (6mm dia GI wire rope) (For vertical joints) 6 nos on each side | each | 12 | 230 | 2760
ix) | 7930 | dowel tubes (Corrugated GI pipes 50 to 80mm dia) (For horizontal joints | m | 3 | 165 | 495
x) | 9999 | Shear key (6mm thick mechanically folded MS plate) | L.S. | 115 | 2.27 | 261.05
xi) | 7931 | Hooks for lifting (Alloy steel) having 2.5 tonne capacity | each | 2 | 310 | 620
xii) |  | Labour for fixing accessories & inserts such as shear loops, shear keys, dowel tubes, lifting hooks
xiii) | 0155 | Mason (average) | day | 0.5 | 857 | 428.5
xiv) | 0115 | Coolie | day | 0.5 | 736 | 368
xvi) |  | Labour for operating of hoisting & fixing moulds
xvii) | 0157 | Operator | day | 0.5 | 897 | 448.5
xviii) | 0116 | Fitter (grade 1) | day | 0.3 | 897 | 269.1
xix) | 0115 | Coolie | day | 0.3 | 736 | 220.8
xx) | 9999 | Sundries (Labour cost such as crane, trailer(flat bed & a frames) & panel racks for stacking of precost concrete panel wall) | L.S. | 173.41 | 2.27 | 393.6407
xix) |  | TOTAL |  |  |  | 20498.1097 | W
2 |  | Add 1 % Water charges on “W-A” |  |  |  | 80.2611
3 |  | TOTAL |  |  |  | 20578.3708 | X
4 |  | Add GST on “X-A” (multiplying factor 0.2127) |  |  |  | 1724.2253
5 |  | TOTAL |  |  |  | 22302.5961 | Y
6 |  | Add 15% CPOH on “Y-A” |  |  |  | 1679.2919
7 |  | TOTAL |  |  |  | 23981.888 | Z
8 |  | Add Cess @ 1% on “Z-A” |  |  |  | 115.0989
9 |  | Total including Contractor profit & GST (Cost of 1.26cum) |  |  |  | 24096.9868
10 |  | Total including Contractor profit & GST (Cost for 1 cum) |  |  |  | 19124.5927