| Sl. No. | # Volume/ Section/ Description | # Clauses | # Bidder’s Query | # POWERGRID Reply |
| --- | --- | --- | --- | --- |
| Volume-II: Technical Specifications |  |  |  |  |
|  | 3-GIS Rev-5A: 27 | TESTING & MAINTENACE EQUIPMENT 1. Portable Partial Discharge measurement test kit with all necessary accessories, Industrial Grade Laptop and licensed software as per technical specification. 2. SF6 Gas Filling, Evacuating, Filtering, Drying, Pumping & Storage Plant with Spares for 5 Years Operation 3.SF6 Gas Leakage Detector 4.SF6 GAS ANALYZER | The Supply of TESTING & MAINTENACE EQUIPMENT will be quote as per BPS or Technical Specification or Both. Kindly Confirm Please. | Clause no: 8.0 of Section Project shall be referred along with BPS. |
|  | 3-GIS Rev-5A: 7.2.13 | The disconnectors and safety grounding switches shall have mechanical/electrical interlocks to prevent closing of the grounding switches when isolator switches are in the closed position and to prevent closing of the disconnectors when the grounding switch is in close position. | The Disconnector and Earthing switch are electrically interlocked with each other. Mechanical interlock is not envisaged. Kindly accept | In case disconnectors and earthing switches are separate modules in GIS design, electrical interlock without mechanical interlock may be accepted provided other requirements of Technical Specifications are fulfilled for such offered design of GIS. |
|  | Annexure-S11 | End Piece Module: As per Annexure-S11: End Piece (Interface) modules with isolating test link for Future extension on one side of Bus bar module. As per Annexure-VIII: End Piece (Interface) modules with the isolating test link for Future extension (on both sides) of Bus bar module. | Please confirm GIS extension module required on one side or both side of busbar? | Interface Module is envisaged on both ends of Bus bar. |
|  | Notes 1. 1-7 Annexure-VII_Technical Parameters of 25MVA Power Transformer | For parallel operation with existing transformer, the impedance, OLTC connection & range and the winding configuration (if necessary) is to be matched. | We have considered impedance as per Clause no. 1.12 of Annexure VII. If the same is going to change customer has to inform before finalizing the order, kindly confirm. | Bidder to quote as per provisions of bidding documents. |
|  | 8.2.5 5 400kV Transformer specification_Rev 13 | The above oil treatment plant (Filtration unit) shall be arranged by the bidder at his own cost. | The Supply of TESTING & MAINTENACE EQUIPMENT will be quote as per BPS or Technical Specification or Both. Kindly Confirm Please. | The Filtration unit referred to in the query shall be arranged by the bidder at his own cost on returnable basis. (Refer Clause no 8.2.5 of Section: Transformer, Rev13) Bidder to quote as per provisions of Bidding documents. |
|  | 18 5 400kV Transformer specification_Rev 13 SECTION- TRANSFORMER (UPTO 400 KV CLASS) | Hand Tools (if specified in BPS) | The Supply of TESTING & MAINTENACE EQUIPMENT will be quote as per BPS or Technical Specification or Both. Kindly Confirm Please. | Clause no: 8.0 of Section Project shall be referred along with BPS. |
|  | 19, 5 400kV Transformer specification_Rev 13 SECTION- TRANSFORMER (UPTO 400 KV CLASS) | Test Kit (if specified in BPS) BDV Kit as per Annexure-J of specification Portable DGA Kit as per Annexure-J of specification | The Supply of TESTING & MAINTENACE EQUIPMENT will be quote as per BPS or Technical Specification or Both. Kindly Confirm Please. | Clause no: 8.0 of Section Project shall be referred along with BPS. |
|  | 20bb, 5 400kV Transformer specification_Rev 13 SECTION- TRANSFORMER (UPTO 400 KV CLASS) | Online dissolved Hydrogen and Moisture Measuring Equipment (if specified in BPS) as per Annexure-L | We have provided Online Dissolved Gas (Multi-gas) and Moisture Analyser hence Online Hydrogen and moisture monitor is not required and the same is not provided. | Online dissolved Hydrogen and Moisture Measuring Equipment is not envisaged in present scope. In case bidder offers Online Dissolved Gas (Multi-gas) and Moisture Analyser, it shall be without additional price implication to POWERGRID. |
|  | 5 400kV Transformer specification_Rev 13 SECTION- TRANSFORMER (UPTO 400 KV CLASS) | If specified in BPS | "If specified in BPS" is mentioned in various places of specification, please provide BPS. | Please refer Price Schedule -1, 2 & 3 in Volume -III of the bidding document for BPS. |
|  | 5 400kV Transformer specification_Rev 13 SECTION- TRANSFORMER (UPTO 400 KV CLASS) | Fibre Optic sensor | Please confirm whether FOS is required (no. of probes also to be specified by customer) | FOS is not envisaged for supply under present scope. |
|  | 5 400kV Transformer specification_Rev 13 SECTION- TRANSFORMER (UPTO 400 KV CLASS) | CT details | Please provide HV and LV CT details. | The details of HV & LV side Bushing CTs required as per protection philosophy of present scope shall be decided during detailed engineering. Bidder shall quote accordingly. Please refer Cl. 11.1 of Section: Project, Rev.1 for current rating of bay. |
|  | 5 400kV Transformer specification_Rev 13 SECTION- TRANSFORMER (UPTO 400 KV CLASS) | Termination | We have considered Bare bushing for both HV and LV. | Please refer Clause no 10.0 of Section: Transformer, Rev13 for type of bushing. |