| S.No | Clause No. & Reference | Description as per Bidding document | BIDDER’s QUERIES | POWERGRID Reply |
| --- | --- | --- | --- | --- |
| Volume-II; Technical Specifications |  |  |  |  |
|  | Model Technical Specification Section- Switchgear- Isolator (Rev. No. 12) Clause No. 3.1 | Description of Contacts of isolatoirs | Whether Isolators are required with Ice-breaking contacts or not. There is no mention of that in technical specification and this is a major query from all the vendors. This is pivotal as the region experiences heavy snowfall during winter season along with long periods of sub zero temperatures. | Refer Cl. 11.6.a, of Section-Project (Part-A) for low temperature requirements of Isolators under present scope. Bidder shall quote accordingly. |
|  | Civil Works |  | Since PEB building is required for GIS hall, DG set room and AHU building, we request you to give layouts/ drawings for the same as the vendors are unable to give a technically correct offer for the same. Following drawings are required: 1) Control Room Building 2) PEB-220 KV GIS 3) 220 KV PEB Penal Room for GIS Hall. 4) 220 KV PEB AHU Room for GIS Hall 5) Pre-Engineered D-G Building 6) Car Parking Drawing 7) Labour Camp | Design and drawing of the following buildings are in bidder’s scope and tentative Plinth area shall be as per BOQ: - Control Room Building - PEB-220 KV GIS - 220 KV PEB Panel Room for GIS Hall. - 220 KV PEB AHU Room for GIS Hall - Pre-Engineered DG Building - Car Parking Drawing Labour camp is not envisaged. Bidder shall quote accordingly. |
|  | PLCC BPS (S.No. 34, 35) |  | The item list of PLCC is not clear from the BPS. Please provide clarity on the lit of items and share the complete technical specifications | Refer to Cl. 3.1.(I) (B) g) of Section-Project (Part-A) for scope of DPC under subject package. Bidding documents are amply clear. Bidder shall quote accordingly. |
|  | Conductor | ACSR Deer Conductor | Specifications of ACSR Deer Conductor are not mentioned in the tender documents. | Bidder may refer Annexure-B1, Section-VIIA of the technical specification for standard Technical Particulars for ACSR Deer Conductor |
|  | Technical specification for GIS (GIS-REV 5A) |  |  |  |
|  | 2.3 | The equipment offered shall be protected against all types of voltage surges and any equipment necessary to satisfy this requirement shall deemed to be included. | We understand that surge arrestors are required to cater the requirement and are of AIS type. | Refer to reply provided in General Query S. No. 6 of Annexure-XI to Section-Project (Part-A). Bidder shall quote accordingly. |
|  | 5.28 | In addition to above suitable portable scissor lift shall be provided for access of distant portion of GIS installation. | We do not envisage this requirement. Walkways if required and portable ladder shall be provided. | Bidder shall quote as per provisions of bidding documents. |
|  | 5.42 | (9) GIS manufacturer as per their design shall preferably use maximum three standard straight horizontal outdoor bus duct lengths for entire GIS installation to optimize the spare requirement. | The GIB shall be as per manufacture's standar practice and actual site condition, request to customer to accept the same. | Outdoor Bus ducts are not envisaged under present scope. Bidder shall quote as per provisions of bidding documents. |
|  | 19. DESIGN REVIEW | d) Calculations to show that there is no Ferro resonance due to capacitance of GIS for the voltage transformers. | ferro resonance calculation not in the scope of GIS OEM | Requirements of Technical Specifications shall prevail. Bidder shall quote accordingly. |
|  | 5.8. | The material and thickness of the enclosures shall be such as to withstand an internal flashover without burns through for a period of 300 ms at rated short time withstand current. The material shall be such that it has no effect of environment as well as from the by-products of SF6 breakdown under arcing condition. This shall be validated with Type Test. | vendor's offered GIS design are completely type tested for internal arc test in line with latest requirements of IEC. We confirm compliance to IEC 62271-203. (Table 4) for all the voltage levels. | Requirements of Technical Specifications shall prevail. Bidder shall quote accordingly. |
|  | 5.2 | Bus bar compartment filled with SF6 Gas and separated by gas tight partitions so as to minimize risk to human life, allow ease of maintenance and limit the effects of gas leaks failures & internal arcs etc. | Vendor's 220 kV is having busbar and disconnector in seperate gas compartments hence this clause is not applicable. Further, offered GIS is globally proven type tested design having passive non segregated busbar design meeting all the functional requirements of service continuity as per specifications. We confirm offered GIS is line with all latest requirements of IEC 62271-203. | Requirements of Technical Specifications shall prevail. Bidder shall quote accordingly. |
|  | 5.35 | For sliding type compensators, markers/ pointers shall be provided to observe expansion or contraction during climatic conditions. | The provision of marker/pointer in compensator is not envisage, request to customer to accept the same. | Requirements of Technical Specifications shall prevail. Bidder shall quote accordingly. |
|  | 2 Nilgrar 220 33kV GIS GA 26102022 Rev1 | GA layout | requesting you to please provide GA layout wherein the dimension of GIS building is clearly mention. | Refer Cl.3.8 of Section-Project (Part-A). Bidder shall quote accordingly. |