| S.N. | Volume | Chapter | Section No. | Clause No. | Clause | Existing Specification | Query / Suggestion | POWERGRID Response |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | II | 1 |  | 1.6 | Scope and General Requirements | Integration of existing and New RTU (Remote Terminal Unit) /DCPC (Data Concentrator Protocol Converter) /DCU (Data Concentrator Unit)/Communication Gateway of SAS | We understand the present scope includes only supply and services of control center for SCADA and Forecasting. There is no scope of supply and services at the substations for eg: RTU (Remote Terminal Unit) /DCPC (Data Concentrator Protocol Converter) /DCU (Data Concentrator Unit) / Communication Gateway of SAS. Also communication link between substations/pooling stations to control center in not in present scope. The above is as per clause 1.7.3 (iv) Please confirm | Present scope of REMC includes integration of RTU/DCPC/SAS with the REMC SCADA system in the scope of bidder. For communiation link between substation to control center refer clause - 1.7.3 Owner’s Responsibilities and Obligations, It is responsibility of the owner to provide DIU/RTU/DCPC/DCU etc. and associated communication infrastructure from STU pooling station to control center. |
| 2 | II | 1 |  | 1.6 | Scope and General Requirements | Integration of SLDC REMC SCADA with respective RLDC REMC SCADA Systems on ICCP protocol | We understand the present RLDC REMC SCADA control center is at SRLDC Bangalore.Please confirm. | Yes, the RLDC REMC SCADA Control center is at SRLDC Banglore |
| 3 | II | 1 |  | 1.6 | Scope and General Requirements | The contractor’s scope shall include customisation of its ICCP protocol, such as configuration of ICCP database for ICCP name, scan period and all other database parameters required to integrate existing and new Control centres successfully. | Kindly provide the details of ICCP version and bilateral association table for the existing system. | The details of ICCP version and bilateral association table for the existing system shall be shared at the time of detailed engineering. |
| 4 | II | 1 |  | 1.6 | Scope and General Requirements | Comprehensive Maintenance of the new system which includes future ICCP & RTU/DPCP/DCU Integrations/ Communication gateway of SAS, Database configurations, Maintaining predefined system availability, Preventive Maintenance Support, Maintaining Spare Inventory etc. | We understand the present scope includes only supply and services of control center for SCADA and Forecasting. There is no scope of supply and services at the substations for eg: RTU (Remote Terminal Unit) /DCPC (Data Concentrator Protocol Converter) /DCU (Data Concentrator Unit) / Communication Gateway of SAS. Also communication link between substations/pooling stations to control center in not in present scope. The above is as per clause 1.7.3 (iv) The comprehensive maintenance shall cover for the scope accordingly. Please confirm | Refer clarification s.no.-1 & clause no. 1.6 of TS , Compreshensive Maintenance of the system includes intregration of ICCP, RTU/DPCP/DCU & Commnication gateway of SAS database etc. |
| 5 | II | 1 |  | 1.7.1 | Contractor’s Responsibilities and Obligations | The Contractor shall be responsible for all cables and wiring associated with the equipment both inside and outside buildings. The Contractor shall also be responsible for determining the adequacy of the local power source for the equipment and for wiring to it, with adequate circuit protective breakers. | Please provide the details of existing UPS capacity and the present loading of the UPS. | Details of existing UPS capacity and loading will be shared at the time of detailed engineering. |
| 6 | II | 1 |  | 1.7.1 | Contractor’s Responsibilities and Obligations | (iv) Provision of Forecasting services (Power & Weather). | We understand that the existing/available weather forecasting data (eg IMD) will be utilised and only 1 no. power/renewable forecasting tool to be provided. No separate weather forecasting service to be provided in the scope. Please confirm. | No weather service (IMD or any other service provider) is existing/available upfront with the owner. It will be in the scope of contractor to provide weather forecast services which will be utilised by the forecasting tool (includes internal forecasting module) provided at the control centre. |
| 7 | II | 1 |  | 1.7.1 | Contractor’s Responsibilities and Obligations | (ix) Integration of the REMC RE scheduling tool with the existing SLDC scheduling tool | The requirement is not clear, Please elaborate. | Presently, Telangana SLDC is using their own RE scheduling tool for scheduling activity,REMC scope includes integration of REMC scheduling tool with the existing in use SLDC Telangana scheduling tool. |
| 8 | II | 1 |  | 1.7.1 | Contractor’s Responsibilities and Obligations | (xxi) The contractor shall submit type test reports for all the equipment’s as per specification for review & approval by Employer within 30 days of Contract Award. The type test reports submitted shall be of the tests conducted within last five (5) years prior to the date of bid opening. In case the test reports are older than five (5) years ago on the date of bid opening or the type test reports are not meeting the specification requirement, the contractor shall carry out the type testing at no additional cost to the employer. | This is not applicable as the present scope does not cover communication link and field equipments like RTU (Remote Terminal Unit) /DCPC (Data Concentrator Protocol Converter) /DCU (Data Concentrator Unit) / Communication Gateway of SAS. Please confirm | No type report shall be required for the items which are not cover under this contract. |
| 9 | II | 2 | 4 | 4.11 | Monitoring and Compliance Manager of Critical Infrastructure Protection Standards | Monitoring and Compliance Manager of Critical Infrastructure Protection Standards. A dedicated software utility/application shall be deployed in the system as part of NMS or on dedicated nodes having following features: | This software requirement is not clear and not reflecting in the price schedule, Please clarify. | TS provisions shall prevail. Bidder has to fulfill necessary requirements mentioned in TS. |
| 10 | II | 2 | 7 | 7.14 | Availability Test | After field performance test, a 1000-hour availability test shall be conducted on supplied systems under normal day-to-day operating conditions. The test shall verify the reliability and integrity of the database, displays, report, all communication interfaces, Weather parameter interfaces and FSP interfaces, under these conditions, verify system availability for 99.9%. Further each server and device and RTUs if available from field shall meet a minimum availability of 98% individually. In case of RTUs, downtime of individual RTUs are excluded from system availability calculations. However, minimum 50% RTUs integrated with the system shall be reporting for test to continue. | We understand the present scope includes only supply and services of control center for SCADA and Forecasting. There is no scope of supply and services at the substations for eg: RTU (Remote Terminal Unit) /DCPC (Data Concentrator Protocol Converter) /DCU (Data Concentrator Unit) / Communication Gateway of SAS. Also communication link between substations/pooling stations to control center in not in present scope. The above is as per clause 1.7.3 (iv) The Availability test shall cover for the present scope only and shall not include field and communication systems. Please confirm | Availability test shall cover all the items supplied under the scope of this contract which include includes integration of RTU/DCPC/SAS with the REMC SCADA system. |
| 11 | I | 2 |  | 1.7 |  | Payment towards Forecasting Services | Forecasting services has been split year wise in the price schedule from yr 1 to yr 4 but Weather services is indicated as quaterly payment only without yearly split. Further we understand that the existing/available weather forecasting data (eg IMD) will be utilised and only 1 no. power/renewable forecasting tool to be provided. No separate weather forecasting service to be provided in the scope. Please clarify. | In case of Power forecasting, cost is divided in two components. First is base component (50% of the total cost) which will be disbursed quarterly in four equal installments and second component is "performance based payement" which will be disbursed at the end of the one year based on the accuracy performance achieved. For weather services refer caluse no. 1.7.1 of above clarification S.no. 6. Further, there will be no weather services (IMD or any other service provider) Existing/available upfront with the owner. It will be in the scope of contrator to provide weather forecast services which will be utiised by forecasting tool (includes internal forecasting module) provided at the control centre. |
| 12 | II | 1 |  | 1.5 | REMC System Architecture | Conceptual Architecture of REMC | Conceptual Architecture has shown one of the block as 'Backup Control Center'. It is assumed that this control centre is SLDC/RLDC backup control center. Kindly clarify if it is different. | Yes, the control center is backup of SLDC Telangana. |
| 13 | II | 2 |  |  | Proposed System | Contractor has to provide standard APIs (Application Programming Interface) provided under project for different application and WEB application. | As per standard practice source code is provided only for developing displays/ reports. We request POWERGRID to clarify the same. | Contractor has to provide standard APIs (Application Programming Interface) for integration of different applications. |
| 14 | II | 2 | 1 | 1.2.5 and 1.2.7 | Data Exchange with RE developers and Data Exchange with Third Party & Offline Applications | Data Exchange through OPC | Kindly clarify the quantity of servers and clients to be considered for OPC data exchange? E.g. In case of OPC data exchange with Historian System it is clearly mentioned in clause 1.7.3 on Page 41 of 287 that clients required are 15 nos. | Refer Clause Up Vol-II Section - 1 , Clause- 1.2.7, OPC Client shall be able to interact with SCADA server using a defined OPC-DA. Up to five (5) server & client shall be connected with SCADA system as per requirement. Accordingly licenses shall be provided to five (5) server & client shall be connected with SCADA system as per requirement. |
| 15 | II | 2 | 1 | 1.2.1 | Data Exchange with Control Centers | The following ICCP blocks shall be implemented in the supplied SCADA system e.g. block 1, block 2 and block 5 (as per requirement). | We request POWERGRID to clarify in detail regarding requirement of Block 5. Is is intended to have Remote Control Opertion from REMC state/region control centers? | Vendor has to supply ICCP block requirement mentioned in TS. Remote Control operation shall be done based on the furture requirements. |
| 16 | II | 2 | 1 | 1.5 | Supervisory Control |  | Is it intended to have Remote Control feature at REMC SCADA systems? We required POWERGRID to clarify the same | Refer clarification s.no. - 15 |
| 17 | II | 2 | 1 | 1.7.2.1 | Interface with SCADA software for acquiring the real-time data | Historian should have an interface to send the output of calculations periodically/ on demand/ event based to SCADA. | Historian Systems are mainly required for Long Term storage of data and analysis based on the same. Data flows generally from SCADA to Historian System. We request POWERGRID to clarify the need to send data from Historian System to SCADA system | TS provisions shall prevail. The provision in TS is kept to view present and past trendes together in SCADA system. |
| 18 | II | 2 | 1 | 1.1.1 | Data Acquisition | Real-time data shall be collected from field devices located at various Substations and Power Plants on IEC 60870-5-101, IEC 60870-5-104 protocol and OPC. The data includes analog, status and SOE inputs. | We request POWERGRID to provide with no. of RTUs to communicate on IEC 60870-5-101 and IEC 60870-5-104 each. | Refer Vol-II, Appendix-C, Table – 6, Max Design Limit of the SCADA system |
| 19 | II | 2 | 4 | 4.11 | Software Requirements | Monitoring and Compliance Manager of Critical Infrastructure Protection Standards | The requirements mentioned under this sections are related to SIEM which is not mentioned in the BoQ. We request POWERGRID to clarify the same | Refer clarification s.no. - 9 |
| 20 | II | 2 |  | Appendix E | Questionnaire | Please describe how the Communication with existing RTU will be established in the new Control Centre without interrupting the operations in the existing System? | Which are the existing systems in every state ? It is already mentioned in section Chapter 1 Section 1.7.3 (iv) that it shall be owner's responsibility. Kindly clarify | Owner shall provide the communication with existing RTU to the Control center. Refer clarification s.no. - 1 |
| 21 | II | 2 |  | Appendix-K | Configuration Diagram |  | Kindly clarify whether Router is required for CFE as the same is not mentioned in the architecture diagram. | Refer Appendix-K,Configuration Diagram, WAN Router for RTU is mentioned in architecture. |
| 22 | II | 2 |  | Appendix-G and Appendix-H | Bill of Quantity |  | USB Blocking software is not included in BoQ. We request POWERGRID to include the same in BoQ / Price schedule | TS provisions shall prevail |
| 23 | II | 2 |  | Appendix-G and Appendix-H | Bill of Quantity |  | BoQ doesn’t include specific hardware for Document Management System, Antivirus and Patch Management Server. We recommend POWERGRID to include the same in the BoQ / Price schedule | TS provisions shall prevail |
| 24 | II | 2 |  | Appendix-G and Appendix-H | Bill of Quantity |  | BoQ doesn’t include any BackUp software. Back up Software will be an essential tool in order to keep back up with proper process and handling it for all types of backups such as internal backup, backup of external media. We request POWERGRID to include the same in the BoQ / Price schedule | TS provisions shall prevail |
| 25 | II | 2 |  | Appendix G | Bill of Quantity | 2.18: 44 U Server Rack with KVM switch & Rack mounted Monitor | We request POWERGRID to consider 42 U size which is a standard size available in market. | TS provisions shall prevail |
| 26 | II | 2 |  | Appendix G | Bill of Quantity | Mandatory Spares: Tape Drive | Kindly clarify whether we need to consider a Tape Drive or Tape Library ? Tape Library is mentioned in BoQ / Appendix G | TS provisions shall prevail |
| 27 | II | 2 |  | Appendix-H | 1. Servers | SCADA, Historian, NMS, ICCP, CFE, Data Replica, Development Server, Repository, Web & CMC :Internal Optical Drive - Blu Ray Drive Read/Write | Blu Ray Drive Read/Write is not supported for Server Hardware. Also, it is not recommended to use drive with 'Write' feature as it may enable writing critical data/files from the servers on external media devices. We thereby request POWERGRID to remove this component for server hardware | TS provisions shall prevail |
| 28 | II | 2 |  | Appendix-H | 1. Servers | SCADA, Historian, ICCP, DDS : External Auxilary Memory - shall use the 16GBPS FC SAN storage | We request POWERGRID to clarify whether the external auxilliary memory is required only for Historian Server | TS provisions shall prevail |
| 29 | II | 2 |  | Appendix-H |  |  | Configurational details for Server Management Console are not provided. We request POWERGRID to provide the same. | DRS of SMC is mentioned in TS. further details shall be finalised during deatiled engineering |
| 30 | II | 2 |  | Appendix-H |  | Monitors for Workstations, Monitors for Servers | We request POWERGRID to clarify what exaclty is meant by 'On Screen Control' ? Is it related to settings of the screen or a "touch feature"? It is not recommended to use touch screen feature on operator/server monitors. | TS provisions shall prevail |
| 31 | II | 2 |  | Appendix-H |  | Black & Whilte Laser Printer - First Page Time Out Color Laserjet Printer - First Page Time Out | We request POWERGRID to revise/reconsider the criteria set for first page time out as per below: - For Black Printer - 15 seconds For Color Laserjet Printer - 18 seconds. | TS provisions shall prevail. |
| 32 | II | 2 | 8 | 8.2 | Web Application | l) E-mail and SMS interface for alarms | We request POWERGRID to clarify the scope of E-mail gateway (Whether this is to be considered by bidder?) | Refer Appendix- G of TS, SMS & Email Gateway is part of BoQ. |
| 33 | II | 1 |  | 1.7.1 | Contractor’s Responsibilities and Obligations | 1.7.1 Contractor’s Responsibilities and Obligations ------ A Tripartite agreement for Internet services will be signed between ------- | Request PGCIL to provide tripartite agreement form at bid stage. | The details of TPA shall be shared during detail engineering |
| 34 | II | 2 | 4 | 4.8.1 | Image Backup and Restoration Utility | Image Backup and Restoration Utility | We understand that Image backup should be part of BOQ item.Please confirm. | TS provision shall prevail |
| 35 | II |  |  |  | General Scope related |  | We understand that timeline shall be mentioned in the contract for providing of field data i.e. static/dynamic data for FSP(Forecasting Service Provider) modeling for timley project completion. | The details shall be shared during detail engineering |
| 36 | II |  |  |  | General Scope related |  | We request PGCIl to provide ISP connection during execution period,Kindly confirm. | TS provision shall prevail |
| 37 | II |  |  |  | General Scope related |  | We suggest to provide specific applicable regulatory guideline in bid dcoument for Forecasting and scheduling , if any . | TS provision shall prevail |
| 38 | II |  |  |  | General Scope related |  | Please provide UI- maps as per owner requirement for Forecasting part. | The details shall be shared during detail engineering |
| 39 | II |  |  |  | General Scope related |  | Please finalize schedule format for data exchange b/w new REMC and existing schedule format and incorporate in the bid if feasible. | The details shall be shared during detail engineering |
| 40 | II |  |  |  | General Scope related |  | Please confirm whether existing UPS have sufficient capacity / provision for the supply of new system | The details shall be shared during detail engineering |