| Sr. No | Clause No. | Clause Description | Bidder Queries | POWERGRID REPLY |
| --- | --- | --- | --- | --- |
| TECHNICAL QUERIES |  |  |  |  |
|  | Section Project, Cl. No.3.0&3.1 | i) Double Bus Double Breaker Scheme. ii) Existing 400 KV AIS Switchyard at Gorakhpur substation is having One & half Busbar arrangement. 420kV SF6 gas insulated switchgear shall have Double Bus Double Breaker bus bar arrangement with fault level 50 KA/1sec. | We would like to inform you that, there is discrepancy in Section project and SLD. So As per customer SLD & BPS we understand to consider the one half breaker arrangement for GIS. Kindly confirm our understanding. | The requirement is ample clear in Bidding document . Bidders to quote accordingly. |
|  | Section Project, Cl. No. 3.1.2 | i. 3-phase, 3150A, SF6 insulated circuit breaker without PIR complete with operating mechanism. iii. 3-phase, 3150A, single pole, group operated isolator switches, complete with manual and motor driven operating mechanisms. iv. 3-phase, single pole, group operated safety grounding switches, complete with manual and motor driven operating mechanisms. v. 3-phase, single pole, (#) group operated high speed grounding switch, complete with group operated manual and motor driven operating mechanisms. | We would like to inform you that, we shall provide i. 1-Phase (Separate for each phase) SF6 gas insulated circuit breaker without PIR, complete with operating mechanism. ii. 1-Phase (Separate for each phase) isolator switches with gang operating mechanism. 3. 1-Phase (Separate for each phase) safety grounding switches with gang operating mechanism. 4. 1-Phase (Separate for each phase) high speed grounding switch with separate operating mechanism. However these mechanism are electrically gang operated. Kindly accept the same. | Bidders to comply the requirement of Clause no. 2.2 of Technical Specification Gas Insulated Switchgear, Rev.5A. For completion of scope of each bay module associated clause of section project shall be referred to. |
|  | Section Project Cl no. 3.1.2 (ii) | 1) Section Project: i) 5-Core Current Transformers implies one 3 core CT & one 2 core CT ii) Three (3) numbers 1-phase, 3150A, 5-core *, multi ratio, current transformers duly distributed on both side of circuit breaker. 2) GIS Rev-5A: Table:3B | We would like to inform you that, there is discrpancy in CT data, As per section project 5 core CT required. However in GIS Rev-5A at Table:3B, 6 Core CT ratio mentioned. Also we have not received CT/PT ratio.We have considered CT ratio as per PGCIL Rev.5A (Table :3B) Request you to provide the same. Kindly Provide/clarify the same. | Bidders to comply as specified in Section project/ Specific Requirement. As per TS in biddding doument ,Distribution of CT cores shall be as below. i) On one side of CB:3 core CT include- ( 2 Protection Cores + 1 Metering core) ii) On other side of CB: 2 core CT include- ( 2 Protection cores) For all other technical requirements, please refer Table: 3B of TS section GIS Rev-5A. |
|  | Section Project,cl no. 10.2 of Specific requirements | i) Mandatory spares shall be as per Annexure-II ii) BPS: Mandatory Spare for GIS | We would like to inform you that we have considered GIS spare parts as per BPS. Kindly confirm the same. | Confirmed. |
|  | BPS , Schedule-3 , line item 94 | Switchyard Panel Room - Civil Works. All civil works as per drawing and specifications complete, including - brickwork, finishing(external and internal), windows etc. However, excavation, PCC, RCC and reinforcement shall be paid separately as per BPS. | The Line Item SR. NO . 91 & 94 are repeated twice in schedule-3 of the price schedule. Please clarify | Please refer Amendement-III. |