| SlN | Clause | Provision | Queries asked by the bidder | POWERGRID’s clarification |
| --- | --- | --- | --- | --- |
| 1. | Section-Project Clause No: 9.2 | 800kV, 420kV and 145kV Bushing shall be Oil filled condenser type with composite polymer insulator (housing) or RIP (Resin Impregnated paper) condenser type with composite polymer insulator (housing) or RIS (Resin Impregnated Synthetic) condenser type with composite polymer insulator (housing). | We understand that the mentioned bushings can be of porcelain or composite polymer housing and hermetically sealed Oil filled condenser type for all four ratings of Transformers. Please confirm our interpretation. | Please refer Clause No-1 of Amendment No-1. |
| 2. | “Price_Schedule” as per Sr. No. B8 | 145 kV, 800 A RIP Bushing is required as Mandatory Spares for 125 MVAr 400 kV Reactor | We understand that the mentioned bushings can be of porcelain or composite polymer housing and hermetically sealed Oil filled condenser type for all four ratings of Transformers. Please confirm our interpretation. | 145kV Bushing shall be RIP (Resin Impregnated paper) condenser type with composite polymer insulator (housing) or RIS (Resin Impregnated Synthetic) condenser type with composite polymer insulator (housing). |