| SlN | Clause | Provision | Queries asked by the bidder | POWERGRID’s clarification |
| --- | --- | --- | --- | --- |
| 1. | Cl no. 23.2 a) of Technical Specification, 765kV Shunt Reactor Rev. 08. Page No: 32 of 66 | Bushing Type Test as per IS/ IEC:60137 for all voltage class (Seismic test on 800kV Bushings) | In this tender, Type of bushing requirement is Oil to SF6 bushing. We Understood from vendor that Seismic test is not applicable for Oil to SF6 bushing. Hence, request PGCIL to withdraw Sesimic test requirement on Oil to SF6 bushing | Seismic test shall be applicable for Oil to SF6 bushing and same shall be as per IEC60137-2017 & IEC62271-211. |
| 2. | Cl no. 23.2 a) of Technical Specification, Upto 400kV Shunt Reactor Rev. 11. Page No: 34 of 75 | Bushing Type Test as per IS/ IEC:60137 for all voltage class (Seismic test on 400kV Bushings) | In this tender, Type of bushing requirement is Oil to SF6 bushing. We Understood from vendor that Seismic test is not applicable for Oil to SF6 bushing. Hence, request PGCIL to withdraw Sesimic test requirement on Oil to SF6 bushing | Seismic test shall be applicable for Oil to SF6 bushing and same shall be as per IEC60137-2017 & IEC62271-211. |