| Sl. No. | Clause No. | Existing Provisions | Amendment |
| --- | --- | --- | --- |
| 1 | Clause No. 9.2 of Section-Project, Rev. 00 | Clause No. 9.2 800kV, 420kV and 145kV Bushing shall be Oil filled condenser type with composite polymer insulator (housing) or RIP (Resin Impregnated paper) condenser type with composite polymer insulator (housing) or RIS (Resin Impregnated Synthetic) condenser type with composite polymer insulator (housing). | Clause No. 9.2 800kV Bushing shall be suitable for GIS SF6/Oil Interface, as per IEC-62271-211. 420kV Bushing shall be suitable for GIS SF6/Oil Interface, as per IEC-62271-211. 145kV Bushing shall be RIP (Resin Impregnated paper) condenser type with composite polymer insulator (housing) or RIS (Resin Impregnated Synthetic) condenser type with composite polymer insulator (housing). |
| 2 | BPS Schedule I & II Reactor Package: RT-19 New Item | SI. No.; Item Description; Unit; Qty.. Reactor Package: RT-19 400kV Reactor Mandatory Spares. New Item. | SAP ID; Item Description; Unit; Qty. Reactor Package: RT-19 400kV Reactor Mandatory Spares. 1000060013; 420KV, 800A OIL TO SF6 BUSHING WITH METAL PARTS AND GASKETS; EA; 1. |
| 3 | BPS Schedule I & II Reactor Package: RT-19 New Item | SI. No.; Item Description; Unit; Qty.. Reactor Package: RT-19 765kV Reactor Mandatory Spares. New Item. | SAP ID; Item Description; Unit; Qty. Reactor Package: RT-19 765kV Reactor Mandatory Spares. 1000060014; 800KV, 2500A OIL TO SF6 BUSHING WITH METAL PARTS AND GASKETS; EA; 1. |
| 4 | Clause No. 9.9 of Section-Project, Rev. 00 | New Clause added. | Clause No. 9.9: Clause No. 7.5.1 of Technical Specification, 765kV Shunt Reactor, Rev. 08, is amended as below: Conservator shall have air cell type constant oil pressure system to prevent oxidation and contamination of oil due to contact with moisture. Conservator Protection Relay (CPR)/Air cell puncture detection relay shall be installed to give alarm in the event of lowering of oil in the conservator due to puncture of air cell in service. Conservator shall be fitted with magnetic oil level gauge (Plug & socket type arrangement) with potential free high and low oil level alarm contacts and prismatic oil level gauge and Conservator Protection Relay. Plug & socket type arrangement with factory fitted cable of adequate length shall be supplied by OEM. Connection of plug and socket with cable at site is not acceptable. |
| 5 | Clause No. 9.10 of Section-Project, Rev. 00 | New Clause added. | Clause No. 9.10: Clause No. 7.5.1 of Technical Specification, Upto 400kV Shunt Reactor, Rev. 11, is amended as below: Conservator shall have air cell type constant oil pressure system to prevent oxidation and contamination of oil due to contact with moisture. Conservator Protection Relay (CPR)/Air cell puncture detection relay shall be installed to give alarm in the event of lowering of oil in the conservator due to puncture of air cell in service. Conservator shall be fitted with magnetic oil level gauge (Plug & socket type arrangement) with potential free high and low oil level alarm contacts and prismatic oil level gauge and Conservator Protection Relay. Plug & socket type arrangement with factory fitted cable of adequate length shall be supplied by OEM. Connection of plug and socket with cable at site is not acceptable. |
| 6 | Clause No. 9.8 of Section-Project, Rev. 00 | New Clause added | Clause No. 9.8: Clause 2.1 (a) of Section GTR, Rev-15 is amended as below: "All equipment/materials/items, as per Annexure-K (Rev 01), as applicable under present scope of works, shall be procured and supplied from domestic manufacturers only with Minimum Local Content for individual items as listed in the above annexure. Any imported equipment/material/item/parts/component (comprising of embedded systems) to be supplied under the contract shall be tested in the certified laboratories to check for any kind of embedded malware/trojans/cyber threats and for adherence to Indian Standards as per the directions issued by Ministry of Power/Govt. of India from time to time. In case of such import from specified “prior reference” countries, the requirement of prior permission from the Govt. of India including protocol for testing in certified and designated laboratories by Ministry of Power/Govt. of India shall also be complied with by the contractor. The bidder/contractor shall list out the products and components producing Toxic e-waste under the contract and shall furnish to the Employer the procedure of safe disposal at the time of closing of the contract." |