| SlN | Clause | Provision | Queries asked by the bidder | POWERGRID’s clarification |
| --- | --- | --- | --- | --- |
| 1. | Section-Project RT-19 Clause No: 2.2.1 a)1 Clause No: 2.2.1 b)1 Clause No: 9.2 | The 765kV Reactor shall be suitable for connecting HV side (765kV), with GIS SF6/Oil Interface, as per IEC-62271-211. The 420kV Reactor shall be suitable for connecting HV side (400kV), with GIS SF6/Oil Interface, as per IEC-62271-211. 800kV, 420kV and 145kV Bushings shall be Oil filled condenser type with composite polymer insulator (housing) or RIP or RIS….. | - Please confirm that whether HV bushing of 765 kV Reactor and 400 kV Reactor shall be of OIL to SF6 RIP type. - Please furnish technical requirements/ specification for OIL to SF6 bushing. - Please clarify the conflict between clause 2.2.1 & 9.2, i.e. as Oil to SF6 bushing shall be RIP type but without polymer insulator. - Please confirm that Bushing and reactor insulation level shall remain same as Section Shunt Reactor. - Please confirm that Testing of 765 and 400 kV reactors shall be allowed with oil-air bushing due to testing/ layout limitation. - Please note that IEC-62271-211 specify “Standard dimensions for typical direct connection between power transformer and gas-insulated metal-enclosed switchgear” up to 550 kV rated voltage. Powergrid may specify the similar details for 800 kV rated voltage (Oil to SF6 Bushing air end termination). - In view of point 4, Powergrid may review the requirement of spare of 765 kV Oil to SF6 Bushing. | - Please refer Clause No-1 of Amendment No-1. - Bushing shall be in-line with IEC 60137-2017 & Technical specification. - Please refer Clause No-1 of Amendment No-1. - Bidding document is quite clear. Bidders to comply the requirement of Technical specification. - Acceptable. However all required arrangements shall be in the scope of bidder. - 800kV & 400kV bushing shall be Oil to SF6 type suitable for GIS connection. The bushings shall be as per manufacturer design and Type Tested. Same shall be shared with GIS manufacturer during detailed Engineering in order to design the GIS interface module. - Please refer Clause No- 2 & 3 of Amendment No-1. |
| 2. | Technical Specification, 765kV Shunt Reactor C/ENGG/MODEL-SPEC/765kV SR Rev. 08 Clause No: 7.5.1 & Technical Specification, Upto 400kV Shunt Reactor C/ENGG/MODEL-SPEC/RT Rev. 11 Clause No: 7.5.1 | Conservator shall be fitted with magnetic oil level gauge with potential free high and low oil level alarm contacts and prismatic oil level gauge and Conservator Protection Relay | Please clarify the type of MOG to be supplied for this project (Whether the requirement is Plug and Socket type or not). #This comment is applicable for both 400 KV & 765 KV reactor. | Plug & Socket type arrangement shall be accepted. Please refer Clause No- 4 & 5 of Amendment No-1. |
| 3 | Technical Specification, 765kV Shunt Reactor C/ENGG/MODEL-SPEC/765kV SR Rev. 08 Clause No: 1.13 & 1.14 Of Annexure-I Technical Specification, Upto 400kV Shunt Reactor C/ENGG/MODEL-SPEC/RT Rev. 11 Clause No: 1.13 & 1.14 Of Annexure-I | 1.13.1. The PVC insulated 1100V grade power cables shall be of Fire Retardant Low Smoke Halogen (FRLSH) type, C2 category, conforming to IS: 1554 (Part-I) and its amendments…… 1.14.1 The 1100V grade control cables shall be of FRLSH type, C2 category conforming to IS: 1554 (Part-1) and its amendments…. | As per Sr. No-4 of Standard Technical Data Sheet - 1.1 KV Grade PVC Power Cables & Control Cable Type and Category of cable is mentioned as FR & C1. However as per Cl no 1.13.1 the type should be FRLSH and type C2. Therefore, POWERGRID is requested to clarify the same. #This comment is applicable for both 400 KV & 765 KV reactor. | 1.1 KV Grade PVC Power Cables & Control Cables Type and Category shall be FRLSH type and C2 category in-line with clause no: 1.13.1 & 1.14.1 of Annexure-I of Technical Specification, Section: 765kV Shunt Reactor, Rev. 08. 1.1 KV Grade PVC Power Cables & Control Cables Type and Category shall be FRLSH type and C2 category in-line with clause no: 1.13.1 & 1.14.1 of Annexure-I of Technical Specification, Section: Upto 400kV Shunt Reactor, Rev. 11. |
| 4 | Section-Project RT-19 Clause No: 2.2.1 a) | 765kV Reactors as mentioned above along with all fittings, accessories including On-Line Insulating Oil Drying System (Cartridge type), individual marshalling box for each Reactor, common marshalling box for each bank of 3-single phase units, foundation bolts (as applicable), insulating oil, Cables etc. including cables required to bring all the control, protection, indication signals of spare unit (110 MVAR) in common marshalling box of all the banks. | Please provide us the distances between marshalling box of spare reactor and common Marshalling box of each bank to determine the length of cable. | The requisite details shall be provided to successful bidder during detailed engineering. |
| 5 | Technical Specification, Upto 400kV Shunt Reactor C/ENGG/MODEL-SPEC/RT Rev. 11 Annexure-H | Technical Parameters of Current Transformers - 420 kV Shunt Reactor On each phase connection & Neutral Grounding Reactor (NGR) | It may be noted that for core 1) Knee point voltage of line side is 200V and Neutral side is 300V. as CT to be used for the differential protection, therefore the Knee point voltage of Neutral side CT is recommended as similar as Line side. Therefore, it is proposed to make the Knee point voltage of aforesaid Neutral side CT as 200 V. kindly review and accept. | Bidder shall quote as per provisions of bidding document. |