| S.No | S.No. of Bidders Query | Ref Clause No. | Provision in Bidding documents | Bidder’s Queries | POWERGRID Reply |
| --- | --- | --- | --- | --- | --- |
| 1 | 1 | SECTION-PROJECT; CL.No:8.5 | Buchholz Relay, Magnetic Oil Level Gauge , Pressure Relief Device & Sudden pressure relay shall be wired through armoured cable of 1.5 sq.mm (minimum), with Metallic (perforated) type cable tray arrangement. Cable shall be directly connected to the terminals of the above equipment. Double compression type metallic cable gland to be provided. Further, connection of cable including cable glands shall be properly insulated by heat shrinkable sleeve. Suitable arrangement (slope/bottom entry) for cable entry to be provided to avoid water ingress through cable. Gasket for terminal box of above equipment shall be of high temperature withstand material and having adequate thickness. Gasket shall be placed inside the slot/groove). Terminal Box protection class shall be IP 65 (minimum) as per IEC 60529 Sr. No.; Equipment; Contacts (Minimum); Minimum Rating of Micro/limit switch. 1; PRD; 1 NO + 1 NC; DC: 250V, 1A AC: 240V, 3A Dielectric isolation 2500V AC/DC for 1 minute. 2; SPR; 1 NO. 3; MOLG; 1 NO. 4; Buchholz Relay; 1NO for alarm + 1 NO for trip. 5; OTI; 4 NO contacts. 6; WTI; 4 NO contacts. | We wish to inform you that, we have received the non compliance to the additional requirement specified in the section project of the subjected TR11 from the Approved & Standard Vendors of M/s. PGCIL i.e., M/s. Viat & M/s. Sukrut. Hence we request for exculsion of the subjected clause. Note: The Supporting communication received from Suppliers is enclosed for your reference | Bidding documents shall prevail. |
|  |  | SECTION-PROJECT; CL.No.:10 | Amendment for change in destination | Our basis of Freight estimation is based on the delivery locations mentioned in the tender document. In case any change in the location during execution stage, we have considered that Railway Shutdown, Bridge Strengthening, Access Road (motorable) until the site are made available M/s. PGCIL. Please kindly confirm | Scope is ample clear in the bidding document. Bidders are also to refer to Clause -10 of the Section-Project of technical specification. |