| Sl. No. | Clause Reference | Existing Provision | Amended Provision |
| --- | --- | --- | --- |
| 1 | Volume II, Section I, Clause 3, | C; Sag Tension Requirements. 1; Ruling span(m); 304. 2; Maximum sag for ruling span at designed maximum continuous operating temperature corresponding to required ampacity per conductor/ sub-conductor as specified at sl. no. (A) (1) above (m); 5.74. 3; Sag for ruling span at minimum temp (i.e. 2.5°C) (m); 3.95. 4; Tension at every day condition (32°C and no wind) (kg); Not exceeding 25% of UTS of proposed conductor. 5; Tension at 32°C and full wind condition (45 kg/m2 wind pressure); ≤ 2756 kg & not exceeding 50% of UTS of proposed conductor. 6; Tension at 2.5°C and 2/3 wind condition (30 kg/m2 wind pressure); ≤ 3063 kg & not exceeding 50% of UTS of proposed conductor. | C; Sag Tension Requirements. 1; Ruling Span (m); 304. 2; Tension at every day condition (32°C and no wind) (kg); Not exceeding 25% of UTS of proposed conductor. 3; Tension at designed maximum temperature and no wind condition(kg); Not exceeding 25% of UTS at designed maximum temperature. 4; Sag for ruling span at designed maximum temperature & no wind condition (m); ≤5.74. 5; Sag for ruling span at minimum temp (i.e. 2.5°C) and no wind condition (m); ≥3.95. 6; Tension at 32°C and full wind condition (45 kg/m2 wind pressure); ≤ 2756 kg & not exceeding 70% of UTS of proposed conductor. 7; Tension at 2.5°C and 2/3 wind condition (30 kg/m2 wind pressure); ≤ 3063 kg & not exceeding 70% of UTS of proposed conductor. |
|  |  | 7; Tension at designed maximum temperature and no wind condition (kg); Not exceeding 25% of UTS at designed maximum temperature. 8; Tension at designed maximum temperature and full wind condition (45 kg/m2 wind pressure); ≤ 2756 kg & not exceeding 50% of UTS at designed maximum temperature of proposed conductor. 9; Tension at knee point temperature & no wind condition (kg); Not exceeding 40% of UTS of core@ of proposed conductor. @UTS of core shall be equal to the Breaking strength of individual core wires after stranding X no. of wires in the core of offered conductor.. | 8; Tension at designed maximum temperature and full wind condition (45 kg/m2 wind pressure); ≤ 2756 kg & not exceeding 70% of UTS at designed maximum temperature of proposed conductor. 9; Tension at designed maximum temperature and 2/3 wind condition (30 kg/m2 wind pressure); ≤ 3063 kg & not exceeding 70% of UTS at designed maximum temperature of proposed conductor. 10; Tension at knee point temperature & no wind condition (kg); Not exceeding 40% of UTS of core@ of proposed conductor. @UTS of core shall be equal to the Breaking strength of individual core wires after stranding X no. of wires in the core of offered conductor.. |
| 2 | Volume II, Section II, Clause 1.3.1 | Sag of the offered HTLS conductor at designed maximum temperature (corresponding to the specified current per conductor/sub-conductor under ambient conditions specified at 1.4)……………………………………. | Sag of the offered HTLS conductor at designed maximum temperature (i.e. the conductor surface temperature corresponding to the specified current per conductor/sub-conductor under ambient conditions specified at 1.4)……………………………………. |
| 3 | Volume II, Section II, Clause 1.5.1 (ii) | PLSCAD Sagging criteria/ conditions shall be based on the sag tension limits specified in Section-I and shall be carried out in a manner that the above-mentioned sag-tension limits are met in “After Creep” as well as in “After Load” condition. | PLSCAD Sagging criteria/ conditions shall be based on the sag tension limits specified in Section-I and shall be carried out in a manner that the above-mentioned specified sag-tension limits are met in “After Creep” as well as in “After Load” condition. |
| 4 | Volume II, Section-II, Clause 1.4 | …………………………………. The calculations for Ampacity shall be based on IEEE Standard 738-2012 in SI units. …………………….. | ……………………………. The calculations for Ampacity shall generally be based on IEEE Standard 738-2012 in SI units except otherwise specified herein. For calculation of the radial temperature gradient within the conductor, effective thermal conductivity (kth) shall be considered as 1 watt/m-°C. Further, conductor sag at designed maximum temperature shall be calculated considering temperature of core corresponding to the designed maximum temperature of conductor, irrespective of the magnitude of radial temperature gradient. ………………………………… |
| 5 | Volume II, Section-II, Clause 1.9.2.1 | ………………………… In case, the designed maximum temperature of the offered HTLS conductor exceeds 180 deg C, ordinary zinc coating/galvanizing of the Steel/Invar core wires shall not be accepted and only aluminium clad or Mischmetal coated wires shall be permitted. ………………………..The properties & composition of core wires guaranteed by the bidder shall be based on the relevant Indian/International Standards. ……………………… | ………………………..In case, the temperature of core corresponding to the designed maximum temperature of the offered HTLS conductor exceeds 180 deg C, ordinary zinc coating/galvanizing of the Steel/Invar core wires shall not be accepted and only aluminium clad or Mischmetal coated wires shall be permitted. …………………………….The properties & composition of core wires guaranteed by the bidder shall be based on the relevant Indian/International Standards, wherever applicable. ………………….. |
| 6 | Volume II, Section-II, Clause 1.8 | ……………………………. In case of composite core, the tolerances shall be ±0.05 mm as per ASTM B987. | ……………………………………….. In case of composite core conforming to ASTM B987, the tolerances shall be ±0.05 mm. |
| 7 | Volume II, Section II, Annexure A, Clause 1.7 | Sheave test The conductor sample of minimum length of 35 meter shall be tensioned at 20 % of the UTS; pulley diameter shall be 32 times that of the conductor; angle between the pulleys shall be 20 degrees. The conductor shall be passed over the pulleys 36 times a speed of 2 m/sec. After this test UTS test on the conductor shall be carried out as mentioned above at clause 1.1 of Annexure-A. In the case of polymer composite core conductors, the core shall be inspected for damage by subjecting the core to a dye penetration test as per ASTM B987 section 14. Dye penetrant exposure time shall be 30 +1/0 minutes. | Sheave test The conductor sample of minimum length of 35 meter shall be tensioned at 20 % of the UTS; pulley diameter shall be not more than 32 times that of the conductor; angle between the pulleys shall be 20 degrees. The conductor shall be passed over the pulleys 36 times a speed of 2 m/sec. After this test UTS test on the conductor shall be carried out as mentioned above at clause 1.1 of Annexure-A. In the case of polymer composite core conductors, the core shall be inspected for damage by subjecting the core to a dye penetration test as per ASTM B987 section 14. Dye penetrant exposure time shall be 30 +1/0 minutes. |
| 8 | Volume II, Section-II, Clause 2.1.1 i) c) | Radio interference voltage test (dry) | Radio interference voltage test (dry) (Applicable for 220KV & above voltage rating) |
| 9 | Volume II, Section-II, Clause 2.1.1 i) d) | Corona extinction voltage test (dry) | Corona extinction voltage test (dry) (Applicable for 220KV & above voltage rating) |
| 10 | Volume II, Section II, Annexure A, Clause 1.3 | Radio Interference Voltage Test Under the conditions as specified under (1.2) above, the conductor samples shall have radio interference voltage below 1000 microvolts. ……………………. | Radio Interference Voltage Test Under the conditions as specified under (1.2) above, the conductor samples shall have radio interference voltage below 1000 microvolts at one MHz when subjected to 50 Hz AC voltage of 305 kV line to ground under dry conditions for 400kV and 154 kV line to ground under dry conditions for 220kV. ……………. |
| 11 | Volume II, Section II, Annexure A, Clause 1.6 | High Temperature endurance & creep test …………………………………………………………The value of Tg after the test, shall however, in no case be less than the design maximum temperature of conductor. …………………………… | High Temperature endurance & creep test …………………………………………………………The value of Tg after the test, shall however, in no case be less than the temperature of core corresponding to the designed maximum temperature of conductor. ……………………………….. |
| 12 | Volume II, Section II, Annexure A, Clause 1.12 | Temperature Cycle Test ……………………………….The value of Tg after the test, shall however, in no case be less than the design maximum temperature of conductor. | Temperature Cycle Test ………………………………….The value of Tg after the test, shall however, in no case be less than the temperature of core corresponding to the designed maximum temperature of conductor. |
| 13 | Volume II, Section II, Annexure A, Clause 1.16 | Coefficient of linear expansion for core A minimum length of 10 m of entire core (intact) shall be tested. The temperature and elongation on a sample shall be continuously measured and recorded at interval of approximately 15 degree C from 15 degree C to designed maximum temperature corresponding to rated current by changing the temperature by suitable means. Coefficient of linear expansion shall be determined from the measured results. | Coefficient of linear expansion for core A minimum length of 10 m of entire core (intact) shall be tested. The temperature and elongation on a sample shall be continuously measured and recorded at interval of approximately 15 degree C from 15 degree C to the temperature of core corresponding to the designed maximum temperature corresponding to rated current by changing the temperature by suitable means. Coefficient of linear expansion shall be determined from the measured results. |
| 14 | 1.31, Annexure-A | Glass Transition Temperature Test on composite core only (if applicable) Test shall be conducted as per ASTM B987. The minimum glass transition temperature shall be either (i) the design maximum continuous operating temperature of the offered HTLS conductor + 35 Deg C or (ii) minimum glass transition temperature as per ASTM B987 i.e.180 deg. C + 25 Deg C ; Whichever is lower. In case, the design maximum continuous operating temperature of the offered HTLS conductor is more than the minimum glass transition temperature as per ASTM B987 i.e. more than 180 deg. C, the test shall be conducted as per ASTM B987 & the minimum glass transition temperature shall be the design maximum continuous operating temperature of the offered HTLS conductor + 25 Deg C. | Glass Transition Temperature Test on composite core only (if applicable) Test shall be conducted as per ASTM B987. The minimum glass transition temperature shall be either (i) the temperature of core corresponding to the designed maximum continuous operating temperature of the offered HTLS conductor + 35 Deg C or (ii) minimum glass transition temperature as per ASTM B987 i.e.180 deg. C + 25 Deg C ; Whichever is lower. In case, the temperature of core corresponding to the designed maximum continuous operating temperature of the offered HTLS conductor is more than the minimum glass transition temperature as per ASTM B987 i.e. more than 180 deg. C, the test shall be conducted as per ASTM B987 & the minimum glass transition temperature shall be the temperature of core corresponding to the designed maximum continuous operating temperature of the offered HTLS conductor + 25 Deg C. |
| 15 | Volume-III, Technical Data Sheet | Schedule-1 (HTLS Conductor) | Replaced with revised schedule-1, Rev-1 of Schedule-1, Technical Data Sheet attached with this Amendment. |