| Sl. No. | Clause ref. | Existing Provision of the Bidding Document | Query asked by the bidders | POWERGRID’s Clarification |
| --- | --- | --- | --- | --- |
| 1 | Volume II, Section I, Clause 3 | C) Sag Tension Requirements 3. Minimum Sag for ruling span at minimum temp (0 deg C) (m) – 3.95 | Kindly confirm Wind pressure – Full wind / No wind Condition - Either After Load or After Creep | Bidders may refer clause 1.5.1(ii), Section-II of Technical Specification & our earlier clarification issued in this regard. It is further clarified that all the sag – tension limits specified in Section-I of Technical Specification (including minimum sag requirement as specified at sr. no. 3 of clause 3C, Section-I of Technical Specification) shall be met in “After Creep” as well as in “After Load” condition. |