| Sl. No. | Clause Reference | Existing Provision | Amended Provision |
| --- | --- | --- | --- |
| 1 | Volume II, Section I, Clause 3 | Sl. No.; Parameters; Requirement. A(1); Minimum Current carrying capacity/Ampacity at maximum design continuous operating temperature(A); 798. | Sl. No.; Parameters; Requirement. A(1); Minimum Current carrying capacity/Ampacity at maximum design continuous operating temperature(A); 450. |
| 2 | Volume II, Section I, Clause 3 | Sl. No.; Parameters; Requirement. C(3); Minimum Sag for ruling span at minimum temp (0 deg C) (m); 3.95. | Sl. No.; Parameters; Requirement. C(3); Minimum Sag for ruling span at minimum temp (0 deg C) and no wind condition (m); 3.95. |
| 3 | Volume-II, Section-I, Clause 5.3. | Hardware Fittings (except clamp) ---------- Note: ^^ Additional extended warranty in terms of 10% CPG corresponding to cost of the item(s).. ------------- | Hardware Fittings (except clamp)---------- Note: ^^ Additional extended warranty in terms of 3% CPG corresponding to cost of the item(s).------------- |
| 4 | Volume-II, Section-I, Clause 5.4 | Licensor-Licensee conditions:------------- ------------------ ^^ Additional extended warranty in terms of 10% CPG corresponding to cost of the item(s). ------------------ | Licensor-Licensee conditions:------------- ------------------ ^^ Additional extended warranty in terms of 3% CPG corresponding to cost of the item(s). ------------------ |
| 5 | Volume-II, Section-I Attached ‘Forms” | FORM OF JOINT UNDERTAKING BY THE LICENSOR ALONGWITH THE LICENSEE | REVISED ANNEXURE-A: FORM OF JOINT UNDERTAKING BY THE LICENSOR ALONGWITH THE LICENSEE attached at Annexure P |
| 6 | Volume II, Section II, Clause 1.4 | Current Carrying Capacity /Ampacity Requirements The offered HTLS conductor shall be suitable to ……. while satisfying other specified technical requirements/ parameters: - Ambient Conditions; Parameter. …….; ……. Ambient temperature; 450 C. …….; …….. ………… | Current Carrying Capacity /Ampacity Requirements The offered HTLS conductor shall be suitable to ……. while satisfying other specified technical requirements/ parameters: - Ambient Conditions; Parameter. …….; ……. Ambient temperature; 400 C. …….; …….. ……… |
| 7 | Volume II, Section II, Clause 1.9.2.1 | 1.9.2.1 The core wire strand(s) shall be of galvanized steel/ Invar wires/ or ………….. However, the material offered for Steel/ Invar core shall meet following minimum requirements regarding torsion & elongation of core wires: Minimum No. of twists in guage length equal to 100 times the dia. of wire which the strand can withstand in the torsion test (before stranding)*; 16. Minimum elongation (%) of the steel strand (after stranding) for a gauge length of 250 mm (after break); 1.5. *A reduction of 2 number of twists is permitted for after stranding values.. | 1.9.2.1 The core wire strand(s) shall be of galvanized steel/ Invar wires/ or ………….. However, the material offered for Steel/ Invar core shall meet following minimum requirements regarding torsion & elongation of core wires: Minimum No. of twists in gauge length equal to 100 times the dia. of wire which the strand can withstand in the torsion test (before stranding)*; 16. Minimum elongation (%) of the core strand (after stranding) for a gauge length of 250 mm (at break); 1.5. *A reduction of 2 number of twists is permitted for after stranding values.. |
| 8 | Volume II, Section II, Clause 2.13.2, Table Sl. no. 18 | Sl. No.; Indian Standard; Title; International Standard. 18; Ampacity; IEEE 738. | Sl. No.; Indian Standard; Title; International Standard. 18; IEEE Standard for Calculating the Current-Temperature Relationship of Bare Overhead Conductors; IEEE 738:2012. |
| 9 | Volume II, Section II, Clause 2.13.2, Table Sl. no. 20 | Sl. No.; Indian Standard; Title; International Standard. 20; Carbon Fibre Composite core (CFCC/TS) for use in Overhead Electrical Conductors; ASTM B987. | Sl. No.; Indian Standard; Title; International Standard. 20; Carbon Fibre Composite core (CFCC/TS) for use in Overhead Electrical Conductors; ASTM B987-20. |
| 10 | Volume II, Section II, Annexure A, Clause 1.7 | Sheave test The conductor sample of minimum length of 35 meter shall be tensioned at 20 % of the UTS; pulley diameter shall be at least 32 times that of the conductor; angle between the pulleys shall be 20 degrees. The conductor shall be passed over the pulleys 36 times a speed of 2 m/sec. After this test UTS test on the conductor shall be carried out as mentioned above at clause 1.1 of Annexure-A. In the case of polymer composite core conductors, the core shall be inspected for damage by subjecting the core to a dye penetration test as per ASTM B987 section 14. Dye penetrant exposure time shall be 30 +1/0 minutes. | Sheave test The conductor sample of minimum length of 35 meter shall be tensioned at 20 % of the UTS; pulley diameter shall be 32 times that of the conductor; angle between the pulleys shall be 20 degrees. The conductor shall be passed over the pulleys 36 times a speed of 2 m/sec. After this test UTS test on the conductor shall be carried out as mentioned above at clause 1.1 of Annexure-A. In the case of polymer composite core conductors, the core shall be inspected for damage by subjecting the core to a dye penetration test as per ASTM B987 section 14. Dye penetrant exposure time shall be 30 +1/0 minutes. |
| 11 | Volume II, Section II, Clause 1.13 of Annexure-A | Heat Resistance test on Aluminium Alloy wire Breaking load test as per clause 1.24 below shall be carried out before and after heating ….. | Heat Resistance test on Aluminium Alloy wire (not applicable for annealed Aluminium) Breaking load test as per clause 1.24 below shall be carried out before and after heating ….. |
| 12 | Volume II, Section II, Annexure-A, Clause 1.24 | Torsion and Elongation Tests on Core wire/ Composite core The test procedures for Torsion and Elongation Tests on Core wires shall be as per clause No. 6.3.3 and 6.3.2 b) of IEC 61232 respectively. In torsion test, the number of complete twists before fracture shall not be less than the value specified in the GTP on a length equal to 100 times the standard diameter of the strand. In case test sample length is ……………………………………….. In case of composite core HTLS conductor, the following procedure shall be applicable: - i) Elongation Test: ……. ii) Torsion Test: ………. Two samples need to be completed in order to satisfy the testing requirement. | Torsion and Elongation Tests on Core wire/ Composite core The test procedures for Torsion and Elongation Tests on Core wires shall be as per clause No. 6.3.3 and 6.3.2 b) of IEC 61232 respectively. In torsion test, the number of complete twists before fracture shall not be less than the value specified in the GTP on a length equal to 100 times the standard diameter of the strand. In case test sample length is ……………………………………….. In case of composite core HTLS conductor, the following procedure shall be applicable: - i) Elongation Test: ……. ii) Torsion Test: ………. Two samples need to be completed in order to satisfy the testing requirement. Percentage total elongation shall be measured at fracture. |
| 13 | Volume II, Section II, Annexure A, Clause no. 1.26 | Wrap test on Core wires The wrap test on core strands shall meet the requirements of IEC 888. In case of aluminium clad core wire, the same shall be wrapped around a mandrel of diameter of five times that of the strand to form a helix of eight turns. The strand shall be unwrapped. No breakage of strand shall occur. | Wrap test on Core wires (not applicable for composite core) The wrap test on core strands shall meet the requirements of IEC 888. In case of aluminium clad core wire, the same shall be wrapped around a mandrel of diameter of five times that of the strand to form a helix of eight turns. The strand shall be unwrapped. No breakage of strand shall occur. |