| Sl. No. | Clause ref. | Existing Provision of the Bidding Document | Query asked by the bidders | POWERGRID’s Clarification |
| --- | --- | --- | --- | --- |
| 1 | Volume II, Section I, Clause 3 | C) Sag Tension Requirements 3. Minimum Sag for ruling span at minimum temp (0 deg C) (m) – 3.95 | Kindly confirm Wind pressure – Full wind / No wind Condition - Either After Load or After Creep | Refer sl. no. 2 of Amendment no. II. It is clarified that Minimum Sag shall be met under either After Load or After Creep conditions. |
| 2 | Volume-II, Section-I, Clause 5.1 | Technical Qualification Requirement for supplier of core of any special material for high temperature low sag conductor (HTLS) The Conductor manufacturer shall use core of any special material (if used) such as invar steel or composite core supplied from the qualified manufacture(s) meeting the following requirements:- The Qualified Manufacturer should have manufactured, tested and supplied at least two hundred (200) km of the same type of core material as used in the HTLS conductor being offered in the package. Further, conductor manufactured from the supplied core of such manufacturers should have been in satisfactory operation$ for a period of at least two years as on date of NOA. | The Conductor manufacturer shall use core of any special material (if used) such as invar steel or composite core supplied from the qualified manufacture(s) meeting the following requirements: - The Qualified Manufacturer should have manufactured, tested and supplied at least one hundred (100) km of the same type of core material as used in the HTLS conductor being offered in the package. Further, conductor manufactured from the supplied core of such manufacturers should have been in satisfactory operation for a period of at least two years as on date of NOA. | Provisions of the bidding documents remain unchanged. |
| 3 | Volume-II, Section-I, Clause 5.2 | Technical Qualification Requirement for manufacturer(s) of fittings and accessories for high temperature low sag conductor (HTLS) 5.2.1 For Qualified Manufacturer (a) The qualified manufacturer(s) should have designed, manufactured, tested and supplied fittings for suspension & tension strings and accessories for any type of conductor, viz. ACSR, AACSR, AAAC etc. for 220kV or above voltage transmission line. Further, the qualified manufacturer(s) for any individual item(s) of clamp fittings and accessories covered under the package should have designed, manufactured, tested and supplied the item(s) of clamp fittings and accessories for High temperature low sag (HTLS) conductor of same technology as that of the conductor being offered in the package(s) for application on 66 kV or above voltage transmission line and the same should have been in satisfactory operation$ for a minimum period of two (2) years as on date of NOA. The manufacturer(s) meeting the above requirement for any individual item or items shall be considered qualified for the respective item or items only. | Technical Qualification Requirement for manufacturer(s) of fittings and accessories for high temperature low sag conductor (HTLS) 5.2.1 For Qualified Manufacturer (a) The qualified manufacturer(s) should have designed, manufactured, tested and supplied fittings for suspension & tension strings and accessories for any type of conductor, viz. ACSR, AACSR, AAAC etc. for 220kV or above voltage transmission line. Further, the qualified manufacturer(s) for any individual item(s) of clamp fittings and accessories covered under the package should have designed, manufactured, tested and supplied the item(s) of clamp fittings and accessories for High temperature low sag (HTLS) conductor of same technology as that of the conductor being offered in the package(s) for application on 66 kV or above voltage transmission line and the same should have been erected, commissioned and charged in Indian Govt. Utility as on date of NOA. The manufacturer(s) meeting the above requirement for any individual item or items shall be considered qualified for the respective item or items only. | Provisions of the bidding documents remain unchanged. |
| 4 | Volume-II, Section-I, Clause 5.2 | Technical Qualification Requirement for manufacturer(s) of fittings and accessories for high temperature low sag conductor (HTLS) 5.2.1 For Qualified Manufacturer (a) The qualified manufacturer(s) should have designed, manufactured, tested and supplied fittings for suspension & tension strings and accessories for any type of conductor, viz. ACSR, AACSR, AAAC etc. for 220kV or above voltage transmission line. Further, the qualified manufacturer(s) for any individual item(s) of clamp fittings and accessories covered under the package should have designed, manufactured, tested and supplied the item(s) of clamp fittings and accessories for High temperature low sag (HTLS) conductor of same technology as that of the conductor being offered in the package(s) for application on 66 kV or above voltage transmission line and the same should have been in satisfactory operation$ for a minimum period of two (2) years as on date of NOA. The manufacturer(s) meeting the above requirement for any individual item or items shall be considered qualified for the respective item or items only. | Technical Qualification Requirement for manufacturer(s) of fittings and accessories for high temperature low sag conductor (HTLS) 5.2.1 For Qualified Manufacturer (a) The qualified manufacturer(s) should have designed, manufactured, tested and supplied fittings for suspension & tension strings and accessories for any type of conductor, viz. ACSR, AACSR, AAAC etc. for 220kV or above voltage transmission line. Further, the qualified manufacturer(s) for any individual item(s) of clamp fittings and accessories covered under the package should have designed, manufactured, tested and supplied the item(s) of clamp fittings and accessories for High temperature low sag (HTLS) conductor of same technology as that of the conductor being offered in the package(s) for application on 66 kV or above voltage transmission line and the same should have been manufactured, tested, supplied and in operation in any Indian transmission Utility as on date of NOA. The manufacturer(s) meeting the above requirement for any individual item or items shall be considered qualified for the respective item or items only. | Provisions of the bidding documents remain unchanged. |
| 5 | Volume II, Section II, Clause 1.9.2 – Core, point 1.9.2.1 | The material offered for Steel/ Invar core shall meet following minimum requirements regarding torsion & elongation of core wires: Minimum elongation (%)of the steel strand(after stranding)for a gauge length of 250 mm (after break) – 1.5 | Kindly amend the clause as per BS EN 50540 Minimum elongation (%)of the steel strand(before stranding)for a gauge length of 250 mm – 1.5 | Refer sl. no. 7 of Amendment no. II. Minimum elongation (%) of the steel strand (after stranding) shall be measured at break. |
| 6 | Volume II, Section II, Clause 1.9.2 – Core, point 1.9.2. | Bidder shall furnish properties and composition of the core wire strand(s) in the schedule GTP of BPS. The properties & composition of core wires guaranteed by the bidder shall be based on the relevant Indian/International Standards. However, the material offered for Steel/ Invar core shall meet following minimum requirements regarding torsion & elongation of core wires: Minimum No. of twists in gauge length equal to 100 times the dia. of wire which the strand can withstand in the torsion test (before stranding) * - 16 Nos Minimum elongation (%) of the steel strand (after stranding) for a gauge length of 250 mm (after break) – 1.5% | Kindly modify/ remove as mentioned below, Bidder shall furnish properties and composition of the core wire strand(s) in the schedule GTP of BPS. The properties & composition of core wires guaranteed by the bidder shall be based on the relevant Indian/International Standards. However, the material offered for Steel/ Invar core shall meet following minimum requirements regarding torsion & elongation of core wires: Minimum No. of twists in guage length equal to 100 times the dia. of wire which the strand can withstand in the torsion test (before stranding) * - 16 Nos Minimum elongation (%) of the steel strand (after stranding) for a gauge length of 250 mm (after break) – 1.5% | Refer sl. no. 7 of Amendment no. II. Minimum elongation (%) of the steel strand (after stranding) shall be measured at break. |
| 7 | Volume II, Section II, Clause 1.9.2 – Core, point 1.9.2.4 | Where composite material confirming to ASTM B987 is offered for core, the material shall be either of high strength grade or extra high strength grade. The materials shall be of such proven quality that its properties are not adversely influenced by the normal operating conditions of transmission line in tropical environment conditions as experienced by the existing line. The bidder shall provide adequate details including specifications/ test reports/ operating experience details/ performance certificates etc. in support of the suitability of the offered materials. | Please add following, Where composite material confirming to ASTM B987 is offered for core, the material shall be either of high strength grade or extra high strength grade. The offered composite core must have a non-conductive Galvanic Protection Barrier Layer. The materials shall be of such proven quality that its properties are not adversely influenced by the normal operating conditions of transmission line in tropical environment conditions as experienced by the existing line. The bidder shall provide adequate details including specifications/ test reports/ operating experience details/ performance certificates etc. in support of the suitability of the offered materials. | Provisions of the bidding documents remain unchanged. |
| 8 | Volume II, Section II |  | Please add following clause in tender, Evaluation of Ohmic Losses & Differential Price Loading | Provisions of the bidding documents remain unchanged. |
| 9 | Volume II, Section II, Clause 2.1.1, (i), point (n) | Salt Spray Test (applicable for stranded composite core conductors having galvanic protection layer not conforming to ASTMB987) | Please remove this requirement | Provisions of the bidding documents remain unchanged. |
| 10 | Volume II, Section II, Clause 2.1.1, (ii), point (a) | Heat resistance test on Aluminium Alloy strands | Please amend as follows: Heat resistance test on Aluminum Alloy strands or core (Not applicable to Composite Core Conductor) | Refer sl. no. 11 of Amendment no. II. This test is not applicable for Annealed Aluminium strands. |
| 11 | Volume II, Section II, Clause 2.2, point (t) | Galvanic Protection Barrier Layer Thickness test on composite core (applicable for composite core conductors having galvanic barrier layer conforming to ASTM B987) | Please amend as follows; Galvanic Protection Barrier Layer Thickness test on composite core (applicable for composite core conductors having galvanic barrier layer conforming to ASTM B987) | Provisions of the bidding documents remain unchanged. |
| 12 | Volume II, Section II, Clause 2.2, Note | Note: All the above tests except (m) shall be carried out on Aluminium Alloy and core strands after stranding only | Kindly add below mentioned, Note: a. All the above tests except (m) shall be carried out on Aluminium Alloy and core strands after stranding only b. In case of composite core all acceptance shall be done before stranding at core manufacturer stage | Provisions of the bidding documents remain unchanged. |
| 13 | Volume II, Section II, Clause 2.13.2 | Table Sr. No. 18 – Ampacity | Title of IEEE 738 is as follows. Please amend. IEEE Standard for Calculating the Current-Temperature Relationship of Bare Overhead Conductors | Refer sl. no. 8 of Amendment no. II complete title for IEEE 738 added. |
| 14 | Volume 2, section 2, clause 2.13.2 | Carbon Fibre Composite core (CFCC/TS) for use in Overhead Electrical Conductors – ASTM B987 | Carbon Fibre Composite core (CFC/TS) for use in Overhead Electrical Conductors –ASTM B987-17 and -20 | Refer sl. no. 9 of Amendment no. II. complete title for ASTM B987 added. |
| 15 | Volume II, Section II, Annexure A, Clause 1.6 | High Temperature endurance & creep test (ii) On other conductor sample, the conductor temperature shall be increased to designed maximum temperature in steps of 20 deg. C and thermal elongation of the conductor sample shall be measured & recorded at each step. The temperature shall be held at each step for sufficient duration for stablisation of temperature. Further, the temperature of the conductor shall be maintained at designed maximum temperature (+10 Deg. C) for 1000 hours. The elongation/creep strain of the conductor during this period shall be measured and recorded at end of 1 hour, 10 hour, 100 hour and subsequently every 100 hour upto 1000 hours time period. After completion of the above, the conductor sample shall be subjected to UTS test as mentioned above at clause 1.1 of Annexure-A. The conductor core shall withstand a load equivalent to 95 % of UTS. In case of polymer composite core conductor, the flexural strength & glass transition temperature of the core shall also be evaluated and the same shall not be degraded by more than10 % over the value guaranteed in GTP. The value of Tg after the test, shall however, in no case be less than the design maximum temperature of conductor. The supplier shall plot the thermal elongation with temperature. | Please amend as follows; (ii) On other conductor sample, the conductor temperature shall be increased to designed maximum temperature in steps of 20 deg. C and thermal elongation of the conductor sample shall be measured & recorded at each step. The temperature shall be held at each step for sufficient duration for stablisation of temperature. Further, the temperature of the conductor shall be maintained at designed maximum temperature (±2.5 Deg. C) for 1000 hours. The elongation/creep strain of the conductor during this period shall be measured and recorded at end of 1 hour, 10 hour, 100 hour and subsequently every 100 hour upto 1000 hours time period. After completion of the above, the conductor sample shall be subjected to UTS test as mentioned above at clause 1.1 of Annexure-A. The conductor core shall withstand a load equivalent to 95 % of UTS. In case of polymer composite core conductor, the flexural strength & glass transition temperature of the core shall also be evaluated and the same shall not be degraded by more than10 % over the value guaranteed in GTP. The value of Tg after the test, shall however, in no case be less than the design maximum temperature of conductor. The supplier shall plot the thermal elongation with temperature. | Provisions of the bidding documents remain unchanged. |
| 16 | Volume II, Section II, Annexure A, Clause 1.13 | Heat Resistance test on Aluminum Alloy wire | Please amend as follows; Heat Resistance test on Aluminum Alloy wire(only for Aluminum Zirconium alloy) | Refer sl. no. 11 of Amendment no. II. This test is not applicable for Annealed Aluminium strands. |
| 17 | Volume II, Section II, Annexure A, Clause 1.24 | Torsion and Elongation Tests on Core wire/ Composite core ii) Torsion Test : The purpose of the test is to determine the resilience of the composite core to twisting and to show that after the composite core has experienced the prescribed twisting, it will not crack or have a loss in tensile strength due to the twisting. The sample length shall be such that the gauge length in between the gripping fixtures is 170 times the diameter of the core in case of High Strength Grade composite cores and 340 times the diameter of the composite core in case of Extra High strength composite core. However, the gauge length shall not be more than 4m. One grip shall then be fixed so that it does not twist and the other end shall be twisted a full 360 degrees and then fixed in this position for 2 minutes. Once the twist time is completed, the core is untwisted an inspected for any crazing or other damage. If no damage is observed, the composite core is then tensile tested to failure and the final load recorded. For the test to be accepted, the composite core must withstand at least 100% of its rated tensile strength. Two samples need to be completed in order to satisfy the testing requirement. | Please amend as follows; ii) Torsion Test : The purpose of the test is to determine the resilience of the composite core to twisting and to show that after the composite core has experienced the prescribed twisting, it will not crack or have a loss in tensile strength due to the twisting. The sample length shall be such that the gauge length in between the gripping fixtures is 170 times the diameter of the core. For core lengths less than 170 times the core OD, rotate the core to maintain the same rotation to length ratio. In case of High Strength Grade composite cores and 340 times the diameter of the composite core in case of Extra High strength composite core. For core lengths less than 340 times the core OD, rotate the core to maintain the same rotation to length ratio. However, the gauge length shall not be more than 4m. One grip shall then be fixed so that it does not twist and the other end shall be twisted a full 360 degrees and then fixed in this position for 2 minutes. Once the twist time is completed, the core is untwisted an inspected for any crazing or other damage. If no damage is observed, the composite core is then tensile tested to failure and the final load recorded. For the test to be accepted, the composite core must withstand at least 100% of its rated tensile strength. Two samples need to be completed in order to satisfy the testing requirement. | Provisions of the bidding documents remain unchanged. |
| 18 | Volume II, Section II, Annexure A, Clause 1.25 | Breaking load test on Aluminium/ Aluminium Alloy & Composite core/ Core wires and D.C Resistance test on Aluminium/ Aluminium Alloy wire The above tests shall be carried out as per IEC: 888/889 or relevant international standards and the results shall meet the requirements of the specification. | Please add as follow for composite core; For composite cores, the breaking load shall be performed as described in Section 9 of ASTM B987. | Provisions of the bidding documents remain unchanged. It is clarified that Breaking load test can be carried out as per IEC 888/ 889 or relevant international standards including ASTM B987, if applicable. |
| 19 | Volume II, Section II, Annexure A, Clause 1.26 | Wrap test on Core wires | Amend title as, Wrap test on Core wires(for Steel Core wires only) | Refer sl. no. 13 of Amendment no. II. It is clarified that Wrap test is not applicable for composite core. |
| 20 | Volume II, Section II, Annexure A, Clause 1.33 | Bending Test on Polymer Composite Core (Type Test) Bending test on polymer composite core (CFC) before stranding shall be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from composite core at conductor manufacturing unit before stranding of conductor. Alternatively, supplier may carry out bending test on polymer composite core (CFC) before stranding on the samples taken at the core manufacturing unit, from the same reel being supplied to conductor manufacturer subject to proper traceability of the same at the conductor manufacturers works. Bending test on polymer composite core (CFC) shall also be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from stranded conductor. For test after stranding the diameter of cylindrical mandrel shall be as following: For high strength grade CFC – 60 times the diameter of CFC For Extra high strength grade CFC – 70 times the diameter of CFC | Please amend requirement as follows; Bending test on polymer composite core (CFC) shall be performed as per ASTM B987/B987M-17 on polymer composite core samples taken from composite core manufacturing facility from the same reel being supplied to conductor manufacturer subject to proper traceability of the same at the conductor manufacturers works. Alternatively, supplier may carry out bending test on polymer composite core (CFC) samples taken at the conductor manufacturing facility before or after stranding. Bending test on polymer composite core (CFC) of these samples shall also be performed as per ASTM B987/B987M-17, and the diameter of cylindrical mandrel shall be as following: For high strength grade CFC – 60 times the diameter of CFC For Extra high strength grade CFC – 70 times the diameter of CFC | Provisions of the bidding documents remain unchanged. |