## AUX SYSTEM
SCADA SIGNAL LIST FOR VARIOUS PROTECTION & CONTROL SIGNALS - REV03 (AUX SYSTEM)
REQUIRED SIGNALS FOR AUX SYSTEM
IED name:
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS
1 | 415V | STNMN1AUXBCU |  | INT | BCU IN LOCAL/ REMOTE
2 | 415V | STNMN1AUXBCU |  | SPI | DG_CB_OPEN PERMITTED OR ENABLED
3 | 415V | STNMN1AUXBCU |  | SPI | DG_CB_CLOSE PERMITTED OR ENABLED
4 | 415V | STNMN1AUXBCU |  | DPI | DG_CB POSITION
5 | 415V | STNMN1AUXBCU |  | CMD | DG_CB COMMAND |  | CLOSE / OPEN
6 | 415V | STNMN1AUXBCU |  | SPI | MSB_INCOMER_1_CB_OPEN PERMITTED OR ENABLED
7 | 415V | STNMN1AUXBCU |  | SPI | MSB_INCOMER_1_CB_CLOSE PERMITTED OR ENABLED
8 | 415V | STNMN1AUXBCU |  | DPI | MSB_INCOMER_1_CB POSITION
9 | 415V | STNMN1AUXBCU |  | CMD | MSB_INCOMER_1_CB COMMAND |  | CLOSE / OPEN
10 | 415V | STNMN1AUXBCU |  | SPI | MSB_INCOMER_2_CB_OPEN PERMITTED OR ENABLED
11 | 415V | STNMN1AUXBCU |  | SPI | MSB_INCOMER_2_CB_CLOSE PERMITTED OR ENABLED
12 | 415V | STNMN1AUXBCU |  | DPI | MSB_INCOMER_2_CB POSITION
13 | 415V | STNMN1AUXBCU |  | CMD | MSB_INCOMER_2_CB COMMAND |  | CLOSE / OPEN
14 | 415V | STNMN1AUXBCU |  | SPI | MSB_BUSCOUPLER_CB_OPEN PERMITTED OR ENABLED
15 | 415V | STNMN1AUXBCU |  | SPI | MSB_BUSCOUPLER_CB_CLOSE PERMITTED OR ENABLED
16 | 415V | STNMN1AUXBCU |  | DPI | MSB_BUSCOUPLER_CB POSITION
17 | 415V | STNMN1AUXBCU |  | CMD | MSB_BUSCOUPLER_CB COMMAND |  | CLOSE / OPEN
18 | 415V | STNMN1AUXBCU |  | SPI | ACDB_INCOMER_1_CB_OPEN PERMITTED OR ENABLED
19 | 415V | STNMN1AUXBCU |  | SPI | ACDB_INCOMER_1_CB_CLOSE PERMITTED OR ENABLED
20 | 415V | STNMN1AUXBCU |  | DPI | ACDB_INCOMER_1_CB POSITION
21 | 415V | STNMN1AUXBCU |  | CMD | ACDB_INCOMER_1_CB COMMAND |  | CLOSE / OPEN
22 | 415V | STNMN1AUXBCU |  | SPI | ACDB_INCOMER_2_CB_OPEN PERMITTED OR ENABLED
23 | 415V | STNMN1AUXBCU |  | SPI | ACDB_INCOMER_2_CB_CLOSE PERMITTED OR ENABLED
24 | 415V | STNMN1AUXBCU |  | DPI | ACDB_INCOMER_2_CB POSITION
25 | 415V | STNMN1AUXBCU |  | CMD | ACDB_INCOMER_2_CB COMMAND |  | CLOSE / OPEN
26 | 415V | STNMN1AUXBCU |  | SPI | ACDB_BUSCOPULER_CB_OPEN PERMITTED OR ENABLED
27 | 415V | STNMN1AUXBCU |  | SPI | ACDB_BUSCOPULER_CB_CLOSE PERMITTED OR ENABLED
28 | 415V | STNMN1AUXBCU |  | DPI | ACDB_BUSCOPULER_CB POSITION
29 | 415V | STNMN1AUXBCU |  | CMD | ACDB_BUSCOPULER_CB COMMAND |  | CLOSE / OPEN
30 | 415V | STNMN1AUXBCU |  | SPI | HVW_MOTOR_CB_OPEN PERMITTED OR ENABLED
31 | 415V | STNMN1AUXBCU |  | SPI | HVW_MOTOR_CB_CLOSE PERMITTED OR ENABLED
32 | 415V | STNMN1AUXBCU |  | DPI | HVW_MOTOR_CB_ POSITION
33 | 415V | STNMN1AUXBCU |  | CMD | HVW_MOTOR_CB_ COMMAND |  | CLOSE / OPEN
34 | 415V | STNMN1AUXBCU |  | SPI | SEB_33kV_CB_OPEN PERMITTED OR ENABLED
35 | 415V | STNMN1AUXBCU |  | SPI | SEB_33kV_CB_CLOSE PERMITTED OR ENABLED
36 | 415V | STNMN1AUXBCU |  | DPI | SEB_33kV_CB_ POSITION
37 | 415V | STNMN1AUXBCU |  | CMD | SEB_33kV_CB_ COMMAND |  | CLOSE / OPEN
38 | 415V | STNMN1AUXBCU |  | SPI | SEB_33kV_ISOLATOR_OPEN PERMITTED OR ENABLED
39 | 415V | STNMN1AUXBCU |  | SPI | SEB_33kV_ISOLATOR_CLOSE PERMITTED OR ENABLED
40 | 415V | STNMN1AUXBCU |  | DPI | SEB_33kV_ISOLATOR_ POSITION
41 | 415V | STNMN1AUXBCU |  | CMD | SEB_33kV_ISOLATOR_ COMMAND |  | CLOSE / OPEN
42 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO_33kV_CB_OPEN PERMITTED OR ENABLED |  | If the inputs taken in Respecetive ICT Protection/BCU these signals may be omitted.
43 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO_33kV_CB_CLOSE PERMITTED OR ENABLED
44 | 415V | STNMN1AUXBCU |  | DPI | TERTIARY TRAFO_33kV_CB_ POSITION
45 | 415V | STNMN1AUXBCU |  | CMD | TERTIARY TRAFO_33kV_CB_ COMMAND
46 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO_33kV_ISOLATOR_OPEN PERMITTED OR ENABLED
47 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO_33kV_ISOLATOR_CLOSE PERMITTED OR ENABLED
48 | 415V | STNMN1AUXBCU |  | DPI | TERTIARY TRAFO_33kV_ISOLATOR_ POSITION
49 | 415V | STNMN1AUXBCU |  | CMD | TERTIARY TRAFO_33kV_ISOLATOR_ COMMAND
THE LOGICAL NODE INSTANCE NUMBER (SCSWIn/SCILOn) FOR BBREAKERS MAY BE ASSIGNED AS PER AVAILABILITY
50 | 415V | STNMN1AUXBCU |  | AI | DG INCOMER CURRENT L1
51 | 415V | STNMN1AUXBCU |  | AI | DG INCOMER CURRENT L2
52 | 415V | STNMN1AUXBCU |  | AI | DG INCOMER CURRENT L3
53 | 415V | STNMN1AUXBCU |  | AI | DG INCOMER VOLTAGE U12
54 | 415V | STNMN1AUXBCU |  | AI | DG INCOMER VOLTAGE U23
55 | 415V | STNMN1AUXBCU |  | AI | DG INCOMER VOLTAGE U31
56 | 415V | STNMN1AUXBCU |  | AI | DG INCOMER ACTIVE POWER (P)
57 | 415V | STNMN1AUXBCU |  | AI | DG INCOMER REACTIVE POWER (Q)
58 | 415V | STNMN1AUXBCU |  | AI | DG INCOMER POWER FACTOR (PF)
59 | 415V | STNMN1AUXBCU |  | AI | DG INCOMER FREQUENCY (HZ)
60 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-1 CURRENT L1
61 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-1 CURRENT L2
62 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-1 CURRENT L3
63 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-1 VOLTAGE U12
64 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-1 VOLTAGE U23
65 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-1 VOLTAGE U31
66 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-1 ACTIVE POWER (P)
67 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-1 REACTIVE POWER (Q)
68 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-1 POWER FACTOR (PF)
69 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-1 FREQUENCY (HZ)
70 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-2 CURRENT L1
71 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-2 CURRENT L2
72 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-2 CURRENT L3
73 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-2 VOLTAGE U12
74 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-2 VOLTAGE U23
75 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-2 VOLTAGE U31
76 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-2 ACTIVE POWER (P)
77 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-2 REACTIVE POWER (Q)
78 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-2 POWER FACTOR (PF)
79 | 415V | STNMN1AUXBCU |  | AI | MSB INCOMER-2 FREQUENCY (HZ)
80 | 415V | STNMN1AUXBCU |  | AI | 220V CHARGER 1 CURRENT
81 | 415V | STNMN1AUXBCU |  | AI | 220V CHARGER 2 CURRENT
82 | 415V | STNMN1AUXBCU |  | AI | 48V CHARGER 1 CURRENT
83 | 415V | STNMN1AUXBCU |  | AI | 48V CHARGER 2 CURRENT
84 | 415V | STNMN1AUXBCU |  | AI | 220V DCDB 1 VOLTAGE
85 | 415V | STNMN1AUXBCU |  | AI | 220V DCDB 1 CURRENT
86 | 415V | STNMN1AUXBCU |  | AI | 220V DCDB 2 VOLTAGE
87 | 415V | STNMN1AUXBCU |  | AI | 220V DCDB 2 CURRENT
88 | 415V | STNMN1AUXBCU |  | AI | 48V DCDB 1 VOLTAGE
89 | 415V | STNMN1AUXBCU |  | AI | 48V DCDB 1 CURRENT
90 | 415V | STNMN1AUXBCU |  | AI | 48V DCDB 2 VOLTAGE
91 | 415V | STNMN1AUXBCU |  | AI | 48V DCDB 2 CURRENT
92 | 415V | STNMN1AUXBCU |  | SPI | 220V CHARGER-1 ON FLOAT MODE
93 | 415V | STNMN1AUXBCU |  | SPI | 220V CHARGER-1 ON BOAST MODE
94 | 415V | STNMN1AUXBCU |  | SPI | 220V CHARGER 1 TROUBLE | Y | CLOSE / OPEN
95 | 415V | STNMN1AUXBCU |  | SPI | 220V DCDB-1 EARTH FAULT OPTD | Y
96 | 415V | STNMN1AUXBCU |  | SPI | 220V CHARGER-2 ON FLOAT MODE
97 | 415V | STNMN1AUXBCU |  | SPI | 220V CHARGER-2 ON BOAST MODE
98 | 415V | STNMN1AUXBCU |  | SPI | 220V CHARGER 2 TROUBLE | Y
99 | 415V | STNMN1AUXBCU |  | SPI | 220V DCDB-2 EARTH FAULT OPTD | Y
100 | 415V | STNMN1AUXBCU |  | SPI | 48V CHARGER-1 ON FLOAT MODE |  | CLOSE / OPEN
101 | 415V | STNMN1AUXBCU |  | SPI | 48V CHARGER-1 ON BOAST MODE
102 | 415V | STNMN1AUXBCU |  | SPI | 48V CHARGER 1 TROUBLE | Y
103 | 415V | STNMN1AUXBCU |  | SPI | 48V CHARGER-2 ON FLOAT MODE
104 | 415V | STNMN1AUXBCU |  | SPI | 48V CHARGER-2 ON BOAST MODE |  | CLOSE / OPEN
105 | 415V | STNMN1AUXBCU |  | SPI | 48V CHARGER 2 TROUBLE | Y
106 | 415V | STNMN1AUXBCU |  | SPI | 415V INCOMER-1 UNDERVOLTAGE | Y
107 | 415V | STNMN1AUXBCU |  | SPI | 415V INCOMER-2 UNDERVOLTAGE | Y | CLOSE / OPEN
108 | 415V | STNMN1AUXBCU |  | SPI | SEB TRAFO - BUCHHOLZ ALARM | Y
109 | 415V | STNMN1AUXBCU |  | SPI | SEB TRAFO - BUCHHOLZ TRIP | Y
110 | 415V | STNMN1AUXBCU |  | SPI | SEB TRAFO - WTI ALARM | Y
111 | 415V | STNMN1AUXBCU |  | SPI | SEB TRAFO - WTI TRIP | Y
112 | 415V | STNMN1AUXBCU |  | SPI | SEB TRAFO - OTI ALARM | Y
113 | 415V | STNMN1AUXBCU |  | SPI | SEB TRAFO - OTI TRIP | Y
114 | 415V | STNMN1AUXBCU |  | SPI | SEB TRAFO - PRD ALARM | Y
115 | 415V | STNMN1AUXBCU |  | SPI | SEB TRAFO - PRD TRIP | Y
116 | 415V | STNMN1AUXBCU |  | SPI | SEB 33KV_TC-1 FAULTY | Y
117 | 415V | STNMN1AUXBCU |  | SPI | SEB 33KV_TC-2 FAULTY | Y
118 | 415V | STNMN1AUXBCU |  | SPI | SEB 33kV PHASE OVERCURRENT START | Y
119 | 415V | STNMN1AUXBCU |  | SPI | SEB33kV PHASE OVERCURRENT TRIP | Y
120 | 415V | STNMN1AUXBCU |  | SPI | SEB 33kV PHASE EARTHFAULT START | Y
121 | 415V | STNMN1AUXBCU |  | SPI | SEB 33kV PHASE EARTHFAULT TRIP | Y
122 | 415V | STNMN1AUXBCU |  | SPI | SEB 33kV PHASE RESIDUAL OVERVOLTAGE START | Y
123 | 415V | STNMN1AUXBCU |  | SPI | SEB 33kV PHASE RESIDUAL OVERVOLTAGE TRIP | Y
124 | 415V | STNMN1AUXBCU |  | SPI | SEB 33kV 86 OPTD | Y
125 | 415V | STNMN1AUXBCU |  | SPI | SEB 33kV CB ASSOCIATED ALARMS | Y
126 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO - BUCHHOLZ ALARM | Y | If the inputs taken in Respecetive ICT Protection/BCU these signals may be omitted.
127 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO - BUCHHOLZ TRIP | Y
128 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO - WTI ALARM | Y
129 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO - WTI TRIP | Y
130 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO - OTI ALARM | Y
131 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO - OTI TRIP | Y
132 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO - PRD ALARM | Y
133 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO - PRD TRIP | Y
134 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY 33KV_TC-1 FAULTY | Y
135 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY 33KV_TC-2 FAULTY | Y
136 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY 33kV PHASE OVERCURRENT START | Y
137 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY33kV PHASE OVERCURRENT TRIP | Y
138 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY 33kV PHASE EARTHFAULT START | Y
139 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY 33kV PHASE EARTHFAULT TRIP | Y
140 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY 33kV PHASE RESIDUAL OVERVOLTAGE START | Y
141 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY 33kV PHASE RESIDUAL OVERVOLTAGE TRIP | Y
142 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY 33kV 86 OPTD | Y
143 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY 33kV CB ASSOCIATED ALARMS | Y
144 | 415V | STNMN1AUXBCU |  | SPI | AUX INCOMER DC-1 FAULTY | Y
145 | 415V | STNMN1AUXBCU |  | SPI | AUX INCOMER DC-2 FAULTY | Y
146 | 415V | STNMN1AUXBCU |  | SPI | WATER STORAGE TANK-1 LEVEL LOW | Y
147 | 415V | STNMN1AUXBCU |  | SPI | WATER STORAGE TANK-2 LEVEL LOW | Y
148 | 415V | STNMN1AUXBCU |  | SPI | HVW MOTOR DRIVEN PUMP RUNNING
149 | 415V | STNMN1AUXBCU |  | SPI | HVW MOTOR DRIVEN PUMP FAILS TO START | Y
150 | 415V | STNMN1AUXBCU |  | SPI | HVW MOTOR PUMP TRIP FEEDBACK | Y
151 | 415V | STNMN1AUXBCU |  | SPI | DIESEL ENGINE RUNNING
152 | 415V | STNMN1AUXBCU |  | SPI | DIESEL ENGINE FAILS TO START | Y
153 | 415V | STNMN1AUXBCU |  | SPI | DIESEL ENGINE TANK LEVEL LOW | Y
154 | 415V | STNMN1AUXBCU |  | SPI | JOCKEY PUMP -1 RUNNING
155 | 415V | STNMN1AUXBCU |  | SPI | JOCKEY PUMP -2 RUNNING
156 | 415V | STNMN1AUXBCU |  | SPI | JOCKEY PUMP -1 FAILS TO START | Y
157 | 415V | STNMN1AUXBCU |  | SPI | JOCKEY PUMP -2 FAILS TO START | Y
158 | 415V | STNMN1AUXBCU |  | SPI | JOCKEY PUMP O/L TRIP | Y
159 | 415V | STNMN1AUXBCU |  | SPI | JOCKEY PUMP PANEL DC HEALTHY | Y
160 | 415V | STNMN1AUXBCU |  | CMD | HVW MOTORT START
161 | 415V | STNMN1AUXBCU |  | CMD | HVW MOTORT STOP
162 | 415V | STNMN1AUXBCU |  | CMD | DIESEL ENGINE START
163 | 415V | STNMN1AUXBCU |  | CMD | DIESEL ENGINE STOP
164 | 415V | STNMN1AUXBCU |  | CMD | JOCKEY PUMP-1 START
165 | 415V | STNMN1AUXBCU |  | CMD | JOCKEY PUMP-1 STOP
166 | 415V | STNMN1AUXBCU |  | CMD | JOCKEY PUMP-2 START
167 | 415V | STNMN1AUXBCU |  | CMD | JOCKEY PUMP-2 STOP
168 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN ZONE -1 | Y
169 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN ZONE -2 | Y
170 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN ZONE -3 | Y
171 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN ZONE -4 | Y
172 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN ZONE -5 | Y
173 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN ZONE -N | Y
174 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN TRANSFORMER-1 | Y | If the inputs taken in Respecetive ICT Protection/BCU these signals may be omitted.
175 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN TRANSFORMER-2 | Y
176 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN TRANSFORMER-N | Y
177 | 415V | STNMN1AUXBCU |  | CMD | DELUGE COMMAND TO TRANSFORMER-1
178 | 415V | STNMN1AUXBCU |  | CMD | DELUGE COMMAND TO TRANSFORMER-2
179 | 415V | STNMN1AUXBCU |  | CMD | DELUGE COMMAND TO TRANSFORMER-N
180 | 415V | STNMN1AUXBCU |  | SPI | DG DIFFERENTIAL PROT TRIP | Y
181 | 415V | STNMN1AUXBCU |  | SPI | DG OC/EF PROT TRIP | Y
182 | 415V | STNMN1AUXBCU |  | SPI | DG FAIL TO START | Y
183 | 415V | STNMN1AUXBCU |  | SPI | ALTERNATOR ON
184 | 415V | STNMN1AUXBCU |  | SPI | DG LUBE OIL LOW PRESSURE ALARM | Y
185 | 415V | STNMN1AUXBCU |  | SPI | HIGH WATER TEMP TRIP | Y | CLOSE / OPEN
186 | 415V | STNMN1AUXBCU |  | SPI | ENGG. COM FAULT | Y
187 | 415V | STNMN1AUXBCU |  | SPI | LACK OF FUEL ALARM | Y
188 | 415V | STNMN1AUXBCU |  | SPI | DG CHARGER-1 ON
189 | 415V | STNMN1AUXBCU |  | SPI | DG CHARGER-1 OFF | Y | CLOSE / OPEN
190 | 415V | STNMN1AUXBCU |  | SPI | DG CHARGER-2 ON
191 | 415V | STNMN1AUXBCU |  | SPI | DG CHARGER-2 OFF | Y
192 | 415V | STNMN1AUXBCU |  | CMD | DG START/STOP COMMAND |  | CLOSE / OPEN
193 | 415V | STNMN1AUXBCU |  | SPI | AUX INCOMER DC-1 FAULTY | Y
194 | 415V | STNMN1AUXBCU |  | SPI | AUX INCOMER DC-2 FAULTY | Y
195 | 415V | STNMN1AUXBCU |  | SPI | TIME SYNCHRONIZATION ERROR | Y
196 | 415V | STNMN1AUXBCU |  | SPI | BCU UNHEALTHY | Y
197 | 415V | STNMN1AUXBCU |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
198 | 415V | STNMN1AUXBCU |  | SPI | RELAY IN TEST MODE | Y
199 | 415V | STNMN1AUXBCU |  | SPI | SETTINGS CHANGED | Y
200 | 415V | STNMN1AUXBCU |  | SPI | DR MEMMORY 80% FULL | Y
201 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-1 |  | ** 20 nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
202 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-2
203 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-3
204 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-4
205 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-5
206 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-6
207 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-7
208 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-8
209 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-9
210 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-10
211 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-11
212 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-12
213 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-13
214 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-14
215 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-15
216 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-16
217 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-17
218 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-18
219 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-19
220 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-20
ADDITIONAL SIGNAL FOR CB TROUBLE ETC AS PER SCHEME
** 20 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database