## Rev History
Hitachi/ABB Standard Signal List
Sl. No | Description | Revision | Remarks
1 | Standard Signals for 765kV Level | Rev-00
2 | Standard Signals for 400kV Level | Rev-00
3 | Standard Signals for 220kV Level | Rev-00
4 | Standard Signals for Aux System | Rev-00
Revision History
Rev.No | Description of Remarks | Date | Remarks
01 | Initital Release | 16.01.2024

## INDEX
ABB SCADA GENERAL SIGNAL LIST FOR VARIOUS PROTECTION & CONTROL SIGNALS - REV03 (INDEX)
BAY | IED MODEL | IED SYMBOLIC NAME | APPLICATION | IED NAME IN SCD
LINE | REC670 | R_REC670_BCU | Bay Control Unit | STNMB1Q01LBCU
| REL670 | R_REL670_21M1 | Main 1 Distance Protection | STNMB1Q01M1DIS
| ** | R_RELAY NAME_21M2 | Main 2 Distance Protection | **
ICT | REC670 | R_REC670_BCU | Bay Control Unit | STNMB1Q01TBCU
| RET670 | R_RET670_87T | Differential Protection | STNMB1Q01TDIF
| RET670 | R_RET670_64 | Restricted Earthfault Protection | STNMB1Q01TREF
| REL670 | R_REL670_BIMP | HV Backup Impedance Protection | STNMB1Q01THVBIMP
| REL670 | R_REL670_BIMP | LV Backup Impedance Protection | STNMB1Q01TLVBIMP
| REL670 | R_REL670_HVBUP | HV Backup OC/EF Protection | STNMB1Q01THBU
| REL670 | R_REL670_LVBUP | LV Backup OC/EF Protection | STNMB1Q01TLBU
BUSREACTOR | REC670 | R_REC670_BCU | Bay Control Unit | STNMB1Q01BRBCU
| RET670 | R_RET670_87R | Differential Protection | STNMB1Q01BRDIF
| RET670 | R_RET670_64R | Restricted Earthfault Protection | STNMB1Q01BRREF
| REL670 | R_REL670_BIMP | Backup Impedance Protection | STNMB1Q01BRBIMP
LINE REACTOR | REC670 | R_REC670_BCU | Bay Control Unit | STNMB1Q01LRBCU
| RET670 | R_RET670_87R | Differential Protection | STNMB1Q01LRDIF
| RET670 | R_RET670_64R | Restricted Earthfault Protection | STNMB1Q01LRREF
| REL670 | R_REL670_BIMP | Backup Impedance Protection | STNMB1Q01LRBIMP
TIE | REC670 | R_REC670_BCU | Bay Control Unit | STNMB1Q01TIEBCU
LBB | REL670 | R_RELAY NAME_50BFR | Breaker Failure Protection | STNMB1Q01BFR
BUSBAR PROTECTION (DECENTRALIZED) | REB500 | BB_REB500_87BM1 | Main1 Busbar Protection | STNMB1BBM1
| REB500 | BB_REB500_87BM2 | Main2 Busbar Protection | STNMB1BBM2
BUSBAR PROTECTION (CENTRALIZED) | REB670 | BB_REB670_87BM1 | Main1 Busbar Protection | STNMB1BBM1
| REB670 | BB_REB670_87BM2 | Main2 Busbar Protection | STNMB1BBM2
NOTE 1: The characters "STNM" stand for Substation Name with maximum 4 characters, this code will be given by POWERGRID for each project.
NOTE 2: The characters "B1" stand for Voltage level, this will be vary based on station voltage level eg. B1 for 765kV, C1 for 400kV & D1 for 220kV etc…
NOTE 3: The characters "Q01" stand for Bay Number, this will be vary based on Bay number eg. Q01 for BAY01, Q02 for BAY02 etc…
NOTE 4: ** Line Main2 Distance protection IED name will be subject to provision availability of maximum number of characters in the IED

## SIGNAL STANDARDIZATION FOR 765
ABB SCADA SIGNAL LIST FOR VARIOUS PROTECTION & CONTROL SIGNALS - REV03 (765kV)
REQUIRED SIGNALS FOR DISTANCE RELAYS
| IED name: | R_REL670_21M1
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/OV2_1/OV2PTOV1/Str/general | SPI | OVERVOLATGE STAGE 1 START
2 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/OV2_1/OV2PTOV1/Op/general | SPI | OVERVOLATGE STAGE 1 TRIP | Y
3 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/OV2PTOV2/Str/general | SPI | OVER VOLTAGE STAGE-2 START | Y |  | Addition | Agreed
4 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/OV2_1/OV2PTOV2/Op/general | SPI | OVERVOLATGE STAGE 2 TRIP | Y
5 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/EF4_1/EF4PTOC1/Str/general | SPI | DEF START
6 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/EF4_1/EF4PTOC1/Op/general | SPI | DEF TRIP | Y
7 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/STBPTOC1/Op/general | SPI | STUB PROTECTION OPERATED | Y | Applicable for One and Half CB Busbar system
8 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCVPSOF1/Op/general | SPI | SOTF OPERATED | Y
9 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Str/general | SPI | START, Z1
10 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/general | SPI | START, Z2
11 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsA | SPI | START, Z2 R PH
12 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsB | SPI | START, Z2 Y PH
13 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsC | SPI | START, Z2 B PH
14 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS3/Str/general | SPI | START, Z3
15 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS4/Str/general | SPI | START, Z4(REVERSE) |  | ** Whichever the zone choses as Reverse | Text correction | Agreed
16 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS5/Str/general | SPI | START, Z5
17 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/general | SPI | GENERAL TRIP, Z1 | Y
18 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsA | SPI | TRIP, Z1 R PH | Y
19 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsB | SPI | TRIP, Z1 Y PH | Y
20 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsC | SPI | TRIP, Z1 B PH | Y
21 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/general | SPI | GENERAL TRIP, Z2 | Y
22 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsA | SPI | TRIP, Z2 R PH | Y
23 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsB | SPI | TRIP, Z2 Y PH | Y
24 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsC | SPI | TRIP, Z2 B PH | Y
25 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS3/Op/general | SPI | GENERAL TRIP, Z3 | Y
26 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS4/Op/general | SPI | GENERAL TRIP, Z4(REVERSE) | Y | ** Whichever the zone choses as Reverse | Text correction | Agreed
27 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS5/Op/general | SPI | GENERAL TRIP, Z5 | Y
28 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/ProTx/stVal | SPI | CARRIER SEND | Y
29 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/ProRx/stVal | SPI | CARRIER RECEIVE | Y
30 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/Op/general | SPI | CARRIER AIDED SCHEME OPERATED | Y
31 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMRPSB1/Str/general | SPI | POWER SWING DETECTED | Y
32 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMRPSB1/BlkZn/stVal | SPI | POWER SWING BLOCKING | Y
33 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SMPPTRC1/Op/general | SPI | DISTANCE RELAY GENERAL TRIP | Y
34 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | R PHASE FAULT | Y |  | Addition | Agreed
35 | 765kV | STNMB1Q01M1DIS |  | SPI | Y PHASE FAULT | Y |  | Addition | Agreed
36 | 765kV | STNMB1Q01M1DIS |  | SPI | B PHASE FAULT | Y |  | Addition | Agreed
37 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltDiskm/mag | DINT | FAULT LOCATOR DISTANCE
38 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltZ/cVal.mag | DINT | FAULT LOCATOR IMPEDANCE
39 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
40 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/BRCPTOC1/Op/general | SPI | BROKEN CONDUCTOR ALARM | Y
41 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
42 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/LPHD1/PhyHealth/stVal | SPI | M1 IED UNHEALTHY | Y
43 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | START AR TO BCU |  |  | Text correction | Agreed
44 | 765kV | STNMB1Q01M1DIS |  | SPI | BLOCK AR TO BCU |  |  | Text correction | Agreed
45 | 765kV | STNMB1Q01M1DIS |  | SPI | LINE ISOLATOR OPEN FOR STUB ACTIVATION |  | Applicable for One and Half CB Busbar system
46 | 765kV | STNMB1Q01M1DIS |  | SPI | DT SEND CH 1 | Y
47 | 765kV | STNMB1Q01M1DIS |  | SPI | DT SEND CH 2 | Y
48 | 765kV | STNMB1Q01M1DIS |  | SPI | DT RECEIVE CH 1 | Y |  |  | Only for DR in REL670, for SCADA to be configured from BCU
49 | 765kV | STNMB1Q01M1DIS |  | SPI | DT RECEIVE CH 2 | Y |  |  | Only for DR in REL670, for SCADA to be configured from BCU
50 | 765kV | STNMB1Q01M1DIS |  | SPI | TRIP RELAY 86 A HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
51 | 765kV | STNMB1Q01M1DIS |  | SPI | TRIP RELAY 86 B HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
52 | 765kV | STNMB1Q01M1DIS |  | SPI | GR A RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in REL670, for SCADA to be configured from BCU
53 | 765kV | STNMB1Q01M1DIS |  | SPI | GR B RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in REL670, for SCADA to be configured from BCU
54 | 765kV | STNMB1Q01M1DIS |  | SPI | CARRIER RECEIVE CH-1 | Y
55 | 765kV | STNMB1Q01M1DIS |  | SPI | CARRIER RECEIVE CH-2 | Y
56 | 765kV | STNMB1Q01M1DIS |  | SPI | CARRIER CHANNEL 1 OUT OF SERVICE | Y
57 | 765kV | STNMB1Q01M1DIS |  | SPI | CARRIER CHANNEL 2 OUT OF SERVICE | Y
58 | 765kV | STNMB1Q01M1DIS |  | SPI | CARRIER CHANNEL 1 FAIL | Y
59 | 765kV | STNMB1Q01M1DIS |  | SPI | CARRIER CHANNEL 2 FAIL | Y
60 | 765kV | STNMB1Q01M1DIS |  | SPI | MAIN 2/1 RELAY FAIL | Y
61 | 765kV | STNMB1Q01M1DIS |  | SPI | CB CLOSE COMMAND FOR SOTF INITIATION |  |  | Text correction
62 | 765kV | STNMB1Q01M1DIS |  | SPI | BCU RELAY FAIL | Y
63 | 765kV | STNMB1Q01M1DIS |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
64 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsA | SPI | START, Z1 R PH |  |  | Addition
65 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsB | SPI | START, Z1 Y PH |  |  | Addition
66 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsC | SPI | START, Z1 B PH |  |  | Addition
67 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP 3PH | Y |  | Addition
68 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP R PH | Y |  | Addition
69 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP Y PH | Y |  | Addition
70 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP B PH | Y |  | Addition
71 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | PREPARE 3-PH TRIP FROM TIE BCU | Y |  | Addition, Available in BCU | It is also required in REL670
72 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | PREPARE 3-PH TRIP FROM MAIN BCU | Y |  | Addition, Available in BCU | It is also required in REL670
73 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | MAIN/ TIE CB AR OPTD | Y |  | Addition, Available in BCU | Only for DR in REL670, for SCADA to be configured from BCU
74 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | MAIN/TIE LBB PROTECTION OPERATED | Y |  | Addition, Available in BBP | Only for DR in REL670, for SCADA to be configured from LBB/BBP relay
75 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | BUSBAR M1/M2 OPTD | Y |  | Addition, Available in BBP | Only for DR in REL670, for SCADA to be configured from BBP relay
76 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | GROUP RELAY 86A OPTD | Y |  | Available in REL670 (Sig. 52) | Agreed
77 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/EchoWei/stVal | SPI | WEAK INFEED ECHO SEND | Y |  | Addition
78 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/EchoWeiOp/stVal | SPI | WEAK INFEED TRIP | Y |  | Addition
79 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/RvABlk/stVal | SPI | CURRENT REVERSAL DETECTED | Y |  | Addition
80 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
81 | 765kV | STNMB1Q01M1DIS |  | SPI | SETTINGS CHANGED | Y |  | Addition
82 | 765kV | STNMB1Q01M1DIS |  | SPI | DR MEMMORY 80% FULL | Y |  | Addition
83 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltDiskm/mag | AI | DISTANCE MEASUREMENT IN KM | Y |  | Available in REL670 (Sig. 37) | Agreed
84 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltZ/cVal/mag | AI | DISTANCE MEASUREMENT IN IMPEDANCE | Y |  | Available in REL670 (Sig. 38) | Agreed
85 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/MON/L4UFCNTn/CntVal/actVal | AI | CH-1 Code-1 Tx (MAIN-1 CARRIER RECEIVE CHANNEL-1) |  |  | CH-1 Code-1 Tx (MAIN-1 CARRIER SEND CHANNEL-1)
86 | 765kV | STNMB1Q01M1DIS |  | AI | CH-1 Code-1 Rx (MAIN-1 CARRIER SEND CHANNEL-1) |  |  | CH-1 Code-1 Rx (MAIN-1 CARRIER RECEIVE CHANNEL-1)
87 | 765kV | STNMB1Q01M1DIS |  | AI | CH-1 Code-2 Tx (MAIN-2 CARRIER RECEIVE CHANNEL-1) |  |  | CH-1 Code-2 Tx (MAIN-2 CARRIER SEND CHANNEL-1)
88 | 765kV | STNMB1Q01M1DIS |  | AI | CH-1 Code-2 Rx (MAIN-2 CARRIER SEND CHANNEL-1) |  |  | CH-1 Code-2 Rx (MAIN-2 CARRIER RECEIVE CHANNEL-1)
89 | 765kV | STNMB1Q01M1DIS |  | AI | CH-2 Code-2 Tx (MAIN-2 CARRIER RECEIVE CHANNEL-2) |  |  | CH-2 Code-2 Tx (MAIN-2 CARRIER SEND CHANNEL-2)
90 | 765kV | STNMB1Q01M1DIS |  | AI | CH-2 Code-2 Rx (MAIN-2 CARRIER SEND CHANNEL-2) |  |  | CH-2 Code-2 Rx (MAIN-2 CARRIER RECEIVECHANNEL-2)
91 | 765kV | STNMB1Q01M1DIS |  | AI | CH-2 Code-1 Tx (MAIN-1 CARRIER RECEIVE CHANNEL-2) |  |  | CH-2 Code-1 Tx (MAIN-1 CARRIER SEND CHANNEL-2)
92 | 765kV | STNMB1Q01M1DIS |  | AI | CH-2 Code-1 Rx (MAIN-1 CARRIER SEND CHANNEL-2) |  |  | CH-2 Code-1 Rx (MAIN-1 CARRIER RECEIVE CHANNEL-2)
93 | 765kV | STNMB1Q01M1DIS |  | AI | CH-1 Code-3 Tx (DT RECEIVE CHANNEL-1) |  |  | CH-1 Code-3 Tx (DT SEND CHANNEL-1)
94 | 765kV | STNMB1Q01M1DIS |  | AI | CH-1 Code-3 Rx (DT SEND CHANNEL-1) |  |  | CH-1 Code-3 Rx (DT RECEIVE CHANNEL-1)
95 | 765kV | STNMB1Q01M1DIS |  | AI | CH-2 Code-3 Tx (DT RECEIVE CHANNEL-2) |  |  | CH-2 Code-3 Tx (DT SEND CHANNEL-2)
96 | 765kV | STNMB1Q01M1DIS |  | AI | CH-2 Code-3 Rx (DT SEND CHANNEL-2) |  |  | CH-2 Code-3 Rx (DT RECEIVE CHANNEL-2)
97 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
98 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-2 | Y |  | Addition
99 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-3 | Y |  | Addition
100 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-4 | Y |  | Addition
101 | 765kV | STNMB1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-5 | Y |  | Addition
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR ICT DIFFERENTIAL RELAYS
| IED name: | R_RET670_87T
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/OEXPVPH1/Str/general | SPI | OVEREXCITATION HV START
2 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/OEXPVPH1/Alm/stVal | SPI | OVEREXCITATION HV ALARM | Y
3 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/OEXPVPH1/Op/general | SPI | OVEREXCITATION HV TRIP | Y
4 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/DifAlm/stVal | SPI | DIFFERENTIAL CURRENT ALARM | Y
5 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/general | SPI | DIFFERENTIAL PROTECTION START
6 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsA | SPI | DIFFERENTIAL PROTECTION RPH START
7 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsB | SPI | DIFFERENTIAL PROTECTION YPH START
8 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsC | SPI | DIFFERENTIAL PROTECTION BPH START
9 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Op/general | SPI | DIFFERENTIAL PROTECTION TRIP | Y
10 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION RPH TRIP | Y
11 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION YPH TRIP | Y
12 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION BPH TRIP | Y
13 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/OpRst/stVal | SPI | DIFFERENTIAL PROTECTION TRIP (RESTRAINED MODE) | Y
14 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/OpUnRst/stVal | SPI | DIFFERENTIAL PROTECTION TRIP (UNRESTRAINED MODE) | Y
15 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Blk2H/stVal | SPI | DIFFERENTIAL PROTECTION 2nd HARMONIC BLOCK
16 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Blk5H/stVal | SPI | DIFFERENTIAL PROTECTION 5th HARMONIC BLOCK
17 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SMPPTRC1/Op/general | SPI | DIFFERENTIAL RELAY GENERAL TRIP | Y
18 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
19 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/LPHD1/PhyHealth/stVal | SPI | DIFFRENTIAL IED UNHEALTHY | Y
20 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | OTI ALARM | Y | APPLICABLE FOR 3 PHASE TRANSFORMERS
21 | 765kV | STNMB1Q01TDIF |  | SPI | WTI HV ALARM | Y
22 | 765kV | STNMB1Q01TDIF |  | SPI | WTI IV ALARM | Y
23 | 765kV | STNMB1Q01TDIF |  | SPI | WTI MV ALARM | Y
24 | 765kV | STNMB1Q01TDIF |  | SPI | BUCCHOLZ_n ALARM | Y |  | Addition
25 | 765kV | STNMB1Q01TDIF |  | SPI | BUCCHOLZ_n TRIP | Y |  | Text correction
26 | 765kV | STNMB1Q01TDIF |  | SPI | OSR _n TRIP | Y |  | Text correction
27 | 765kV | STNMB1Q01TDIF |  | SPI | PRD _n TRIP | Y |  | Text correction
28 | 765kV | STNMB1Q01TDIF |  | SPI | FIRE PROTECTION OPERATED | Y
29 | 765kV | STNMB1Q01TDIF |  | SPI | LOW OIL LEVEL | Y
30 | 765kV | STNMB1Q01TDIF |  | SPI | OTI R PH ALARM | Y | APPLICABLE FOR SINGLE PHASE TRANSFORMERS (If a dedicated IED is provided for spare transformer protection, only spare phase signals are required to be used)
31 | 765kV | STNMB1Q01TDIF |  | SPI | OTI Y PH ALARM | Y
32 | 765kV | STNMB1Q01TDIF |  | SPI | OTI B PH ALARM | Y
33 | 765kV | STNMB1Q01TDIF |  | SPI | OTI SPARE ICT ALARM | Y
34 | 765kV | STNMB1Q01TDIF |  | SPI | WTI HV R PH ALARM | Y
35 | 765kV | STNMB1Q01TDIF |  | SPI | WTI HV Y PH ALARM | Y
36 | 765kV | STNMB1Q01TDIF |  | SPI | WTI HV B PH ALARM | Y
37 | 765kV | STNMB1Q01TDIF |  | SPI | WTI HV SPARE ICT ALARM | Y
38 | 765kV | STNMB1Q01TDIF |  | SPI | WTI MV R PH ALARM | Y
39 | 765kV | STNMB1Q01TDIF |  | SPI | WTI MV Y PH ALARM | Y
40 | 765kV | STNMB1Q01TDIF |  | SPI | WTI MV B PH ALARM | Y
41 | 765kV | STNMB1Q01TDIF |  | SPI | WTI MV SPARE ICT ALARM | Y
42 | 765kV | STNMB1Q01TDIF |  | SPI | WTI IV R PH ALARM | Y
43 | 765kV | STNMB1Q01TDIF |  | SPI | WTI IV Y PH ALARM | Y
44 | 765kV | STNMB1Q01TDIF |  | SPI | WTI IV B PH ALARM | Y
45 | 765kV | STNMB1Q01TDIF |  | SPI | WTI IV SPARE ICT ALARM | Y
46 | 765kV | STNMB1Q01TDIF |  | SPI | BUCHHOLZ_n R PH ALARM | Y |  | Addition
47 | 765kV | STNMB1Q01TDIF |  | SPI | BUCHHOLZ_n Y PH ALARM | Y |  | Addition
48 | 765kV | STNMB1Q01TDIF |  | SPI | BUCHHOLZ_n B PH ALARM | Y |  | Addition
49 | 765kV | STNMB1Q01TDIF |  | SPI | BUCHHOLZ_n SPARE ICT TRIP | Y |  | Addition, BUCHHOLZ_n SPARE ICT ALARM
50 | 765kV | STNMB1Q01TDIF |  | SPI | BUCHHOLZ_n R PH TRIP | Y |  | Text correction
51 | 765kV | STNMB1Q01TDIF |  | SPI | BUCHHOLZ_n Y PH TRIP | Y |  | Text correction
52 | 765kV | STNMB1Q01TDIF |  | SPI | BUCHHOLZ_n B PH TRIP | Y |  | Text correction
53 | 765kV | STNMB1Q01TDIF |  | SPI | BUCHHOLZ_n SPARE ICT TRIP | Y |  | Text correction
54 | 765kV | STNMB1Q01TDIF |  | SPI | OSR_n R PH TRIP | Y |  | Text correction
55 | 765kV | STNMB1Q01TDIF |  | SPI | OSR_n Y PH TRIP | Y |  | Text correction
56 | 765kV | STNMB1Q01TDIF |  | SPI | OSR_n B PH TRIP | Y |  | Text correction
57 | 765kV | STNMB1Q01TDIF |  | SPI | OSR_n SPARE ICT TRIP | Y |  | Text correction
58 | 765kV | STNMB1Q01TDIF |  | SPI | PRD n R PH TRIP | Y |  | Text correction
59 | 765kV | STNMB1Q01TDIF |  | SPI | PRD nY PH TRIP | Y |  | Text correction
60 | 765kV | STNMB1Q01TDIF |  | SPI | PRD n B PH TRIP | Y |  | Text correction
61 | 765kV | STNMB1Q01TDIF |  | SPI | PRD n SPARE ICT TRIP | Y |  | Text correction
62 | 765kV | STNMB1Q01TDIF |  | SPI | LOW OIL LEVEL R PH | Y
63 | 765kV | STNMB1Q01TDIF |  | SPI | LOW OIL LEVEL Y PH | Y
64 | 765kV | STNMB1Q01TDIF |  | SPI | LOW OIL LEVEL B PH | Y
65 | 765kV | STNMB1Q01TDIF |  | SPI | LOW OIL LEVEL SPARE ICT | Y
66 | 765kV | STNMB1Q01TDIF |  | SPI | FIRE PROTECTION R PH OPERATED | Y
67 | 765kV | STNMB1Q01TDIF |  | SPI | FIRE PROTECTION Y PH OPERATED | Y
68 | 765kV | STNMB1Q01TDIF |  | SPI | FIRE PROTECTION B PH OPERATED | Y
69 | 765kV | STNMB1Q01TDIF |  | SPI | FIRE PROTECTION SPARE ICT OPERATED | Y
70 | 765kV | STNMB1Q01TDIF |  | SPI | TRIP RELAY 86 A HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
71 | 765kV | STNMB1Q01TDIF |  | SPI | TRIP RELAY 86 B HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
72 | 765kV | STNMB1Q01TDIF |  | SPI | GR A RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RET670, for SCADA to be configured from BCU
73 | 765kV | STNMB1Q01TDIF |  | SPI | GR B RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RET670, for SCADA to be configured from BCU
74 | 765kV | STNMB1Q01TDIF |  | SPI | REF RELAY FAIL | Y
75 | 765kV | STNMB1Q01TDIF |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
** It may be noted that the Body Protection alarms & trips have been Grouped into two separate relays Differential (Group A) & REF (Group B) relays. The hardwiring for same must be done accordingly and approved scheme shall be modified if required. Same is applicable for Reactor protection also.
76 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/OC4_1/OC4PTOC1/Str/general | SPI | TERTIARY 33kV PHASE OVERCURRENT START | Y |  | Addition
77 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/OC4_1/OC4PTOC1/Op/general | SPI | TERTIARY33kV PHASE OVERCURRENT TRIP | Y |  | Addition
78 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/EF4_1/EF4PTOC1/Str/general | SPI | TERTIARY 33kV PHASE EARTHFAULT START | Y |  | Addition
79 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/EF4_1/EF4PTOC1/Op/general | SPI | TERTIARY 33kV PHASE EARTHFAULT TRIP | Y |  | Addition
80 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/ROV2_1/ROV2PTOV1/Str/general | SPI | TERTIARY 33kV PHASE RESIDUAL OVERVOLTAGE START | Y |  | Addition
81 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/ROV2_1/ROV2PTOV1/OP/general | SPI | TERTIARY 33kV PHASE RESIDUAL OVERVOLTAGE TRIP | Y |  | Addition
82 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | TERTIARY 33kV 86 OPTD | Y |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
83 | 765kV | STNMB1Q01TDIF |  | SPI | TERTIARY TRAFO - BUCHHOLZ ALARM | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
84 | 765kV | STNMB1Q01TDIF |  | SPI | TERTIARY TRAFO - BUCHHOLZ TRIP | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
85 | 765kV | STNMB1Q01TDIF |  | SPI | TERTIARY TRAFO - WTI ALARM | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
86 | 765kV | STNMB1Q01TDIF |  | SPI | TERTIARY TRAFO - WTI TRIP | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
87 | 765kV | STNMB1Q01TDIF |  | SPI | TERTIARY TRAFO - OTI ALARM | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
88 | 765kV | STNMB1Q01TDIF |  | SPI | TERTIARY TRAFO - OTI TRIP | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
89 | 765kV | STNMB1Q01TDIF |  | SPI | TERTIARY TRAFO - PRD ALARM | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
90 | 765kV | STNMB1Q01TDIF |  | SPI | TERTIARY TRAFO - PRD TRIP | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
91 | 765kV | STNMB1Q01TDIF |  | SPI | TERTIARY 33KV_TC-1 FAULTY | Y |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
92 | 765kV | STNMB1Q01TDIF |  | SPI | TERTIARY 33KV_TC-2 FAULTY | Y |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
93 | 765kV | STNMB1Q01TDIF |  | SPI | TERTIARY 33kV CB ASSOCIATED ALARMS | Y |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
94 | 765kV | STNMB1Q01TDIF |  | SPI | RELAY IN TEST MODE | Y |  | Addition
95 | 765kV | STNMB1Q01TDIF |  | SPI | SETTINGS CHANGED | Y |  | Addition
96 | 765kV | STNMB1Q01TDIF |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
97 | 765kV | STNMB1Q01TDIF |  | CMD | DELUGE COMMAND |  | APPLICABLE FOR 3 PHASE TRANSFORMERS | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
98 | 765kV | STNMB1Q01TDIF |  | CMD | DELUGE COMMAND R PH |  | APPLICABLE FOR SINGLE PHASE TRANSFORMERS (If a dedicated IED is provided for spare transformer protection, only spare phase signals are required to be used) | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
99 | 765kV | STNMB1Q01TDIF |  | CMD | DELUGE COMMAND Y PH |  |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
100 | 765kV | STNMB1Q01TDIF |  | CMD | DELUGE COMMAND B PH |  |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
101 | 765kV | STNMB1Q01TDIF |  | CMD | DELUGE COMMAND SPARE |  |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
102 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL//EF4_1/EF4PTOC2/Str/general | SPI | NEUTRAL OVERCURRENT ALARM | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
103 | 765kV | STNMB1Q01TDIF | SS_BAY_DIFFERENTIAL//LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
104 | 765kV | STNMB1Q01TDIF |  | SPI | SPARE ALARM-2 | Y |  | Addition
105 | 765kV | STNMB1Q01TDIF |  | SPI | SPARE ALARM-3 | Y |  | Addition
106 | 765kV | STNMB1Q01TDIF |  | SPI | SPARE ALARM-4 | Y |  | Addition
107 | 765kV | STNMB1Q01TDIF |  | SPI | SPARE ALARM-5 | Y |  | Addition
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR ICT REF RELAYS
| IED name: | R_RET670_64
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 765kV | STNMB1Q01TREF | SS_BAY_REF/LD0/OEXPVPH1/Str/general | SPI | OVEREXCITATION MV START
2 | 765kV | STNMB1Q01TREF | SS_BAY_REF/LD0/OEXPVPH1/Alm/stVal | SPI | OVEREXCITATION MV ALARM | Y
3 | 765kV | STNMB1Q01TREF | SS_BAY_REF/LD0/OEXPVPH1/Op/general | SPI | OVEREXCITATION MV TRIP | Y
4 | 765kV | STNMB1Q01TREF | SS_BAY_REF/LD0/HZPDIF1/Alm/stVal | SPI | REF ALARM
5 | 765kV | STNMB1Q01TREF | SS_BAY_REF/LD0/HZPDIF1/Op/general | SPI | REF TRIP | Y
6 | 765kV | STNMB1Q01TREF | SS_BAY_REF/LD0/SMPPTRC1/Op/general | SPI | REF RELAY GENERAL TRIP | Y
7 | 765kV | STNMB1Q01TREF | SS_BAY_REF/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
8 | 765kV | STNMB1Q01TREF | SS_BAY_REF/LD0/LPHD1/PhyHealth/stVal | SPI | REF IED UNHEALTHY | Y
9 | 765kV | STNMB1Q01TREF | SS_BAY_REF/LD0/SP16GGIO n/Ind n/stVal | SPI | OTI TRIP | Y | APPLICABLE FOR 3 PHASE TRANSFORMERS
10 | 765kV | STNMB1Q01TREF |  | SPI | WTI HV TRIP | Y
11 | 765kV | STNMB1Q01TREF |  | SPI | WTI MV TRIP | Y
12 | 765kV | STNMB1Q01TREF |  | SPI | WTI LV TRIP | Y
13 | 765kV | STNMB1Q01TREF |  | SPI | OSR 2 TRIP | Y
14 | 765kV | STNMB1Q01TREF |  | SPI | PRD 2 TRIP | Y
15 | 765kV | STNMB1Q01TREF |  | SPI | BUCCHOLZ_n ALARM | Y |  | Text correction
16 | 765kV | STNMB1Q01TREF |  | SPI | BUCCHOLZ_n TRIP | Y |  | Addition
17 | 765kV | STNMB1Q01TREF |  | SPI | OTI R PH TRIP | Y | APPLICABLE FOR SINGLE PHASE TRANSFORMERS (If a dedicated IED is provided for spare transformer protection, only spare phase signals are required to be used)
18 | 765kV | STNMB1Q01TREF |  | SPI | OTI Y PH TRIP | Y
19 | 765kV | STNMB1Q01TREF |  | SPI | OTI B PH TRIP | Y
20 | 765kV | STNMB1Q01TREF |  | SPI | OTI SPARE ICT TRIP | Y
21 | 765kV | STNMB1Q01TREF |  | SPI | WTI HV R PH TRIP | Y
22 | 765kV | STNMB1Q01TREF |  | SPI | WTI HV Y PH TRIP | Y
23 | 765kV | STNMB1Q01TREF |  | SPI | WTI HV B PH TRIP | Y
24 | 765kV | STNMB1Q01TREF |  | SPI | WTI HV SPARE ICT TRIP | Y
25 | 765kV | STNMB1Q01TREF |  | SPI | WTI MV R PH TRIP | Y
26 | 765kV | STNMB1Q01TREF |  | SPI | WTI MV Y PH TRIP | Y
27 | 765kV | STNMB1Q01TREF |  | SPI | WTI MV B PH TRIP | Y
28 | 765kV | STNMB1Q01TREF |  | SPI | WTI MV SPARE ICT TRIP | Y
29 | 765kV | STNMB1Q01TREF |  | SPI | WTI IV R PH TRIP | Y
30 | 765kV | STNMB1Q01TREF |  | SPI | WTI IV Y PH TRIP | Y
31 | 765kV | STNMB1Q01TREF |  | SPI | WTI IV B PH TRIP | Y
32 | 765kV | STNMB1Q01TREF |  | SPI | WTI IV SPARE ICT TRIP | Y
33 | 765kV | STNMB1Q01TREF |  | SPI | BUCCHOLZ R PH ALARM | Y
34 | 765kV | STNMB1Q01TREF |  | SPI | BUCCHOLZ Y PH ALARM | Y
35 | 765kV | STNMB1Q01TREF |  | SPI | BUCCHOLZ B PH ALARM | Y
36 | 765kV | STNMB1Q01TREF |  | SPI | BUCCHOLZ SPARE ICT ALARM | Y
37 | 765kV | STNMB1Q01TREF |  | SPI | OSR 2 R PH TRIP | Y
38 | 765kV | STNMB1Q01TREF |  | SPI | OSR 2 Y PH TRIP | Y
39 | 765kV | STNMB1Q01TREF |  | SPI | OSR 2 B PH TRIP | Y
40 | 765kV | STNMB1Q01TREF |  | SPI | OSR 2 SPARE ICT TRIP | Y
41 | 765kV | STNMB1Q01TREF |  | SPI | PRD 2 R PH TRIP | Y
42 | 765kV | STNMB1Q01TREF |  | SPI | PRD 2 Y PH TRIP | Y
43 | 765kV | STNMB1Q01TREF |  | SPI | PRD 2 B PH TRIP | Y
44 | 765kV | STNMB1Q01TREF |  | SPI | PRD 2 SPARE ICT TRIP | Y
45 | 765kV | STNMB1Q01TREF |  | SPI | DIFFERENTIAL RELAY FAIL | Y
46 | 765kV | STNMB1Q01TREF |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
47 | 765kV | STNMB1Q01TREF |  | SPI | RELAY IN TEST MODE | Y |  | Addition
48 | 765kV | STNMB1Q01TREF |  | SPI | SETTINGS CHANGED | Y |  | Addition
49 | 765kV | STNMB1Q01TREF |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
50 | 765kV | STNMB1Q01TREF |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
51 | 765kV | STNMB1Q01TREF |  | SPI | SPARE ALARM-2 | Y |  | Addition
52 | 765kV | STNMB1Q01TREF |  | SPI | SPARE ALARM-3 | Y |  | Addition
53 | 765kV | STNMB1Q01TREF |  | SPI | SPARE ALARM-4 | Y |  | Addition
54 | 765kV | STNMB1Q01TREF |  | SPI | SPARE ALARM-5 | Y |  | Addition
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR ICT BACKUP HV IMPEDANCE PROTECTION RELAY | [7 empty] | Additional Relay - Impedance Protection Signals are part of ICT REF PROTECTION RELAY
| IED name: | R_REL670_21T
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/ZMCAPDIS1/Str/phsA | SPI | BACKUP IMPEDANCE START, Z1 R PH
2 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/ZMCAPDIS1/Str/phsB | SPI | BACKUP IMPEDANCE START, Z1 Y PH
3 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMPE/LD0/ZMCAPDIS1/Str/phsC | SPI | BACKUP IMPEDANCE START, Z1 B PH
4 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS1.Str.general | SPI | BACKUP IMPEDANCE START |  |  | BACKUP IMPEDANCE ZONE-1 START | Agreed
5 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS1.Op.general | SPI | BACKUP IMPEDANCE ZONE-1 TRIP | Y
6 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/ZMCAPDIS2/Str/phsA | SPI | BACKUP IMPEDANCE START, Z2 R PH
7 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/ZMCAPDIS2/Str/phsB | SPI | BACKUP IMPEDANCE START, Z2 Y PH
8 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMPE/LD0/ZMCAPDIS2/Str/phsC | SPI | BACKUP IMPEDANCE START, Z2 B PH
9 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS2.Str.general | SPI | BACKUP IMPEDANCE ZONE-2 START
10 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS2.Op.general | SPI | BACKUP IMPEDANCE ZONE-2 TRIP | Y
11 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS3.Str.general | SPI | BACKUP IMPEDANCE ZONE-3 START
12 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS3.Op.general | SPI | BACKUP IMPEDANCE ZONE-3 TRIP | Y
13 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS4.Str.general | SPI | BACKUP IMPEDANCE ZONE-4 START
14 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS4.Op.general | SPI | BACKUP IMPEDANCE ZONE-4 TRIP | Y
15 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SMPPTRC1/Op/general | SPI | BACKUP IMPEDANCE RELAY GENERAL TRIP | Y
16 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/OC4_1/OC4PTOC1/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 START |  |  | OC/EF PROTECTION SIGNALS ARE PART OF HV DIRECTIONAL OVERCURRENT & EARTHFAULT PROTECTION RELAY
17 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/OC4_1/OC4PTOC1/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 TRIP | Y
18 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/EF4_1/EF4PTOC1/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 START
19 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/EF4_1/EF4PTOC1/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 TRIP | Y
20 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/OC4_1/OC4PTOC2/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 START
21 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/OC4_1/OC4PTOC2/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 TRIP | Y
22 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/EF4_1/EF4PTOC2/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 START
23 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/EF4_1/EF4PTOC2/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 TRIP | Y
24 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SMPPTRC/*** | SPI | BACKUP IMPEDANCE GENERAL TRIP 3PH | Y
25 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SMPPTRC/*** | SPI | BACKUP IMPEDANCE GENERAL TRIP R PH | Y
26 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SMPPTRC/*** | SPI | BACKUP IMPEDANCE GENERAL TRIP Y PH | Y
27 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SMPPTRC/*** | SPI | BACKUP IMPEDANCE GENERAL TRIP B PH | Y
28 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
29 | 765kV | STNMB1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
30 | 765kV | STNMB1Q01THVBIMP |  | SPI | BACKUP IMPEDANCE IED UNHEALTHY | Y
31 | 765kV | STNMB1Q01THVBIMP |  | SPI | RELAY IN TEST MODE | Y
32 | 765kV | STNMB1Q01THVBIMP |  | SPI | SETTINGS CHANGED | Y
33 | 765kV | STNMB1Q01THVBIMP |  | SPI | DR MEMORY 80% FULL | Y
34 | 765kV | STNMB1Q01THVBIMP |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
35 | 765kV | STNMB1Q01THVBIMP |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
36 | 765kV | STNMB1Q01THVBIMP |  | SPI | SPARE ALARM-2 | Y
37 | 765kV | STNMB1Q01THVBIMP |  | SPI | SPARE ALARM-3 | Y
38 | 765kV | STNMB1Q01THVBIMP |  | SPI | SPARE ALARM-4 | Y
39 | 765kV | STNMB1Q01THVBIMP |  | SPI | SPARE ALARM-5 | Y
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR ICT BACKUP IV IMPEDANCE PROTECTION RELAY
| IED name: | R_REL670_21T
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 765kV |  | SS_BAY_LV BACKUP IMP/LD0/ZMCAPDIS1/Str/phsA | SPI | BACKUP IMPEDANCE START, Z1 R PH
2 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0/ZMCAPDIS1/Str/phsB | SPI | BACKUP IMPEDANCE START, Z1 Y PH
3 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMPE/LD0/ZMCAPDIS1/Str/phsC | SPI | BACKUP IMPEDANCE START, Z1 B PH
4 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0.ZMHPDIS1.Str.general | SPI | BACKUP IMPEDANCE START |  |  | BACKUP IMPEDANCE ZONE-1 START | Agreed
5 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0.ZMHPDIS1.Op.general | SPI | BACKUP IMPEDANCE ZONE-1 TRIP | Y
6 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0/ZMCAPDIS2/Str/phsA | SPI | BACKUP IMPEDANCE START, Z2 R PH
7 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0/ZMCAPDIS2/Str/phsB | SPI | BACKUP IMPEDANCE START, Z2 Y PH
8 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMPE/LD0/ZMCAPDIS2/Str/phsC | SPI | BACKUP IMPEDANCE START, Z2B PH
9 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0.ZMHPDIS2.Str.general | SPI | BACKUP IMPEDANCE ZONE-2 START
10 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0.ZMHPDIS2.Op.general | SPI | BACKUP IMPEDANCE ZONE-2 TRIP | Y
11 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0.ZMHPDIS3.Str.general | SPI | BACKUP IMPEDANCE ZONE-3 START
12 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0.ZMHPDIS3.Op.general | SPI | BACKUP IMPEDANCE ZONE-3 TRIP | Y
13 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0.ZMHPDIS4.Str.general | SPI | BACKUP IMPEDANCE ZONE-4 START
14 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0.ZMHPDIS4.Op.general | SPI | BACKUP IMPEDANCE ZONE-4 TRIP | Y
15 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0/SMPPTRC1/Op/general | SPI | BACKUP IMPEDANCE RELAY GENERAL TRIP | Y
16 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/OC4_1/OC4PTOC1/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 START
17 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/OC4_1/OC4PTOC1/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 TRIP | Y
18 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/EF4_1/EF4PTOC1/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 START
19 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/EF4_1/EF4PTOC1/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 TRIP | Y
20 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/OC4_1/OC4PTOC2/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 START
21 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/OC4_1/OC4PTOC2/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 TRIP | Y
22 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/EF4_1/EF4PTOC2/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 START
23 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/EF4_1/EF4PTOC2/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 TRIP | Y
24 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0/SMPPTRC/*** | SPI | BACKUP IMPEDANCE GENERAL TRIP 3PH | Y
25 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0/SMPPTRC/*** | SPI | BACKUP IMPEDANCE GENERAL TRIP R PH | Y
26 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0/SMPPTRC/*** | SPI | BACKUP IMPEDANCE GENERAL TRIP Y PH | Y
27 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0/SMPPTRC/*** | SPI | BACKUP IMPEDANCE GENERAL TRIP B PH | Y
28 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
29 | 765kV | STNMB1Q01TLVBIMP | SS_BAY_LV BACKUP IMP/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
30 | 765kV | STNMB1Q01TLVBIMP |  | SPI | BACKUP IMPEDANCE IED UNHEALTHY | Y
31 | 765kV | STNMB1Q01TLVBIMP |  | SPI | RELAY IN TEST MODE | Y
32 | 765kV | STNMB1Q01TLVBIMP |  | SPI | SETTINGS CHANGED | Y
33 | 765kV | STNMB1Q01TLVBIMP |  | SPI | DR MEMORY 80% FULL | Y
34 | 765kV | STNMB1Q01TLVBIMP |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
35 | 765kV | STNMB1Q01TLVBIMP |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
36 | 765kV | STNMB1Q01TLVBIMP |  | SPI | SPARE ALARM-2 | Y
37 | 765kV | STNMB1Q01TLVBIMP |  | SPI | SPARE ALARM-3 | Y
38 | 765kV | STNMB1Q01TLVBIMP |  | SPI | SPARE ALARM-4 | Y
39 | 765kV | STNMB1Q01TLVBIMP |  | SPI | SPARE ALARM-5 | Y
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR HV DIRECTIONAL OVERCURRENT AND EARTH FAULT RELAYS
| IED name: | R_REL670_HVBUP
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 765kV | STNDB1Q01THBU | SS_BAY_HV BACKUP OC EF/OC4_1/OC4PTOC1/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 START |  |  | Text correction
2 | 765kV | STNDB1Q01THBU | SS_BAY_HV BACKUP OC EFE/OC4_1/OC4PTOC1/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 TRIP | Y |  | Text correction
3 | 765kV | STNDB1Q01THBU | SS_BAY_HV BACKUP OC EF/EF4_1/EF4PTOC1/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 START |  |  | Text correction
4 | 765kV | STNDB1Q01THBU | SS_BAY_HV BACKUP OC EF/EF4_1/EF4PTOC1/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 TRIP | Y |  | Text correction
5 | 765kV | STNDB1Q01THBU | SS_BAY_HV BACKUP OC EF/OC4_1/OC4PTOC2/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 START |  | if Non Directional then name has to be replaced with Directional to Non-Directional | Addition
6 | 765kV | STNDB1Q01THBU | SS_BAY_HV BACKUP OC EF/OC4_1/OC4PTOC2/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 TRIP | Y |  | Addition
7 | 765kV | STNDB1Q01THBU | SS_BAY_HV BACKUP OC EF/EF4_1/EF4PTOC2/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 START |  |  | Addition
8 | 765kV | STNDB1Q01THBU | SS_BAY_HV BACKUP OC EF/EF4_1/EF4PTOC2/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 TRIP | Y |  | Addition
9 | 765kV | STNDB1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
10 | 765kV | STNDB1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/SMPPTRC1/Op/general | SPI | GENERAL TRIP | Y
11 | 765kV | STNDB1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
12 | 765kV | STNDB1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/LPHD1/PhyHealth/stVal | SPI | BACKUP OC/EF IED UNHEALTHY | Y
13 | 765kV | STNDB1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/SP16GGIO n/Ind n/stVal | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
14 | 765kV | STNDB1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
15 | 765kV | STNDB1Q01THBU |  | SPI | SETTINGS CHANGED | Y |  | Addition
16 | 765kV | STNDB1Q01THBU |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
17 | 765kV | STNDB1Q01THBU |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
18 | 765kV | STNDB1Q01THBU |  | SPI | SPARE ALARM-2 | Y |  | Addition
19 | 765kV | STNDB1Q01THBU |  | SPI | SPARE ALARM-3 | Y |  | Addition
20 | 765kV | STNDB1Q01THBU |  | SPI | SPARE ALARM-4 | Y |  | Addition
21 | 765kV | STNDB1Q01THBU |  | SPI | SPARE ALARM-5 | Y |  | Addition
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR LV DIRECTIONAL OVERCURRENT AND EARTH FAULT RELAYS | [7 empty] | This Protection Signals are part of ICT BACKUP IV IMPEDANCE PROTECTION RELAY
| IED name: | R_REL670_LVBUP
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 765kV | STNMB1Q01TLBU | SS_BAY_LV BACKUP OC EF/OC4_1/OC4PTOC1/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 START |  |  | Text correction
2 | 765kV | STNMB1Q01TLBU | SS_BAY_LV BACKUP OC EFE/OC4_1/OC4PTOC1/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 TRIP | Y |  | Text correction
3 | 765kV | STNMB1Q01TLBU | SS_BAY_LV BACKUP OC EF/EF4_1/EF4PTOC1/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 START |  |  | Text correction
4 | 765kV | STNMB1Q01TLBU | SS_BAY_LV BACKUP OC EF/EF4_1/EF4PTOC1/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 TRIP | Y |  | Text correction
5 | 765kV | STNMB1Q01TLBU | SS_BAY_LV BACKUP OC EF/OC4_1/OC4PTOC2/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 START |  | if Non Directional then name has to be replaced with Directional to Non-Directional | Addition
6 | 765kV | STNMB1Q01TLBU | SS_BAY_LV BACKUP OC EF/OC4_1/OC4PTOC2/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 TRIP | Y |  | Addition
7 | 765kV | STNMB1Q01TLBU | SS_BAY_LV BACKUP OC EF/EF4_1/EF4PTOC2/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 START |  |  | Addition
8 | 765kV | STNMB1Q01TLBU | SS_BAY_LV BACKUP OC EF/EF4_1/EF4PTOC2/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 TRIP | Y |  | Addition
9 | 765kV | STNMB1Q01TLBU | SS_BAY_LV BACKUP OC EF/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
10 | 765kV | STNMB1Q01TLBU | SS_BAY_LV BACKUP OC EF/LD0/SMPPTRC1/Op/general | SPI | GENERAL TRIP | Y
11 | 765kV | STNMB1Q01TLBU | SS_BAY_LV BACKUP OC EF/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
12 | 765kV | STNMB1Q01TLBU | SS_BAY_LV BACKUP OC EF/LD0/LPHD1/PhyHealth/stVal | SPI | BACKUP OC/EF IED UNHEALTHY | Y
13 | 765kV | STNMB1Q01TLBU | SS_BAY_LV BACKUP OC EF/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
14 | 765kV | STNMB1Q01TLBU |  | SPI | SETTINGS CHANGED | Y |  | Addition
15 | 765kV | STNMB1Q01TLBU |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
16 | 765kV | STNMB1Q01TLBU |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR REACTOR DIFFERENTIAL RELAYS
| IED name: | R_RET670_87R
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Op/general | SPI | DIFFERENTIAL PROTECTION TRIP | Y
2 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION RPH TRIP | Y
3 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION YPH TRIP | Y
4 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION BPH TRIP | Y
5 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/DifAlm/stVal | SPI | DIFFERENTIAL CURRENT ALARM | Y
6 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/general | SPI | DIFFERENTIAL PROTECTION START
7 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsA | SPI | DIFFERENTIAL PROTECTION RPH START
8 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsB | SPI | DIFFERENTIAL PROTECTION YPH START
9 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsC | SPI | DIFFERENTIAL PROTECTION BPH START
10 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SMPPTRC1/Op/general | SPI | DIFFERENTIAL RELAY GENERAL TRIP | Y
11 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/OpRst/stVal | SPI | DIFFERENTIAL PROTECTION TRIP (RESTRAINED MODE) | Y |  | Addition
12 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/OpUnRst/stVal | SPI | DIFFERENTIAL PROTECTION TRIP (UNRESTRAINED MODE) | Y |  | Addition
13 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Blk2H/stVal | SPI | DIFFERENTIAL PROTECTION 2nd HARMONIC BLOCK | Y |  | Addition
14 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Blk5H/stVal | SPI | DIFFERENTIAL PROTECTION 5th HARMONIC BLOCK | Y |  | Addition
15 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | BUSBAR PROT OPTD | Y |  | Addition, Need to discuss | Only for DR in RET670, for SCADA to be configured from BBP relay
16 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
17 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | DIFFRENTIAL IED UNHEALTHY | Y |  |  | *
18 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | OTI TRIP | Y | APPLICABLE FOR 3 PHASE REACTORS | Interchanged between Diff. & REF relays
19 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | WTI ALARM | Y |  | Already available
20 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | BUCCHOLZ-A TRIP | Y |  | Addition
21 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | BUCCHOLZ-B ALARM | Y |  | Addition
22 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | PRV-1 TRIP(NO) | Y |  | Text correction
23 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | FIRE PROTECTION OPERATED | Y |  | Already available
24 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | LOW OIL LEVEL ALARM | Y |  | Already available
25 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | PRV-1 TRIP(NC) | Y |  | Addition, Need to discuss | Yet to be finalized by PGCIL
26 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | FLOW SENSITIVE CONSERVATOR VALVE ALARM | Y |  | Addition
27 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | REACTOR MB ALARMS | Y |  | Addition
28 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | OTI R PH ALARM | Y | APPLICABLE FOR SINGLE PHASE REACTORS (If a dedicated IED is provided for spare reactor protection, only spare phase signals are required to be used)
29 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | OTI Y PH ALARM | Y
30 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | OTI B PH ALARM | Y
31 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | OTI SPARE PH ALARM | Y
32 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | WTI R PH ALARM | Y
33 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | WTI Y PH ALARM | Y
34 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | WTI B PH ALARM | Y
35 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | WTI SPARE PH ALARM | Y
36 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | BUCCHOLZ_n R PH ALARM | Y |  | Interchanged between Diff. & REF relays
37 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | BUCCHOLZ_n Y PH ALARM | Y |  | Interchanged between Diff. & REF relays
38 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | BUCCHOLZ_n B PH ALARM | Y |  | Interchanged between Diff. & REF relays
39 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | BUCCHOLZ_n SPARE PH ALARM | Y |  | Interchanged between Diff. & REF relays
40 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | BUCCHOLZ_n R PH TRIP | Y |  | Text correction
41 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | BUCCHOLZ_n Y PH TRIP | Y |  | Text correction
42 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | BUCCHOLZ_n B PH TRIP | Y |  | Text correction
43 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | BUCCHOLZ_n SPARE PH TRIP | Y |  | Text correction
44 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | OSR R PH TRIP | Y
45 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | OSR Y PH TRIP | Y
46 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | OSR B PH TRIP | Y
47 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | OSR SPARE PH TRIP | Y
48 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | PRD R PH TRIP | Y |  |  | Yet to be finalized by PGCIL
49 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | PRD Y PH TRIP | Y |  |  | Yet to be finalized by PGCIL
50 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | PRD B PH TRIP | Y |  |  | Yet to be finalized by PGCIL
51 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | PRD SPARE PH TRIP | Y
52 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | LOW OIL LEVEL R PH | Y
53 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | LOW OIL LEVEL Y PH | Y
54 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | LOW OIL LEVEL B PH | Y
55 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | LOW OIL LEVEL SPARE PH | Y
56 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | FIRE PROTECTION R PH OPERATED | Y
57 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | FIRE PROTECTION Y PH OPERATED | Y
58 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | FIRE PROTECTION B PH OPERATED | Y
59 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | FIRE PROTECTION SPARE OPERATED | Y
60 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | TRIP RELAY 86 A HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
61 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | TRIP RELAY 86 B HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
62 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | GR A RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RET670, for SCADA to be configured from BBP relay
63 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | GR B RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RET670, for SCADA to be configured from BBP relay
64 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | GR A RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Available in RET670 (Sig. 62)
65 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | GR B RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Available in RET670 (Sig. 63)
66 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | REF RELAY FAIL | Y
67 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | RELAY IN TEST MODE | Y |  | Addition
68 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | SETTINGS CHANGED | Y |  | Addition
69 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
70 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
71 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
72 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | SPARE ALARM-2 | Y |  | Addition
73 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | SPARE ALARM-3 | Y |  | Addition
74 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | SPARE ALARM-4 | Y |  | Addition
75 | 765kV | STNMB1Q01LRDIF /STNMB1Q01BRDIF |  | SPI | SPARE ALARM-5 | Y |  | Addition
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR REACTOR REF RELAYS
| IED name: | R_RET670_64R
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF | SS_BAY_REF/LD0/HZPDIF1/Alm/stVal | SPI | REF ALARM
2 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF | SS_BAY_REF/LD0/HZPDIF1/Op/general | SPI | REF TRIP | Y
3 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF | SS_BAY_REF/LD0/SMPPTRC1/Op/general | SPI | REF RELAY GENERAL TRIP | Y
4 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF | SS_BAY_REF/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
5 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF | SS_BAY_REF/LD0/LPHD1/PhyHealth/stVal | SPI | REF IED UNHEALTHY | Y
6 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF | SS_BAY_REF/LD0/SP16GGIO n/Ind n/stVal | SPI | OTI ALARM | Y | APPLICABLE FOR 3 PHASE REACTORS | Interchanged between Diff. & REF relays
7 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | WTI TRIP | Y |  | Already available
8 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | BUCCHOLZ-A ALARM | Y |  | Addition
9 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | BUCCHOLZ-B TRIP | Y |  | Addition
10 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | PRV-2 TRIP | Y |  | Addition
11 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | FIRE PROTECTION OPERATED | Y |  | Addition
12 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | HIGH LEVEL OIL ALARM | Y |  | Addition
13 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | 86B TRIP RELAY SUPERVSION ALARM | Y |  | Addition, Need to discuss
14 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | REACTOR MB ALARMS | Y |  | Addition
15 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | OTI R PH TRIP | Y | APPLICABLE FOR SINGLE PHASE REACTORS (If a dedicated IED is provided for spare Reactor protection, only spare phase signals are required to be used)
16 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | OTI Y PH TRIP | Y
17 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | OTI B PH TRIP | Y
18 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | OTI SPARE PH TRIP | Y
19 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | WTI R PH TRIP | Y
20 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | WTI Y PH TRIP | Y
21 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | WTI B PH TRIP | Y
22 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | WTI SPARE PH TRIP | Y
23 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | BUCCHOLZ R PH ALARM | Y
24 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | BUCCHOLZ Y PH ALARM | Y
25 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | BUCCHOLZ B PH ALARM | Y
26 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | BUCCHOLZ SPARE PH ALARM | Y
27 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | DIFFERENTIAL RELAY FAIL | Y
28 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | RELAY IN TEST MODE | Y |  | Addition
29 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | SETTINGS CHANGED | Y |  | Addition
30 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
31 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
32 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | SPARE ALARM-2 | Y |  | Addition
33 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | SPARE ALARM-3 | Y |  | Addition
34 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | SPARE ALARM-4 | Y |  | Addition
35 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | SPARE ALARM-5 | Y |  | Addition
36 | 765kV | STNMB1Q01LRREF /STNMB1Q01BRREF |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR REACTOR BACKUP IMPEDANCE PROTECTION RELAY
| IED name: | R_REL670_21R
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/LD0.ZMHPDIS1.Str.general | SPI | BACKUP IMPEDANCE START
2 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/LD0.ZMHPDIS1.Op.general | SPI | BACKUP IMPEDANCE TRIP | Y
3 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/LD0/SMPPTRC1/Op/general | SPI | BACKUP IMPEDANCE RELAY GENERAL TRIP | Y
4 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/OC4_1/OC4PTOC1/Str/general | SPI | BACKUP OVERCURRENT START
5 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/OC4_1/OC4PTOC1/Op/general | SPI | BACKUP OVERCURRENT TRIP | Y
6 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/EF4_1/EF4PTOC1/Str/general | SPI | BACKUP EARTHFAULT START
7 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/EF4_1/EF4PTOC1/Op/general | SPI | BACKUP EARTHFAULT TRIP | Y
8 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
9 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
10 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/LD0/LPHD1/PhyHealth/stVal | SPI | BACKUP IMPEDANCE IED UNHEALTHY | Y
11 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP | SS_BAY_HV BACKUP OC EF/LD0/LPHD1/PhyHealth/stVal | SPI | NGR BUCHHOLZ ALARM | Y | For Line Reactor NGR associated alarms | Addition
12 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | NGR BUCHHOLZ TRIP | Y |  | Addition
13 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | NGR OTI ALARM | Y |  | Addition
14 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | NGR OTI TRIP | Y |  | Addition
15 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | NGR WTI ALARM | Y |  | Addition
16 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | NGR WTI TRIP | Y |  | Addition
17 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | NGR OSR TRIP | Y |  | Addition
18 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | NGR CB ASSOCIATED ALARMS | Y | All NGC CB associated alarms to be monitored | Addition
19 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | NGR BYPASS ISOLATOR ASSOCIATED ALARMS | Y | All NGR Bypass Isolator associated alarms to be monitored | Addition
20 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | BACKUP IMPEDANCE IED UNHEALTHY | Y |  | Addition
21 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | CMD | NGR BYPASS COMMAND | Y |  | Addition
22 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | RELAY IN TEST MODE | Y |  | Addition
23 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | SETTINGS CHANGED | Y |  | Addition
24 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | DR MEMMORY 80% FULL | Y |  | Addition
25 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
26 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
27 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | SPARE ALARM-2 | Y |  | Addition
28 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | SPARE ALARM-3 | Y |  | Addition
29 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | SPARE ALARM-4 | Y |  | Addition
30 | 765kV | STNMB1Q01LRBIMP /STNMB1Q01LRBIMP |  | SPI | SPARE ALARM-5 | Y |  | Addition
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR BUSBAR PROTECTION RELAYS (DECENTRALIZED) - REB 500
| IED name: | BB_REB500_87B
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/BCZ_PDIF1/DifAlm | SPI | BUSBAR CHECKZONE ALARM | Y |  | Addition
2 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/BCZ_PDIF1/Op/general | SPI | BUSBAR CHECKZONE TRIP | Y |  | Addition
3 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/CALH1/GrAlm2/stVal | SPI | BUSBAR CT CIRCUIT ERROR | Y |  |  | Agreed
4 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF1/Op/PhsA | SPI | BUSBAR ZONE 1 TRIP R- PHASE | Y |  | Addition, BUSBAR TRIP R- PHASE is configurable (Zone1/2 phasewise trip signal is not configurable) | Agreed
5 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF1/Op/PhsB | SPI | BUSBAR ZONE 1 TRIP Y- PHASE | Y |  | Addition, BUSBAR TRIP Y- PHASE Is configurable (Zone1/2 phasewise trip signal is not configurable) | Agreed
6 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF1/Op/PhsC | SPI | BUSBAR ZONE 1 TRIP B- PHASE | Y |  | Addition, BUSBAR TRIP B- PHASE Is configurable (Zone1/2 phasewise trip signal is not configurable) | Agreed
7 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF1/Op/general | SPI | BUSBAR ZONE 1 TRIP | Y
8 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/BZ_PDIF1/Blk | SPI | BUSBAR ZONE 1 BLOCKED | Y
9 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | BREAKER FAILURE - BUSBAR 1 BLOCKED | Y |  | Addition, Need to discuss (Signal not configurable), Sig. 8 (BUSBAR ZONE 1 BLOCKED) is common blocking signal which will active when busbar blocked from external switch, Isolator intermidiate status, CT Circuit error conditions)
10 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF1/DifAlm | SPI | BUSBAR ZONE-1 CT CIRCUIT ERROR | Y |  | BUSBAR CT CIRCUIT ERROR is configured in Signal No.-03 (Zone1/2 CT CIRCUIT signal not configurable)
11 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | BUSBAR ZONE 1 BLOCKED EXTERNAL BY SWITCH | Y
12 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF2/Op/PhsA | SPI | BUSBAR ZONE 2 TRIP R- PHASE | Y |  | Addition, BUSBAR TRIP R- PHASE is configurable (Zone1/2 phasewise trip signal is not configurable)
13 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF2/Op/PhsB | SPI | BUSBAR ZONE 2 TRIP Y- PHASE | Y |  | Addition, BUSBAR TRIP Y- PHASE Is configurable (Zone1/2 phasewise trip signal is not configurable)
14 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF2/Op/PhsC | SPI | BUSBAR ZONE 2 TRIP B- PHASE | Y |  | Addition, BUSBAR TRIP B- PHASE Is configurable (Zone1/2 phasewise trip signal is not configurable)
15 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF2/Op/general | SPI | BUSBAR ZONE 2 TRIP | Y
16 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/BZ_PDIF2/Blk | SPI | BUSBAR ZONE 2 BLOCKED | Y
17 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | BREAKER FAILURE - BUSBAR 2 BLOCKED | Y |  | Addition, Need to discuss (Signal not configurable), Sig. 15 (BUSBAR ZONE 2 BLOCKED) is common blocking signal which will active when busbar blocked from external switch, Isolator intermidiate status, CT Circuit error conditions)
18 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF2/DifAlm | SPI | BUSBAR ZONE-2 CT CIRCUIT ERROR | Y |  | BUSBAR CT CIRCUIT ERROR is configured in Signal No.-03 (Zone1/2 CT CIRCUIT signal not configurable)
19 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | BUSBAR ZONE 2 BLOCKED EXTERNAL BY SWITCH | Y
20 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/CALH1/GrAlm1/stVal | SPI | ISOLATOR IN INTERMEDIATE STATUS | Y | TO BE USED RELATES TO STATUS OF SWITCHING ELEMENT
21 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/PTRC/Tr/general | SPI | BAY N TRIP | Y | For each Bays | Addition
22 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB0 n/LPHD n/PhyHealth/stVal | SPI | BUSBAR BLOCKED DUE TO COMMUNICATION ERROR_Bay_n | Y | For each Bays | Addition
23 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/GAPC/Ind08/stVal | SPI | BAY_N_BREAKER FAILURE R-PH INITIATION | Y | For each Bays | Addition
24 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/GAPC/Ind09/stVal | SPI | BAY_N_BREAKER FAILURE Y-PH INITIATION | Y | For each Bays | Addition
25 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/GAPC/Ind10/stVal | SPI | BAY_N_BREAKER FAILURE B-PH INITIATION | Y | For each Bays | Addition
26 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/GAPC/Ind11/stVal | SPI | BAY_N_BREAKER FAILURE 3PH INITIATION | Y | For each Bays | Addition
27 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/GAPC/Ind04/stVal | SPI | BAY_N_EXTERNAL BUSBAR ZONE n | Y | For signals where BB tripped through External Tripping commands(GD, Half Dia) | Addition
28 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/RBRF/OpIn/general | SPI | BAY_N_BREAKER FAILURE RETRIP | Y | For each Bays | Addition
29 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/RBRF/OpEx/general | SPI | BAY_N_BREAKER FAILURE BACKTRIP | Y | For each Bays | Addition
30 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/RBRF/OpIn/PhsA | SPI | BAY_N_BREAKER FAILURE RPH- RETRIP | Y | For each Bays | Addition
31 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/RBRF/OpIn/PhsB | SPI | BAY_N_BREAKER FAILURE YPH- RETRIP | Y | For each Bays | Addition
32 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/RBRF/OpIn/PhsC | SPI | BAY_N_BREAKER FAILURE BPH- RETRIP | Y | For each Bays | Addition
33 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/LPHD1/PhyHealth/stVal | SPI | BBP CENTRAL UNIT IED UNHEALTHY | Y
34 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
35 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SETTINGS CHANGED | Y |  | Addition, Need to discuss (Signal not configurable)
36 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme | Addition
37 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-1 | Y | ** 10 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
38 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-2 | Y |  | Addition
39 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-3 | Y |  | Addition
40 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-4 | Y |  | Addition
41 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-5 | Y |  | Addition
42 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-6 | Y |  | Addition
43 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-7 | Y |  | Addition
44 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-8 | Y |  | Addition
45 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-9 | Y |  | Addition
46 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-10 | Y |  | Addition
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 10 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR BUSBAR PROTECTION RELAYS (CENTRALIZED) - REB 670
| IED name: | BB_REB670_87B
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/BBS/BZBSPDIF1/Op/general | SPI | BUSBAR ZONE 1 TRIP | Y | BBS - Single Phase & BBT-Three Phase Variant. STNMD1BBM1R/Y/B if phasewise Busbar IEDs are deployed.
2 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/BBS/BZBSPDIF2/Op/general | SPI | BUSBAR ZONE 2 TRIP | Y
3 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/BBS/BZBSPDIF1/OpnCTAlm/stVal | SPI | BUSBAR ZONE 1 CT CIRCUIT ERROR | Y
4 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/BBS/BZBSPDIF2/OpnCTAlm/stVal | SPI | BUSBAR ZONE 2 CT CIRCUIT ERROR | Y
5 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/LD0/SP16GGIO n /Ind n/stVal | SPI | BUSBAR ZONE 1 BLOCKED EXTERNAL BY SWITCH | Y
6 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/LD0/SP16GGIO n /Ind n/stVal | SPI | BUSBAR ZONE 2 BLOCKED EXTERNAL BY SWITCH | Y
7 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/LD0/SP16GGIO n /Ind n/stVal | SPI | BUSBAR ZONE 1 PROTECTION BLOCKED | Y
8 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/LD0/SP16GGIO n /Ind n/stVal | SPI | BUSBAR ZONE 2 PROTECTION BLOCKED | Y
9 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/BBS6/BCZPDIF1/Op/general | SPI | BUSBAR CHECKZONE TRIP | Y
10 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/BBS/BBSPTRC n/Tr/general | SPI | BAY n TRIP | Y | **** If Bay Breaker Failure function internally utilised then BFP related Initiation, Retrip, Backtrip & other signal refered with Standalone LBB relay.
11 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/LD0/SP16GGIO n/Ind n/stVal | SPI | BAY n BREAKER FAILURE BACKUP TRIP | Y | For each bay signals to be configured and reported | Addition
12 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/LD0/SP16GGIO n/Ind n/stVal | SPI | LCC BUSBAR GAS ZONE TRIP | Y | IF Applicable for GIS | Addition
13 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
14 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/LD0/LPHD1/PhyHealth/stVal | SPI | BBP IED UNHEALTHY | Y
15 | 765kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
16 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SETTINGS CHANGED | Y |  | Addition
17 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | DR MEMMORY 80% FULL | Y |  | Addition
18 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-1 | Y | **10 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
19 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-2 | Y |  | Addition
20 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-3 | Y |  | Addition
21 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-4 | Y |  | Addition
22 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-5 | Y |  | Addition
23 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-6 | Y |  | Addition
24 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-7 | Y |  | Addition
25 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-8 | Y |  | Addition
26 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-9 | Y |  | Addition
27 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | SPARE ALARM-10 | Y |  | Addition
28 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | BUSBAR ZONE 1 TRIP R- PHASE | Y |  | Addition
29 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | BUSBAR ZONE 1 TRIP Y- PHASE | Y |  | Addition
30 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | BUSBAR ZONE 1 TRIP B- PHASE | Y |  | Addition
31 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | BUSBAR ZONE 2 TRIP R- PHASE | Y |  | Addition
32 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | BUSBAR ZONE 2 TRIP Y- PHASE | Y |  | Addition
33 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | BUSBAR ZONE 2 TRIP B- PHASE | Y |  | Addition
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 10 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR BREAKER FAILURE PROTECTION RELAY
| IED name: | R_RELAY NAME_50BFR
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/GGIO n/ST/ Ind n | SPI | BREAKER FAILURE PROTECTION START | Y
2 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/CCRBRF1/OpEx/general | SPI | BREAKER FAILURE BACKUP TRIP | Y |  | Text correction
3 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/CCRBRF1/OpIn/general | SPI | BREAKER FAILURE RETRIP | Y
4 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/CCRBRF1/OpIn/PhsA | SPI | BREAKER FAILURE RETRIP RPH | Y |  | Addition
5 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/CCRBRF1/OpIn/PhsB | SPI | BREAKER FAILURE RETRIP YPH | Y |  | Addition
6 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/CCRBRF1/OpIn/PhsC | SPI | BREAKER FAILURE RETRIP BPH | Y |  | Addition
7 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
8 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/LPHD1/PhyHealth/stVal | SPI | BFP IED UNHEALTHY | Y
9 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | BREAKER FAILURE R-PHASE INITIATION FROM M1/M2 | Y |  | Addition
10 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | BREAKER FAILURE Y-PHASE INITIATION FROM M1/M2 | Y |  | Addition
11 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | BREAKER FAILURE B-PHASE INITIATION FROM M1/M2 | Y |  | Addition
12 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | BREAKER FAILURE 3-PHASE INITIATION FROM 86A/86B/BB | Y |  | Addition
13 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | BREAKER FAILURE FROM LCC (If applicable) | Y | Applicable for GIS LCC | Addition
14 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | IV GR-A INT TRIP RELAY OPTD (If applicable) | Y | Applicable for ICT Bays incomers | Addition
15 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | IV GR-B INT TRIP RELAY OPTD (If applicable) | Y |  | Addition
17 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
18 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | SETTINGS CHANGED | Y |  | Addition
19 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | DR MEMMORY 80% FULL | Y |  | Addition
20 | 765kV | STNMB1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/SP16GGIO n/Ind n/stVal | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
21 | 765kV | STNMB1Q01BFR |  | SPI | SPARE ALARM-1 | Y | ** 10 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
22 | 765kV | STNMB1Q01BFR |  | SPI | SPARE ALARM-2 | Y |  | Addition
23 | 765kV | STNMB1Q01BFR |  | SPI | SPARE ALARM-3 | Y |  | Addition
24 | 765kV | STNMB1Q01BFR |  | SPI | SPARE ALARM-4 | Y |  | Addition
25 | 765kV | STNMB1Q01BFR |  | SPI | SPARE ALARM-5 | Y |  | Addition
26 | 765kV | STNMB1Q01BFR |  | SPI | SPARE ALARM-6 | Y |  | Addition
27 | 765kV | STNMB1Q01BFR |  | SPI | SPARE ALARM-7 | Y |  | Addition
28 | 765kV | STNMB1Q01BFR |  | SPI | SPARE ALARM-8 | Y |  | Addition
29 | 765kV | STNMB1Q01BFR |  | SPI | SPARE ALARM-9 | Y |  | Addition
30 | 765kV | STNMB1Q01BFR |  | SPI | SPARE ALARM-10 | Y |  | Addition
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 10 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR BAY CONTROL UNIT
| IED name: | R_REC670_BCU
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | ADDITIONAL REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/QCBAY1/LocSwPos/stVal | INT | BCU IN LOCAL/ REMOTE
2 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/Op/general | SPI | CLOSE COMMAND FROM BCU FOR AUTORECLOSE |  | FOR BCUs HAVING AUTORECLSOURE FUNCTION INBUILT
3 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | GR-A TRIP RELAY FAULTY | Y |  |  | Addition
4 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | GR-B TRIP RELAY FAULTY | Y |  |  | Addition
5 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | DT RECEIVE CHANNEL-1 | Y |  |  | Addition, Available in REL670 | Only for DR in REL670, for SCADA to be configured from BCU
6 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | DT RECEIVE CHANNEL-2 | Y |  |  | Addition, Available in REL670 | Only for DR in REL670, for SCADA to be configured from BCU
7 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/AutoRecSt/StVal | SPI | AUTORECLOSE FUNCTION ON | Y |  |  | Addition
8 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/AutoRecSt/StVal | SPI | AUTORECLOSE FUNCTION OFF | Y |  |  | Addition
9 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | START AUTORECLOSE FUNCTION | Y |  |  | Addition
10 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/BlkRec/stVal | SPI | BLOCK AUTORECLOSE FUNCTION | Y
11 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/Prp3PhOp/stVal | SPI | PREPARE 3PH TRIP AUTORECLOSE | Y
12 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/RdyRec/stVal | SPI | AUTORECLOSE FUNCTION READY |  |  |  | Text correction
13 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/ActRec/stVal | SPI | AUTORECLOSE IN PROGRESS | Y |  |  | Text correction
14 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/SucRec/stVal | SPI | AUTORECLOSE SUCCESSFUL | Y |  |  | Text correction
15 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/UnsRec/stVal | SPI | AUTORECLOSE UNSUCCESSFUL | Y |  |  | Text correction
16 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SXCBR1/Pos/stVal | DPI | BAY_CB R PH POSITION
17 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SXCBR2/Pos/stVal | DPI | BAY_CB Y PH POSITION
18 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SXCBR3/Pos/stVal | DPI | BAY_CB B PH POSITION
19 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI1/Pos/stVal | DPI | BAY_CB POSITION
20 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI1/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI1/Pos/ctlOperOn for Close | CMD | BAY_CB_COMMAND |  | CLOSE / OPEN
21 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO1/EnaOpn/stVal | SPI | BAY_CB_OPEN PERMITTED OR ENABLED
22 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO1/EnaCls/stVal | SPI | BAY_CB_CLOSE PERMITTED OR ENABLED
23 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI2/Pos/stVal | DPI | BAY_89A_ISOLATOR POSITION
24 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI2/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI2/Pos/ctlOperOn for Close | CMD | BAY_89A_ISO COMMAND |  | CLOSE / OPEN
25 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO2/EnaOpn/stVal | SPI | BAY_89A_ISO OPEN PERMITTED OR ENABLED
26 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO2/EnaCls/stVal | SPI | BAY_89A_ISO CLOSE PERMITTED OR ENABLED
27 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI3/Pos/stVal | DPI | BAY_89AE/AE1_ISOLATOR POSITION
28 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI3/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI3/Pos/ctlOperOn for Close | CMD | BAY_89AE/AE1_ISO COMMAND |  | CLOSE / OPEN
29 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO3/EnaOpn/stVal | SPI | BAY_89AE/AE1_ISO OPEN PERMITTED OR ENABLED
30 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO3/EnaCls/stVal | SPI | BAY_89AE/AE1_ISO CLOSE PERMITTED OR ENABLED
31 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI4/Pos/stVal | DPI | BAY_89B_ISOLATOR POSITION
32 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI4/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI4/Pos/ctlOperOn for Close | CMD | BAY_89B_ISO COMMAND |  | CLOSE / OPEN
33 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO4/EnaOpn/stVal | SPI | BAY_89B_ISO OPEN PERMITTED OR ENABLED
34 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO4/EnaCls/stVal | SPI | BAY_89B_ISO CLOSE PERMITTED OR ENABLED
35 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI5/Pos/stVal | DPI | BAY_89BE/BE1_ISOLATOR POSITION
36 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI5/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI5/Pos/ctlOperOn for Close | CMD | BAY_89BE/BE1_ISO COMMAND |  | CLOSE / OPEN
37 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO5/EnaOpn/stVal | SPI | BAY_89BE/BE1_ISO OPEN PERMITTED OR ENABLED
38 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO5/EnaCls/stVal | SPI | BAY_89BE/BE1_ISO CLOSE PERMITTED OR ENABLED
39 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI6/Pos/stVal | DPI | BAY_89L/T/BR_ISOLATOR POSITION |  |  | FOR 3 PHASE TRANSFORMERS & REACTORS CSWI6 MAY BE USED FOR 89T/BR, BUT FOR SINGLE PHASE TRANSFORMERS & REACTORS SAME HAS BEEN SEPARATELY MENTIONED
40 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI6/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI6/Pos/ctlOperOn for Close | CMD | BAY_89L/T/BR_ISO COMMAND |  | CLOSE / OPEN
41 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO6/EnaOpn/stVal | SPI | BAY_89L/T/BR_ISO OPEN PERMITTED OR ENABLED
42 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO6/EnaCls/stVal | SPI | BAY_89L/T/BR_ISO CLOSE PERMITTED OR ENABLED
43 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI7/Pos/stVal | DPI | BAY_89LE/TE/BRE_ISOLATOR POSITION |  |  | FOR 3 PHASE TRANSFORMERS & REACTORS CSWI7 MAY BE USED FOR 89TE/BRE, BUT FOR SINGLE PHASE PHASE TRANSFORMERS & REACTORS SAME HAS BEEN SEPARATELY MENTIONED
44 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI7/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI7/Pos/ctlOperOn for Close | CMD | BAY_89LE/TE/BRE_ISO COMMAND |  | CLOSE / OPEN
45 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO7/EnaOpn/stVal | SPI | BAY_89LE/TE/BRE_ISO OPEN PERMITTED OR ENABLED
46 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO7/EnaCls/stVal | SPI | BAY_89LE/TE/BRE_ISO CLOSE PERMITTED OR ENABLED
47 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI8/Pos/stVal | DPI | BAY_89LR/89C_ISOLATOR POSITION |  |  | FOR 3 PHASE LINE REACTORS CSWI8 MAY BE USED FOR 89LR, BUT FOR SINGLE PHASE LINE REACTORS SAME HAS BEEN SEPARATELY MENTIONED
48 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI8/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI8/Pos/ctlOperOn for Close | CMD | BAY_89LR/89C_ISO COMMAND |  | CLOSE / OPEN
49 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO8/EnaOpn/stVal | SPI | BAY_89LR/89C_ISO OPEN PERMITTED OR ENABLED
50 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO8/EnaCls/stVal | SPI | BAY_89LR/89C_ISO CLOSE PERMITTED OR ENABLED
51 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI9/Pos/stVal | DPI | BAY_89LRE_ISOLATOR POSITION |  |  | FOR 3 PHASE LINE REACTORS CSWI9 MAY BE USED FOR 89LRE, BUT FOR SINGLE PHASE LINE REACTORS SAME HAS BEEN SEPARATELY MENTIONED
52 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI9/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI9/Pos/ctlOperOn for Close | CMD | BAY_89LRE_ISO COMMAND |  | CLOSE / OPEN
53 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO9/EnaOpn/stVal | SPI | BAY_89LRE_ISO OPEN PERMITTED OR ENABLED
54 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO9/EnaCls/stVal | SPI | BAY_89LRE_ISO CLOSE PERMITTED OR ENABLED
55 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI10/Pos/stVal | DPI | BAY_89BRS1&2_ISOLATOR POSITION |  |  | FOR 3 PHASE BUS & LINE REACTORS CSWI10 MAY BE USED FOR 89BRS1&2, BUT FOR SINGLE PHASE TRANSFORMERS SAME HAS BEEN SEPARATELY MENTIONED
56 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI10Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI10/Pos/ctlOperOn for Close | CMD | BAY_89BRS1&2_ISO COMMAND |  | CLOSE / OPEN
57 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO10/EnaOpn/stVal | SPI | BAY_89BRS1&2_ISO OPEN PERMITTED OR ENABLED
58 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO10/EnaCls/stVal | SPI | BAY_89BRS1&2_ISO CLOSE PERMITTED OR ENABLED
59 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI11/Pos/stVal | DPI | BAY_89BRS1E_ISOLATOR POSITION |  |  | FOR 3 PHASE TRANSFORMERS & REACTORS CSWI11 MAY BE USED FOR 89BRS1E, BUT FOR SINGLE PHASE TRANSFORMERS SAME HAS BEEN SEPARATELY MENTIONED
60 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI11/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI11/Pos/ctlOperOn for Close | CMD | BAY_89BRS1E_ISO COMMAND |  | CLOSE / OPEN
61 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO11/EnaOpn/stVal | SPI | BAY_89BRS1E_ISO OPEN PERMITTED OR ENABLED
62 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO11/EnaCls/stVal | SPI | BAY_89BRS1E_ISO CLOSE PERMITTED OR ENABLED
63 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI12/Pos/stVal | DPI | BAY_89AE2/BE2_ISOLATOR POSITION |  |  | USED FOR BUS EARTH SWITCH OF ISOLATOR, WHEN BUS EARTH SWITCH (89AE2/BE2) IS PROVIDED
64 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI12/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI12/Pos/ctlOperOn for Close | CMD | BAY_89AE2/BE2_ISO COMMAND |  | CLOSE / OPEN
65 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO12/EnaOpn/stVal | SPI | BAY_89AE2/BE2_ISO OPEN PERMITTED OR ENABLED
66 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO12/EnaCls/stVal | SPI | BAY_89AE2/BE2_ISO CLOSE PERMITTED OR ENABLED
THE LOGICAL NODE INSTANCE NUMBER (SCSWIn/SCILOn) FOR BUS EARTH SWITCHES, ISOLATOR & EARTHSWITCHES FOR 3 PH/1PH REACTORS & ITCs, e.g 89 BR, BRE, LR, LRE, RS1, RS2, RS1E, 89T,TE, 89AE2, 89BE2 MAY BE ASSIGNED AS PER AVAILABILITY
67 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
68 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/LPHD1/PhyHealth/stVal | SPI | BCU UNHEALTHY | Y
69 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/SES_1/SESRSYN2/Rel/stVal | SPI | CONDITIONS OK FOR SYNCHRONIZATION
70 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI |  |  |  | APPLICABLE FOR ONE AND HALF CIRCUIT BREAKER
71 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | SPRING DISCHARGED | Y | FOR SPRING MECHANISM CBs | ANNUNCIATION FOR CIRCUIT BREAKER
72 | 765kV | STNMB1Q01BNMBCU |  | SPI | AC MOTOR SUPPLY FAIL | Y
73 | 765kV | STNMB1Q01BNMBCU |  | SPI | SF6 GAS LOW | Y
74 | 765kV | STNMB1Q01BNMBCU |  | SPI | OPERATION LOCKED OUT | Y
75 | 765kV | STNMB1Q01BNMBCU |  | SPI | CB READY FOR AUTORECLOSURE | Y
76 | 765kV | STNMB1Q01BNMBCU |  | SPI | DC SUPPLY FAIL | Y
77 | 765kV | STNMB1Q01BNMBCU |  | SPI | TC-1 FAIL | Y
78 | 765kV | STNMB1Q01BNMBCU |  | SPI | TC-2 FAIL | Y
79 | 765kV | STNMB1Q01BNMBCU |  | SPI | TRIP RELAY 86 A FAULTY (SUPERVISION) | Y |  |  | Addition
80 | 765kV | STNMB1Q01BNMBCU |  | SPI | TRIP RELAY 86 B FAULTY (SUPERVISION) | Y |  |  | Addition
81 | 765kV | STNMB1Q01BNMBCU |  | SPI | TC-1 FAULTY R-PH | Y |  |  | Addition
82 | 765kV | STNMB1Q01BNMBCU |  | SPI | TC-1 FAULTY Y-PH | Y |  |  | Addition
83 | 765kV | STNMB1Q01BNMBCU |  | SPI | TC-1 FAULTY B-PH | Y |  |  | Addition
84 | 765kV | STNMB1Q01BNMBCU |  | SPI | TC-2 FAULTY R-PH | Y |  |  | Addition
85 | 765kV | STNMB1Q01BNMBCU |  | SPI | TC-2 FAULTY Y-PH | Y |  |  | Addition
86 | 765kV | STNMB1Q01BNMBCU |  | SPI | TC-2 FAULTY B-PH | Y |  |  | Addition
87 | 765kV | STNMB1Q01BNMBCU |  | SPI | DT RECEIVE CH-1 | Y |  |  | Available in REC670 (Sig. 5) | Agreed
88 | 765kV | STNMB1Q01BNMBCU |  | SPI | DT RECEIVE CH-2 | Y |  |  | Available in REC670 (Sig. 6) | Agreed
89 | 765kV | STNMB1Q01BNMBCU |  | SPI | CB MANUAL TRIP CMD | Y |  |  | Addition
90 | 765kV | STNMB1Q01BNMBCU |  | SPI | CB MANUAL CLOSE CMD | Y |  |  | Addition
91 | 765kV | STNMB1Q01BNMBCU |  | SPI | START A/R | Y |  |  | Addition
92 | 765kV | STNMB1Q01BNMBCU |  | SPI | BLOCK A/R | Y |  |  | Addition
93 | 765kV | STNMB1Q01BNMBCU |  | SPI | PREPARE 3PH TRIP | Y |  |  | Addition, Available in REC670 (Sig. 11) | Agreed
94 | 765kV | STNMB1Q01BNMBCU |  | SPI | BUSBAR PROTN OPTD | Y |  |  | Addition
95 | 765kV | STNMB1Q01BNMBCU |  | SPI | S.A. COUNTER R-PH | Y |  |  | Addition | As per CRP scheme will be configured in BCU/Protection relay | 0
96 | 765kV | STNMB1Q01BNMBCU |  | SPI | S.A. COUNTER Y-PH | Y |  |  | Addition | As per CRP scheme will be configured in BCU/Protection relay
97 | 765kV | STNMB1Q01BNMBCU |  | SPI | S.A. COUNTER B-PH | Y |  |  | Addition | As per CRP scheme will be configured in BCU/Protection relay
98 | 765kV | STNMB1Q01BNMBCU |  | SPI | INCOMER DC-1 FAIL | Y |  |  | Addition
99 | 765kV | STNMB1Q01BNMBCU |  | SPI | INCOMER DC-2 FAIL | Y |  |  | Addition
100 | 765kV | STNMB1Q01BNMBCU |  | SPI | POLE DISCREPANCY RELAY OPTD | Y
101 | 765kV | STNMB1Q01BNMBCU |  | SPI | COMPRESSOR SUPPLY FAIL | Y | FOR HYDRAULLIC MECHANISM CBs
102 | 765kV | STNMB1Q01BNMBCU |  | SPI | AIR PRESSURE LOW | Y
103 | 765kV | STNMB1Q01BNMBCU |  | SPI | COMPRESSOR RUN TIME SUPERVISION | Y
104 | 765kV | STNMB1Q01BNMBCU |  | SPI | CB R-PH RECLOSE ALARM | Y |  |  | Addition
105 | 765kV | STNMB1Q01BNMBCU |  | SPI | CB Y-PH RECLOSE ALARM | Y |  |  | Addition
106 | 765kV | STNMB1Q01BNMBCU |  | SPI | CB B-PH RECLOSE ALARM | Y |  |  | Addition
107 | 765kV | STNMB1Q01BNMBCU |  | SPI | CSD OPERATION LIMIT ALARM WHEN OPENING | Y |  |  | Addition
108 | 765kV | STNMB1Q01BNMBCU |  | SPI | CSD OPERATION LIMIT ALARM WHEN CLOSING | Y |  |  | Addition
109 | 765kV | STNMB1Q01BNMBCU |  | SPI | CSD GROUP ALARM | Y |  |  | Addition
110 | 765kV | STNMB1Q01BNMBCU |  | SPI | CSD RESERVED | Y |  |  | Addition
111 | 765kV | STNMB1Q01BNMBCU |  | SPI | CSD SYNCHROTEQ IN LOCAL MODE | Y |  |  | Addition
112 | 765kV | STNMB1Q01BNMBCU |  | SPI | CSD CB INTERFACE ALARM | Y |  |  | Addition
113 | 765kV | STNMB1Q01BNMBCU |  | SPI | CSD SENSOR ALARM | Y |  |  | Addition
114 | 765kV | STNMB1Q01BNMBCU |  | SPI | CSD IN | Y |  |  | Addition
115 | 765kV | STNMB1Q01BNMBCU |  | SPI | CSD BYPASS | Y |  |  | Addition
116 | 765kV | STNMB1Q01BNMBCU |  | SPI | CSD FAIL | Y
117 | 765kV | STNMB1Q01BNMBCU |  | SPI | ICT/REACTOR-n R PH OUT OF SERVICE | Y | Single phase ICT/Reactor OUT of service & Spare reactor out of service information |  | Addition
118 | 765kV | STNMB1Q01BNMBCU |  | SPI | ICT/REACTOR-n Y PH OUT OF SERVICE | Y |  |  | Addition
119 | 765kV | STNMB1Q01BNMBCU |  | SPI | ICT/REACTOR-n B PH OUT OF SERVICE | Y |  |  | Addition
120 | 765kV | STNMB1Q01BNMBCU |  | SPI | ICT/REACTOR SPARE PH IN SERVICE IN ICT/REACTOR-N | Y |  |  | Addition
121 | 765kV | STNMB1Q01BNMBCU |  | SPI | BUS-1 VT RESET |  |  | VT SELECTION FOR TRANSFORMER & REACTOR
122 | 765kV | STNMB1Q01BNMBCU |  | SPI | BUS-2 VT RESET
123 | 765kV | STNMB1Q01BNMBCU |  | SPI | LINE VT RESET
124 | 765kV | STNMB1Q01BNMBCU |  | SPI | BUS-1 VT SELECTED
125 | 765kV | STNMB1Q01BNMBCU |  | SPI | BUS-2 VT SELECTED
126 | 765kV | STNMB1Q01BNMBCU |  | SPI | LINE VTSELECTED
127 | 765kV | STNMB1Q01BNMBCU |  | SPI | GAS COMPARTMENT n Alarm Stage n | Y | Stage 1 to n as per scheme | ANNUNCIATION FOR GIS BAYS
128 | 765kV | STNMB1Q01BNMBCU |  | SPI | LCC PANEL AC SUPPLY FAIL | Y
129 | 765kV | STNMB1Q01BNMBCU |  | SPI | LCC PANEL DC SUPPLY FAIL | Y
130 | 765kV | STNMB1Q01BNMBCU |  | SPI | SELECTOR SWITCH POSITION LOCAL/REMOTE | Y
131 | 765kV | STNMB1Q01BNMBCU |  | SPI | BUS VT MCB TRIP | Y |  | FOR BCUs HAVING BUS VT INPUT
132 | 765kV | STNMB1Q01BNMBCU |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
133 | 765kV | STNMB1Q01BNMBCU |  | SPI | RELAY IN TEST MODE | Y |  |  | Addition
134 | 765kV | STNMB1Q01BNMBCU |  | SPI | SETTINGS CHANGED | Y |  |  | Addition
135 | 765kV | STNMB1Q01BNMBCU |  | SPI | DR MEMMORY 80% FULL | Y |  |  | Addition
136 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/MON/CMMXU1/A/phsA/cVal/mag | AI | CURRENT L1 |  |  |  | Addition
137 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/MON/CMMXU1/A/phsB/cVal/mag | AI | CURRENT L2 |  |  |  | Addition
138 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/MON/CMMXU1/A/phsC/cVal/mag | AI | CURRENT L3 |  |  |  | Addition
139 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/MON/VMMXU1/PPV/phsAB/cVal/mag | AI | VOLTAGE U12 |  |  |  | Addition
140 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/MON/VMMXU1/PPV/phsBC/cVal/mag | AI | VOLTAGE U23 |  |  |  | Addition
141 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/MON/VMMXU1/PPV/phsCA/cVal/mag | AI | VOLTAGE U31 |  |  |  | Addition
142 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/MON/CVMMXN1/Watt/mag | AI | ACTIVE POWER (P) |  |  |  | Addition
143 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/MON/CVMMXN1/VolAmpr/mag | AI | REACTIVE POWER (Q) |  |  |  | Addition
144 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/MON/CVMMXN1/PwrFact/mag | AI | POWER FACTOR (PF) |  |  |  | Addition
145 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/MON/CVMMXN1/PwrFact/mag | AI | FREQUENCY (HZ) |  |  |  | Addition
146 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCUMON/L4UFCNTn/CntVal/actVal | AI | S.A. COUNTER R-PH |  |  |  | Available in REC670 (Sig. 95) | Agreed
147 | 765kV | STNMB1Q01BNMBCU |  | AI | S.A. COUNTER Y-PH |  |  |  | Available in REC670 (Sig. 95) | Agreed
148 | 765kV | STNMB1Q01BNMBCU |  | AI | S.A. COUNTER B-PH |  |  |  | Available in REC670 (Sig. 95) | Agreed
149 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/MON/MVGAPC/AnIn_n/mag | AI | TAP POSITION R PH |  |  |  | Addition
150 | 765kV | STNMB1Q01BNMBCU |  | AI | TAP POSITION Y PH |  |  |  | Addition
151 | 765kV | STNMB1Q01BNMBCU |  | AI | TAP POSITION B PH |  |  |  | Addition
152 | 765kV | STNMB1Q01BNMBCU |  | AI | WTI HV R PH |  |  |  | Addition
153 | 765kV | STNMB1Q01BNMBCU |  | AI | WTI IV R PH |  |  |  | Addition
154 | 765kV | STNMB1Q01BNMBCU |  | AI | WTI LV R PH |  |  |  | Addition
155 | 765kV | STNMB1Q01BNMBCU |  | AI | OTI R PH |  |  |  | Addition
156 | 765kV | STNMB1Q01BNMBCU |  | AI | WTI HV Y PH |  |  |  | Addition
157 | 765kV | STNMB1Q01BNMBCU |  | AI | WTI IV Y PH |  |  |  | Addition
158 | 765kV | STNMB1Q01BNMBCU |  | AI | WTI LV Y PH |  |  |  | Addition
159 | 765kV | STNMB1Q01BNMBCU |  | AI | OTI Y PH |  |  |  | Addition
160 | 765kV | STNMB1Q01BNMBCU |  | AI | WTI HV B PH |  |  |  | Addition
161 | 765kV | STNMB1Q01BNMBCU |  | AI | WTI IV B PH |  |  |  | Addition
162 | 765kV | STNMB1Q01BNMBCU |  | AI | WTI LV B PH |  |  |  | Addition
163 | 765kV | STNMB1Q01BNMBCU |  | AI | OTI B PH |  |  |  | Addition
164 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCUMON/L4UFCNTn/CntVal/actVal | AI | BREAKER R-PHASE OPERATION COUNTER |  |  |  | Addition
165 | 765kV | STNMB1Q01BNMBCU |  | AI | BREAKER Y-PHASE OPERATION COUNTER |  |  |  | Addition
166 | 765kV | STNMB1Q01BNMBCU |  | AI | BREAKER B-PHASE OPERATION COUNTER |  |  |  | Addition
167 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | RPH MOG LOW OIL LEVEL ALARM | Y |  | FOR 3Phase TRANSFORMER, INPUTS CAN BE DISTRIBUTED TO ANY IED. BUTSIGNAL SHOULD BE AS PER TRANSFORMER AVIALABLE SIGNAL | Addition
168 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH MOG LOW OIL LEVEL ALARM | Y |  |  | Addition
169 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH MOG LOW OIL LEVEL ALARM | Y |  |  | Addition
170 | 765kV | STNMB1Q01BNMBCU |  | SPI | SP-PH MOG LOW OIL LEVEL ALARM | Y |  |  | Addition
171 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH MOG HIGH OIL LEVEL ALARM | Y |  |  | Addition
172 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH MOG HIGH OIL LEVEL ALARM | Y |  |  | Addition
173 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH MOG HIGH OIL LEVEL ALARM | Y |  |  | Addition
174 | 765kV | STNMB1Q01BNMBCU |  | SPI | SP-PH MOG HIGH OIL LEVEL ALARM | Y |  |  | Addition
175 | 765kV | STNMB1Q01BNMBCU |  | SPI | R-PH OIL FLOW SENSITIVE VALVE ALARM | Y |  |  | Addition
176 | 765kV | STNMB1Q01BNMBCU |  | SPI | Y-PH OIL FLOW SENSITIVE VALVE ALARM | Y |  |  | Addition
177 | 765kV | STNMB1Q01BNMBCU |  | SPI | B-PH OIL FLOW SENSITIVE VALVE ALARM | Y |  |  | Addition
178 | 765kV | STNMB1Q01BNMBCU |  | SPI | SP-PH OIL FLOW SENSITIVE VALVE ALARM | Y |  |  | Addition
179 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH PUMP FAIL - BANK A | Y |  |  | Addition
180 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH PUMP FAIL - BANK B | Y |  |  | Addition
181 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH PUMP FAIL - BANK C | Y |  |  | Addition
182 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH PUMP FAIL - BANK D | Y |  |  | Addition
183 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH PUMP FAIL - BANK A | Y |  |  | Addition
184 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH PUMP FAIL - BANK B | Y |  |  | Addition
185 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH PUMP FAIL - BANK C | Y |  |  | Addition
186 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH PUMP FAIL - BANK D | Y |  |  | Addition
187 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH PUMP FAIL - BANK A | Y |  |  | Addition
188 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH PUMP FAIL - BANK B | Y |  |  | Addition
189 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH PUMP FAIL - BANK C | Y |  |  | Addition
190 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH PUMP FAIL - BANK D | Y |  |  | Addition
191 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH PUMP FAIL - BANK A | Y |  |  | Addition
192 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH PUMP FAIL - BANK B | Y |  |  | Addition
193 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH PUMP FAIL - BANK C | Y |  |  | Addition
194 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH PUMP FAIL - BANK D | Y |  |  | Addition
195 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH THERMAL OVERLOAD TRIP - BANK A | Y |  |  | Addition
196 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH THERMAL OVERLOAD TRIP - BANK B | Y |  |  | Addition
197 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH THERMAL OVERLOAD TRIP - BANK C | Y |  |  | Addition
198 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH THERMAL OVERLOAD TRIP - BANK D | Y |  |  | Addition
199 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH THERMAL OVERLOAD TRIP - BANK A | Y |  |  | Addition
200 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH THERMAL OVERLOAD TRIP - BANK B | Y |  |  | Addition
201 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH THERMAL OVERLOAD TRIP - BANK C | Y |  |  | Addition
202 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH THERMAL OVERLOAD TRIP - BANK D | Y |  |  | Addition
203 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH THERMAL OVERLOAD TRIP - BANK A | Y |  |  | Addition
204 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH THERMAL OVERLOAD TRIP - BANK B | Y |  |  | Addition
205 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH THERMAL OVERLOAD TRIP - BANK C | Y |  |  | Addition
206 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH THERMAL OVERLOAD TRIP - BANK D | Y |  |  | Addition
207 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH THERMAL OVERLOAD TRIP - BANK A | Y |  |  | Addition
208 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH THERMAL OVERLOAD TRIP - BANK B | Y |  |  | Addition
209 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH THERMAL OVERLOAD TRIP - BANK C | Y |  |  | Addition
210 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH THERMAL OVERLOAD TRIP - BANK D | Y |  |  | Addition
211 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH LOW OIL FLOW/REVERSE FLOW - BANK A | Y |  |  | Addition
212 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH LOW OIL FLOW/REVERSE FLOW - BANK B | Y |  |  | Addition
213 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH LOW OIL FLOW/REVERSE FLOW - BANK C | Y |  |  | Addition
214 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH LOW OIL FLOW/REVERSE FLOW - BANK D | Y |  |  | Addition
215 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH LOW OIL FLOW/REVERSE FLOW - BANK A | Y |  |  | Addition
216 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH LOW OIL FLOW/REVERSE FLOW - BANK B | Y |  |  | Addition
217 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH LOW OIL FLOW/REVERSE FLOW - BANK C | Y |  |  | Addition
218 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH LOW OIL FLOW/REVERSE FLOW - BANK D | Y |  |  | Addition
219 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH LOW OIL FLOW/REVERSE FLOW - BANK A | Y |  |  | Addition
220 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH LOW OIL FLOW/REVERSE FLOW - BANK B | Y |  |  | Addition
221 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH LOW OIL FLOW/REVERSE FLOW - BANK C | Y |  |  | Addition
222 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH LOW OIL FLOW/REVERSE FLOW - BANK D | Y |  |  | Addition
223 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH LOW OIL FLOW/REVERSE FLOW - BANK A | Y |  |  | Addition
224 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH LOW OIL FLOW/REVERSE FLOW - BANK B | Y |  |  | Addition
225 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH LOW OIL FLOW/REVERSE FLOW - BANK C | Y |  |  | Addition
226 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH LOW OIL FLOW/REVERSE FLOW - BANK D | Y |  |  | Addition
227 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH COOLER CONTROL SUPPLY FAIL | Y |  |  | Addition
228 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH COOLER CONTROL SUPPLY FAIL | Y |  |  | Addition
229 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH COOLER CONTROL SUPPLY FAIL | Y |  |  | Addition
230 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH COOLER CONTROL SUPPLY FAIL | Y |  |  | Addition
231 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH SUPPLY CHANGE OVER FAIL | Y |  |  | Addition
232 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH SUPPLY CHANGE OVER FAIL | Y |  |  | Addition
233 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH SUPPLY CHANGE OVER FAIL | Y |  |  | Addition
234 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH SUPPLY CHANGE OVER FAIL | Y |  |  | Addition
235 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH SUPPLY - A FAIL | Y |  |  | Addition
236 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH SUPPLY - A FAIL | Y |  |  | Addition
237 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH SUPPLY - A FAIL | Y |  |  | Addition
238 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH SUPPLY - A FAIL | Y |  |  | Addition
239 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH SUPPLY - B FAIL | Y |  |  | Addition
240 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH SUPPLY - B FAIL | Y |  |  | Addition
241 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH SUPPLY - B FAIL | Y |  |  | Addition
242 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH SUPPLY - B FAIL | Y |  |  | Addition
243 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH OLTC MOTOR OVERLOAD | Y |  |  | Addition
244 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH TAP CHANGE IN PROGRESS | Y |  |  | Addition
245 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH TAP CHANGE IN COMPLETE | Y |  |  | Addition
246 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH OLTC IN LOCAL | Y |  |  | Addition
247 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH OLTC IN REMOTE | Y |  |  | Addition
248 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH TAP CHANGE CONTROL SUPPLY FAIL | Y |  |  | Addition
249 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH LOWEST POSITION REACHDED | Y |  |  | Addition
250 | 765kV | STNMB1Q01BNMBCU |  | SPI | RPH HIGHESHT POSITION REACHDED | Y |  |  | Addition
251 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SPC1CGGIO n/ctlOpen | CMD | RPH OLTC RAISE COMMAND | Y |  |  | Addition
252 | 765kV | STNMB1Q01BNMBCU |  | CMD | RPH OLTC LOWER COMMAND | Y |  |  | Addition
253 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | YPH OLTC MOTOR OVERLOAD | Y |  |  | Addition
254 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH TAP CHANGE IN PROGRESS | Y |  |  | Addition
255 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH TAP CHANGE IN COMPLETE | Y |  |  | Addition
256 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH OLTC IN LOCAL | Y |  |  | Addition
257 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH OLTC IN REMOTE | Y |  |  | Addition
258 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH TAP CHANGE CONTROL SUPPLY FAIL | Y |  |  | Addition
259 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH LOWEST POSITION REACHDED | Y |  |  | Addition
260 | 765kV | STNMB1Q01BNMBCU |  | SPI | YPH HIGHESHT POSITION REACHDED | Y |  |  | Addition
261 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SPC1CGGIO n/ctlOpen | CMD | YPH OLTC RAISE COMMAND | Y |  |  | Addition
262 | 765kV | STNMB1Q01BNMBCU |  | CMD | YPH OLTC LOWER COMMAND | Y |  |  | Addition
263 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | BPH OLTC MOTOR OVERLOAD | Y |  |  | Addition
264 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH TAP CHANGE IN PROGRESS | Y |  |  | Addition
265 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH TAP CHANGE IN COMPLETE | Y |  |  | Addition
266 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH OLTC IN LOCAL | Y |  |  | Addition
267 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH OLTC IN REMOTE | Y |  |  | Addition
268 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH TAP CHANGE CONTROL SUPPLY FAIL | Y |  |  | Addition
269 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH LOWEST POSITION REACHDED | Y |  |  | Addition
270 | 765kV | STNMB1Q01BNMBCU |  | SPI | BPH HIGHESHT POSITION REACHDED | Y |  |  | Addition
271 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SPC1CGGIO n/ctlOpen | CMD | BPH OLTC RAISE COMMAND | Y |  |  | Addition
272 | 765kV | STNMB1Q01BNMBCU |  | CMD | BPH OLTC LOWER COMMAND | Y |  |  | Addition
273 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | SPH OLTC MOTOR OVERLOAD | Y |  |  | Addition
274 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH TAP CHANGE IN PROGRESS | Y |  |  | Addition
275 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH TAP CHANGE IN COMPLETE | Y |  |  | Addition
276 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH OLTC IN LOCAL | Y |  |  | Addition
277 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH OLTC IN REMOTE | Y |  |  | Addition
278 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH TAP CHANGE CONTROL SUPPLY FAIL | Y |  |  | Addition
279 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH LOWEST POSITION REACHDED | Y |  |  | Addition
280 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPH HIGHESHT POSITION REACHDED | Y |  |  | Addition
281 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SPC1CGGIO n/ctlOpen | CMD | SPH OLTC RAISE COMMAND | Y |  |  | Addition
282 | 765kV | STNMB1Q01BNMBCU |  | CMD | SPH OLTC LOWER COMMAND | Y |  |  | Addition
283 | 765kV | STNMB1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-1 | Y | ** 10 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database |  | Addition
284 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPARE ALARM-2 | Y |  |  | Addition
285 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPARE ALARM-3 | Y |  |  | Addition
286 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPARE ALARM-4 | Y |  |  | Addition
287 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPARE ALARM-5 | Y |  |  | Addition
288 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPARE ALARM-6 | Y |  |  | Addition
289 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPARE ALARM-7 | Y |  |  | Addition
290 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPARE ALARM-8 | Y |  |  | Addition
291 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPARE ALARM-9 | Y |  |  | Addition
292 | 765kV | STNMB1Q01BNMBCU |  | SPI | SPARE ALARM-10 | Y |  |  | Addition
ADDITIONAL SIGNAL FOR CB TROUBLE ETC AS PER SCHEME
** 10 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
NOTE 1: The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified.
NOTE 2: If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.
NOTE 3: The characters "STNM" stand for Substation Name with maximum 4 characters, this code will be given by POWERGRID for each project.
NOTE 4: The characters "Q01" stand for Bay Number, this will be vary based on Bay number eg. Q01 for BAY01, Q02 for BAY02 etc…
NOTE 5: The characters "BNM" stand for Bay Name, this will be vary based on Bay name eg. L for LINE, BR for BUSREACTOR, LR for LINEREACTOR, TIE for TIE & ICT fo ICT bay.
REQUIRED SIGNALS FOR LINE DIFFERENTAIL cum DISTANCE RELAYS
| IED name: | R_REL670_21M1
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/OV2_1/OV2PTOV1/Str/general | SPI | OVERVOLATGE STAGE 1 START
2 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/OV2_1/OV2PTOV1/Op/general | SPI | OVERVOLATGE STAGE 1 TRIP | Y
3 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/OV2PTOV2/Str/general | SPI | OVER VOLTAGE STAGE-2 START | Y |  | Addition
4 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/OV2_1/OV2PTOV2/Op/general | SPI | OVERVOLATGE STAGE 2 TRIP | Y
5 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/EF4_1/EF4PTOC1/Str/general | SPI | DEF START
6 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/EF4_1/EF4PTOC1/Op/general | SPI | DEF TRIP | Y
7 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/STBPTOC1/Op/general | SPI | STUB PROTECTION OPERATED | Y | Applicable for One and Half CB Busbar system
8 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCVPSOF1/Op/general | SPI | SOTF OPERATED | Y
9 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Str/general | SPI | START, Z1
10 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/general | SPI | START, Z2
11 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsA | SPI | START, Z2 R PH
12 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsB | SPI | START, Z2 Y PH
13 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsC | SPI | START, Z2 B PH
14 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS3/Str/general | SPI | START, Z3
15 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS4/Str/general | SPI | START, Z4(REVERSE) |  | ** Whichever the zone choses as Reverse | Text correction
16 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS5/Str/general | SPI | START, Z5
17 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/general | SPI | GENERAL TRIP, Z1 | Y
18 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsA | SPI | TRIP, Z1 R PH | Y
19 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsB | SPI | TRIP, Z1 Y PH | Y
20 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsC | SPI | TRIP, Z1 B PH | Y
21 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/general | SPI | GENERAL TRIP, Z2 | Y
22 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsA | SPI | TRIP, Z2 R PH | Y
23 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsB | SPI | TRIP, Z2 Y PH | Y
24 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsC | SPI | TRIP, Z2 B PH | Y
25 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS3/Op/general | SPI | GENERAL TRIP, Z3 | Y
26 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS4/Op/general | SPI | GENERAL TRIP, Z4(REVERSE) | Y | ** Whichever the zone choses as Reverse | Text correction
27 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS5/Op/general | SPI | GENERAL TRIP, Z5 | Y
28 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/ProTx/stVal | SPI | CARRIER SEND | Y
29 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/ProRx/stVal | SPI | CARRIER RECEIVE | Y
30 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/Op/general | SPI | CARRIER AIDED SCHEME OPERATED | Y
31 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMRPSB1/Str/general | SPI | POWER SWING DETECTED | Y
32 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMRPSB1/BlkZn/stVal | SPI | POWER SWING BLOCKING | Y
33 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SMPPTRC1/Op/general | SPI | DISTANCE RELAY GENERAL TRIP | Y
34 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | R PHASE FAULT | Y |  | Addition
35 | 765kV | STNMB1Q01LM1DIF |  | SPI | Y PHASE FAULT | Y |  | Addition
36 | 765kV | STNMB1Q01LM1DIF |  | SPI | B PHASE FAULT | Y |  | Addition
37 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltDiskm/mag | DINT | FAULT LOCATOR DISTANCE
38 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltZ/cVal.mag | DINT | FAULT LOCATOR IMPEDANCE
39 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
40 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/BRCPTOC1/Op/general | SPI | BROKEN CONDUCTOR ALARM | Y
41 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
42 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/LPHD1/PhyHealth/stVal | SPI | M1 IED UNHEALTHY | Y
43 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | START AR TO BCU |  |  | Text correction
44 | 765kV | STNMB1Q01LM1DIF |  | SPI | BLOCK AR TO BCU |  |  | Text correction
45 | 765kV | STNMB1Q01LM1DIF |  | SPI | LINE ISOLATOR OPEN FOR STUB ACTIVATION |  | Applicable for One and Half CB Busbar system
46 | 765kV | STNMB1Q01LM1DIF |  | SPI | DT SEND CH 1 | Y
47 | 765kV | STNMB1Q01LM1DIF |  | SPI | DT SEND CH 2 | Y
48 | 765kV | STNMB1Q01LM1DIF |  | SPI | DT RECEIVE CH 1 | Y |  |  | Only for DR in RED670, for SCADA to be configured from BCU
49 | 765kV | STNMB1Q01LM1DIF |  | SPI | DT RECEIVE CH 2 | Y |  |  | Only for DR in RED670, for SCADA to be configured from BCU
50 | 765kV | STNMB1Q01LM1DIF |  | SPI | TRIP RELAY 86 A HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
51 | 765kV | STNMB1Q01LM1DIF |  | SPI | TRIP RELAY 86 B HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
52 | 765kV | STNMB1Q01LM1DIF |  | SPI | GR A RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RED670, for SCADA to be configured from BCU
53 | 765kV | STNMB1Q01LM1DIF |  | SPI | GR B RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RED670, for SCADA to be configured from BCU
54 | 765kV | STNMB1Q01LM1DIF |  | SPI | CARRIER RECEIVE CH-1 | Y
55 | 765kV | STNMB1Q01LM1DIF |  | SPI | CARRIER RECEIVE CH-2 | Y
56 | 765kV | STNMB1Q01LM1DIF |  | SPI | CARRIER CHANNEL 1 OUT OF SERVICE | Y
57 | 765kV | STNMB1Q01LM1DIF |  | SPI | CARRIER CHANNEL 2 OUT OF SERVICE | Y
58 | 765kV | STNMB1Q01LM1DIF |  | SPI | CARRIER CHANNEL 1 FAIL | Y
59 | 765kV | STNMB1Q01LM1DIF |  | SPI | CARRIER CHANNEL 2 FAIL | Y
60 | 765kV | STNMB1Q01LM1DIF |  | SPI | MAIN 2/1 RELAY FAIL | Y
61 | 765kV | STNMB1Q01LM1DIF |  | SPI | CB CLOSE COMMAND FOR SOTF INITIATION |  |  | Text correction
62 | 765kV | STNMB1Q01LM1DIF |  | SPI | BCU RELAY FAIL | Y
63 | 765kV | STNMB1Q01LM1DIF |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
64 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsA | SPI | START, Z1 R PH |  |  | Addition
65 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsB | SPI | START, Z1 Y PH |  |  | Addition
66 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsC | SPI | START, Z1 B PH |  |  | Addition
67 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP 3PH | Y |  | Addition
68 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP R PH | Y |  | Addition
69 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP Y PH | Y |  | Addition
70 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP B PH | Y |  | Addition
71 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | PREPARE 3-PH TRIP FROM TIE BCU | Y |  | Addition, Available in BCU | It is also required in RED670
72 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | PREPARE 3-PH TRIP FROM MAIN BCU | Y |  | Addition, Available in BCU | It is also required in RED670
73 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | MAIN/ TIE CB AR OPTD | Y |  | Addition, Available in BCU | Only for DR in RED670, for SCADA to be configured from BCU
74 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | MAIN/TIE LBB PROTECTION OPERATED | Y |  | Addition, Available in BBP | Only for DR in RED670, for SCADA to be configured from LBB/BBP relay
75 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | BUSBAR M1/M2 OPTD | Y |  | Addition, Available in BBP | Only for DR in RED670, for SCADA to be configured from BBP relay
76 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | GROUP RELAY 86A OPTD | Y |  | Available in REL670 (Sig. 52) | Agreed
77 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/EchoWei/stVal | SPI | WEAK INFEED ECHO SEND | Y |  | Addition
78 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/EchoWeiOp/stVal | SPI | WEAK INFEED TRIP | Y |  | Addition
79 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/RvABlk/stVal | SPI | CURRENT REVERSAL DETECTED | Y |  | Addition
80 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
81 | 765kV | STNMB1Q01LM1DIF |  | SPI | SETTINGS CHANGED | Y |  | Addition
82 | 765kV | STNMB1Q01LM1DIF |  | SPI | DR MEMMORY 80% FULL | Y |  | Addition
83 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltDiskm/mag | AI | DISTANCE MEASUREMENT IN KM | Y |  | Available in REL670 (Sig. 37) | Agreed
84 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltZ/cVal/mag | AI | DISTANCE MEASUREMENT IN IMPEDANCE | Y |  | Available in REL670 (Sig. 38) | Agreed
85 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/MON/L4UFCNTn/CntVal/actVal | AI | CH-1 Code-1 Tx (MAIN-1 CARRIER RECEIVE CHANNEL-1) |  |  | CH-1 Code-1 Tx (MAIN-1 CARRIER SEND CHANNEL-1)
86 | 765kV | STNMB1Q01LM1DIF |  | AI | CH-1 Code-1 Rx (MAIN-1 CARRIER SEND CHANNEL-1) |  |  | CH-1 Code-1 Rx (MAIN-1 CARRIER RECEIVE CHANNEL-1)
87 | 765kV | STNMB1Q01LM1DIF |  | AI | CH-1 Code-2 Tx (MAIN-2 CARRIER RECEIVE CHANNEL-1) |  |  | CH-1 Code-2 Tx (MAIN-2 CARRIER SEND CHANNEL-1)
88 | 765kV | STNMB1Q01LM1DIF |  | AI | CH-1 Code-2 Rx (MAIN-2 CARRIER SEND CHANNEL-1) |  |  | CH-1 Code-2 Rx (MAIN-2 CARRIER RECEIVE CHANNEL-1)
89 | 765kV | STNMB1Q01LM1DIF |  | AI | CH-2 Code-2 Tx (MAIN-2 CARRIER RECEIVE CHANNEL-2) |  |  | CH-2 Code-2 Tx (MAIN-2 CARRIER SEND CHANNEL-2)
90 | 765kV | STNMB1Q01LM1DIF |  | AI | CH-2 Code-2 Rx (MAIN-2 CARRIER SEND CHANNEL-2) |  |  | CH-2 Code-2 Rx (MAIN-2 CARRIER RECEIVECHANNEL-2)
91 | 765kV | STNMB1Q01LM1DIF |  | AI | CH-2 Code-1 Tx (MAIN-1 CARRIER RECEIVE CHANNEL-2) |  |  | CH-2 Code-1 Tx (MAIN-1 CARRIER SEND CHANNEL-2)
92 | 765kV | STNMB1Q01LM1DIF |  | AI | CH-2 Code-1 Rx (MAIN-1 CARRIER SEND CHANNEL-2) |  |  | CH-2 Code-1 Rx (MAIN-1 CARRIER RECEIVE CHANNEL-2)
93 | 765kV | STNMB1Q01LM1DIF |  | AI | CH-1 Code-3 Tx (DT RECEIVE CHANNEL-1) |  |  | CH-1 Code-3 Tx (DT SEND CHANNEL-1)
94 | 765kV | STNMB1Q01LM1DIF |  | AI | CH-1 Code-3 Rx (DT SEND CHANNEL-1) |  |  | CH-1 Code-3 Rx (DT RECEIVE CHANNEL-1)
95 | 765kV | STNMB1Q01LM1DIF |  | AI | CH-2 Code-3 Tx (DT RECEIVE CHANNEL-2) |  |  | CH-2 Code-3 Tx (DT SEND CHANNEL-2)
96 | 765kV | STNMB1Q01LM1DIF |  | AI | CH-2 Code-3 Rx (DT SEND CHANNEL-2) |  |  | CH-2 Code-3 Rx (DT RECEIVE CHANNEL-2)
97 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
98 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-2 | Y |  | Addition
99 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-3 | Y |  | Addition
100 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-4 | Y |  | Addition
101 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-5 | Y |  | Addition
102 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Op/general | SPI | DIFFERENTIAL PROTECTION TRIP | Y | Line Differential protection, 3 CT sets, 2-3 line ends Variant
103 | 765kV |  | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Op/general | SPI |  | Y | Line Differential protection, 6 CT sets, 3-5 line ends Variant
104 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Op/phsA | SPI | DIFFERENTIAL PROTECTION RPH TRIP | Y | Line Differential protection, 3 CT sets, 2-3 line ends Variant
105 | 765kV |  | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Op/phsA | SPI |  | Y | Line Differential protection, 6 CT sets, 3-5 line ends Variant
106 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Op/phsB | SPI | DIFFERENTIAL PROTECTION YPH TRIP | Y | Line Differential protection, 3 CT sets, 2-3 line ends Variant
107 | 765kV |  | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Op/phsB | SPI |  | Y | Line Differential protection, 6 CT sets, 3-5 line ends Variant
108 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Op/phsC | SPI | DIFFERENTIAL PROTECTION BPH TRIP | Y | Line Differential protection, 3 CT sets, 2-3 line ends Variant
109 | 765kV |  | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Op/phsC | SPI |  | Y | Line Differential protection, 6 CT sets, 3-5 line ends Variant
110 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Str/general | SPI | DIFFERENTIAL PROTECTION START |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
111 | 765kV |  | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Str/general | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
112 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Str/phsA | SPI | DIFFERENTIAL PROTECTION RPH START |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
113 | 765kV |  | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Str/phsA | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
114 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Str/phsB | SPI | DIFFERENTIAL PROTECTION YPH START |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
115 | 765kV |  | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Str/phsB | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
116 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Str/phsC | SPI | DIFFERENTIAL PROTECTION BPH START |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
117 | 765kV |  | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Str/phsC | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
102 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/OpnCTAlm/stVal | SPI | DIFFERENTIAL PROTECTION OCT ALARM |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
103 | 765kV |  | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/OpnCTAlm/stVal | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
104 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/StrRst/stVal | SPI | DIFFERENTIAL PROTECTION OPTD (RESTRAINED MODE) |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
105 | 765kV |  | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/StrRst/stVal | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
106 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/StrUnRst/stVal | SPI | DIFFERENTIAL PROTECTION OPTD (UNRESTRAINED MODE) |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
107 | 765kV |  | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/StrUnRst/stVal | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
108 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Blk2H/stVal | SPI | DIFFERENTIAL PROTECTION 2nd HARMONIC BLOCK |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant | Applicable for Line cum Transformer bay
109 | 765kV |  | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Blk2H/stVal | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
110 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Blk5H/stVal | SPI | DIFFERENTIAL PROTECTION 5th HARMONIC BLOCK |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant | Applicable for Line cum Transformer bay
111 | 765kV |  | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Blk5H/stVal | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
112 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION COMMUNICATION FAIL
113 | 765kV | STNMB1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | REMOTE END INTERTRIP RECEIVE
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME

## SIGNAL STANDARDIZATION FOR 400
ABB SCADA SIGNAL LIST FOR VARIOUS PROTECTION & CONTROL SIGNALS - REV03 (400kV)
REQUIRED SIGNALS FOR DISTANCE RELAYS
| IED name: | R_REL670_21M1
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/OV2_1/OV2PTOV1/Str/general | SPI | OVERVOLATGE STAGE 1 START
2 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/OV2_1/OV2PTOV1/Op/general | SPI | OVERVOLATGE STAGE 1 TRIP | Y
3 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/OV2_1/OV2PTOV2/Str/general | SPI | OVER VOLTAGE STAGE-2 START | Y |  | Addition
4 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/OV2_1/OV2PTOV2/Op/general | SPI | OVERVOLATGE STAGE 2 TRIP | Y
5 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/EF4_1/EF4PTOC1/Str/general | SPI | DEF START
6 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/EF4_1/EF4PTOC1/Op/general | SPI | DEF TRIP | Y
7 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/STBPTOC1/Op/general | SPI | STUB PROTECTION OPERATED | Y | Applicable for One and Half CB Busbar system
8 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCVPSOF1/Op/general | SPI | SOTF OPERATED | Y
9 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Str/general | SPI | START, Z1
10 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/general | SPI | START, Z2
11 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsA | SPI | START, Z2 R PH
12 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsB | SPI | START, Z2 Y PH
13 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsC | SPI | START, Z2 B PH
14 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS3/Str/general | SPI | START, Z3
15 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS4/Str/general | SPI | START, Z4(REVERSE) |  | ** Whichever the zone choses as Reverse | Text correction
16 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS5/Str/general | SPI | START, Z5
17 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/general | SPI | GENERAL TRIP, Z1 | Y
18 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsA | SPI | TRIP, Z1 R PH | Y
19 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsB | SPI | TRIP, Z1 Y PH | Y
20 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsC | SPI | TRIP, Z1 B PH | Y
21 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/general | SPI | GENERAL TRIP, Z2 | Y
22 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsA | SPI | TRIP, Z2 R PH | Y
23 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsB | SPI | TRIP, Z2 Y PH | Y
24 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsC | SPI | TRIP, Z2 B PH | Y
25 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS3/Op/general | SPI | GENERAL TRIP, Z3 | Y
26 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS4/Op/general | SPI | GENERAL TRIP, Z4(REVERSE) | Y | ** Whichever the zone choses as Reverse | Text correction
27 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS5/Op/general | SPI | GENERAL TRIP, Z5 | Y
28 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/ProTx/stVal | SPI | CARRIER SEND | Y
29 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/ProRx/stVal | SPI | CARRIER RECEIVE | Y
30 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/Op/general | SPI | CARRIER AIDED SCHEME OPERATED | Y
31 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMRPSB1/Str/general | SPI | POWER SWING DETECTED | Y
32 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMRPSB1/BlkZn/stVal | SPI | POWER SWING BLOCKING | Y
33 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SMPPTRC1/Op/general | SPI | DISTANCE RELAY GENERAL TRIP | Y
34 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | R PHASE FAULT | Y |  | Addition
35 | 400kV | STNMC1Q01M1DIS |  | SPI | Y PHASE FAULT | Y |  | Addition
36 | 400kV | STNMC1Q01M1DIS |  | SPI | B PHASE FAULT | Y |  | Addition
37 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltDiskm/mag | DINT | FAULT LOCATOR DISTANCE
38 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltZ/cVal.mag | DINT | FAULT LOCATOR IMPEDANCE
39 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
40 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/BRCPTOC1/Op/general | SPI | BROKEN CONDUCTOR ALARM | Y
41 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
42 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/LPHD1/PhyHealth/stVal | SPI | M1 IED UNHEALTHY | Y
43 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | START AR TO BCU |  |  | Text correction
44 | 400kV | STNMC1Q01M1DIS |  | SPI | BLOCK AR TO BCU |  |  | Text correction
45 | 400kV | STNMC1Q01M1DIS |  | SPI | LINE ISOLATOR OPEN FOR STUB ACTIVATION |  | Applicable for One and Half CB Busbar system
46 | 400kV | STNMC1Q01M1DIS |  | SPI | DT SEND CH 1 | Y
47 | 400kV | STNMC1Q01M1DIS |  | SPI | DT SEND CH 2 | Y
48 | 400kV | STNMC1Q01M1DIS |  | SPI | DT RECEIVE CH 1 | Y |  |  | Only for DR in REL670, for SCADA to be configured from BCU
49 | 400kV | STNMC1Q01M1DIS |  | SPI | DT RECEIVE CH 2 | Y |  |  | Only for DR in REL670, for SCADA to be configured from BCU
50 | 400kV | STNMC1Q01M1DIS |  | SPI | TRIP RELAY 86 A HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
51 | 400kV | STNMC1Q01M1DIS |  | SPI | TRIP RELAY 86 B HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
52 | 400kV | STNMC1Q01M1DIS |  | SPI | GR A RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in REL670, for SCADA to be configured from BCU
53 | 400kV | STNMC1Q01M1DIS |  | SPI | GR B RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in REL670, for SCADA to be configured from BCU
54 | 400kV | STNMC1Q01M1DIS |  | SPI | CARRIER RECEIVE CH-1 | Y
55 | 400kV | STNMC1Q01M1DIS |  | SPI | CARRIER RECEIVE CH-2 | Y
56 | 400kV | STNMC1Q01M1DIS |  | SPI | CARRIER CHANNEL 1 OUT OF SERVICE | Y
57 | 400kV | STNMC1Q01M1DIS |  | SPI | CARRIER CHANNEL 2 OUT OF SERVICE | Y
58 | 400kV | STNMC1Q01M1DIS |  | SPI | CARRIER CHANNEL 1 FAIL | Y
59 | 400kV | STNMC1Q01M1DIS |  | SPI | CARRIER CHANNEL 2 FAIL | Y
60 | 400kV | STNMC1Q01M1DIS |  | SPI | MAIN 2/1 RELAY FAIL | Y
61 | 400kV | STNMC1Q01M1DIS |  | SPI | CB CLOSE COMMAND FOR SOTF INITIATION |  |  | Text correction
62 | 400kV | STNMC1Q01M1DIS |  | SPI | BCU RELAY FAIL | Y
63 | 400kV | STNMC1Q01M1DIS |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
64 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsA | SPI | START, Z1 R PH |  |  | Addition
65 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsB | SPI | START, Z1 Y PH |  |  | Addition
66 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsC | SPI | START, Z1 B PH |  |  | Addition
67 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP 3PH | Y |  | Addition
68 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP R PH | Y |  | Addition
69 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP Y PH | Y |  | Addition
70 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP B PH | Y |  | Addition
71 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | PREPARE 3-PH TRIP FROM TIE BCU | Y |  | Addition, Available in BCU | It is also required in REL670
72 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | PREPARE 3-PH TRIP FROM MAIN BCU | Y |  | Addition, Available in BCU | It is also required in REL670
73 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | MAIN/ TIE CB AR OPTD | Y |  | Addition, Available in BCU | Only for DR in REL670, for SCADA to be configured from BCU
74 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | MAIN/ TIE LBB PROTECTION OPERATED | Y |  | Addition, Available in BBP | Only for DR in REL670, for SCADA to be configured from LBB/BBP relay
75 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | BUSBAR M1/M2 OPTD | Y |  | Addition, Available in BBP | Only for DR in REL670, for SCADA to be configured from BBP relay
76 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | GROUP RELAY 86A OPTD | Y |  | Available in REL670 (Sig. 52) | Agreed
77 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/EchoWei/stVal | SPI | WEAK INFEED ECHO SEND | Y |  | Addition
78 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/EchoWeiOp/stVal | SPI | WEAK INFEED TRIP | Y |  | Addition
79 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/RvABlk/stVal | SPI | CURRENT REVERSAL DETECTED | Y |  | Addition
80 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
81 | 400kV | STNMC1Q01M1DIS |  | SPI | SETTINGS CHANGED | Y |  | Addition
82 | 400kV | STNMC1Q01M1DIS |  | SPI | DR MEMMORY 80% FULL | Y |  | Addition
83 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltDiskm/mag | AI | DISTANCE MEASUREMENT IN KM | Y |  | Available in REL670 (Sig. 37) | Agreed
84 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltZ/cVal/mag | AI | DISTANCE MEASUREMENT IN IMPEDANCE | Y |  | Available in REL670 (Sig. 38) | Agreed
85 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/MON/L4UFCNTn/CntVal/actVal | AI | CH-1 Code-1 Tx |  |  | CH-1 Code-1 Tx (MAIN-1 CARRIER SEND CHANNEL-1)
86 | 400kV | STNMC1Q01M1DIS |  | AI | CH-1 Code-1 Rx |  |  | CH-1 Code-1 Rx (MAIN-1 CARRIER RECEIVE CHANNEL-1)
87 | 400kV | STNMC1Q01M1DIS |  | AI | CH-1 Code-2 Tx |  |  | CH-1 Code-2 Tx (MAIN-2 CARRIER SEND CHANNEL-1)
88 | 400kV | STNMC1Q01M1DIS |  | AI | CH-1 Code-2 Rx |  |  | CH-1 Code-2 Rx (MAIN-2 CARRIER RECEIVE CHANNEL-1)
89 | 400kV | STNMC1Q01M1DIS |  | AI | CH-2 Code-2 Tx |  |  | CH-2 Code-2 Tx (MAIN-2 CARRIER SEND CHANNEL-2)
90 | 400kV | STNMC1Q01M1DIS |  | AI | CH-2 Code-2 Rx |  |  | CH-2 Code-2 Rx (MAIN-2 CARRIER RECEIVECHANNEL-2)
91 | 400kV | STNMC1Q01M1DIS |  | AI | CH-2 Code-1 Tx |  |  | CH-2 Code-1 Tx (MAIN-1 CARRIER SEND CHANNEL-2)
92 | 400kV | STNMC1Q01M1DIS |  | AI | CH-2 Code-1 Rx |  |  | CH-2 Code-1 Rx (MAIN-1 CARRIER RECEIVE CHANNEL-2)
93 | 400kV | STNMC1Q01M1DIS |  | AI | CH-1 Code-3 Tx |  |  | CH-1 Code-3 Tx (DT SEND CHANNEL-1)
94 | 400kV | STNMC1Q01M1DIS |  | AI | CH-1 Code-3 Rx |  |  | CH-1 Code-3 Rx (DT RECEIVE CHANNEL-1)
95 | 400kV | STNMC1Q01M1DIS |  | AI | CH-2 Code-3 Tx |  |  | CH-2 Code-3 Tx (DT SEND CHANNEL-2)
96 | 400kV | STNMC1Q01M1DIS |  | AI | CH-2 Code-3 Rx |  |  | CH-2 Code-3 Rx (DT RECEIVE CHANNEL-2)
97 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
98 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-2 | Y |  | Addition
99 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-3 | Y |  | Addition
100 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-4 | Y |  | Addition
101 | 400kV | STNMC1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-5 | Y |  | Addition
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR ICT DIFFERENTIAL RELAYS
| IED name: | R_RET670_87T
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/OEXPVPH1/Str/general | SPI | OVEREXCITATION HV START
2 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/OEXPVPH1/Alm/stVal | SPI | OVEREXCITATION HV ALARM | Y
3 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/OEXPVPH1/Op/general | SPI | OVEREXCITATION HV TRIP | Y
4 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/DifAlm/stVal | SPI | DIFFERENTIAL CURRENT ALARM | Y
5 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/general | SPI | DIFFERENTIAL PROTECTION START
6 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsA | SPI | DIFFERENTIAL PROTECTION RPH START
7 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsB | SPI | DIFFERENTIAL PROTECTION YPH START
8 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsC | SPI | DIFFERENTIAL PROTECTION BPH START
9 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Op/general | SPI | DIFFERENTIAL PROTECTION TRIP | Y
10 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION RPH TRIP | Y
11 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION YPH TRIP | Y
12 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION BPH TRIP | Y
13 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/OpRst/stVal | SPI | DIFFERENTIAL PROTECTION TRIP (RESTRAINED MODE) | Y
14 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/OpUnRst/stVal | SPI | DIFFERENTIAL PROTECTION TRIP (UNRESTRAINED MODE) | Y
15 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Blk2H/stVal | SPI | DIFFERENTIAL PROTECTION 2nd HARMONIC BLOCK
16 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Blk5H/stVal | SPI | DIFFERENTIAL PROTECTION 5th HARMONIC BLOCK
17 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SMPPTRC1/Op/general | SPI | DIFFERENTIAL RELAY GENERAL TRIP | Y
18 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
19 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/LPHD1/PhyHealth/stVal | SPI | DIFFRENTIAL IED UNHEALTHY | Y
20 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | OTI ALARM | Y | APPLICABLE FOR 3 PHASE TRANSFORMERS
21 | 400kV | STNMC1Q01TDIF |  | SPI | WTI HV ALARM | Y
22 | 400kV | STNMC1Q01TDIF |  | SPI | WTI IV ALARM | Y
23 | 400kV | STNMC1Q01TDIF |  | SPI | WTI MV ALARM | Y
24 | 400kV | STNMC1Q01TDIF |  | SPI | BUCCHOLZ_n ALARM | Y |  | Addition
25 | 400kV | STNMC1Q01TDIF |  | SPI | BUCCHOLZ_n TRIP | Y |  | Text correction
26 | 400kV | STNMC1Q01TDIF |  | SPI | OSR _n TRIP | Y |  | Text correction
27 | 400kV | STNMC1Q01TDIF |  | SPI | PRD _n TRIP | Y |  | Text correction
28 | 400kV | STNMC1Q01TDIF |  | SPI | FIRE PROTECTION OPERATED | Y
29 | 400kV | STNMC1Q01TDIF |  | SPI | LOW OIL LEVEL | Y
30 | 400kV | STNMC1Q01TDIF |  | SPI | OTI R PH ALARM | Y | APPLICABLE FOR SINGLE PHASE TRANSFORMERS (If a dedicated IED is provided for spare transformer protection, only spare phase signals are required to be used)
31 | 400kV | STNMC1Q01TDIF |  | SPI | OTI Y PH ALARM | Y
32 | 400kV | STNMC1Q01TDIF |  | SPI | OTI B PH ALARM | Y
33 | 400kV | STNMC1Q01TDIF |  | SPI | OTI SPARE ICT ALARM | Y
34 | 400kV | STNMC1Q01TDIF |  | SPI | WTI HV R PH ALARM | Y
35 | 400kV | STNMC1Q01TDIF |  | SPI | WTI HV Y PH ALARM | Y
36 | 400kV | STNMC1Q01TDIF |  | SPI | WTI HV B PH ALARM | Y
37 | 400kV | STNMC1Q01TDIF |  | SPI | WTI HV SPARE ICT ALARM | Y
38 | 400kV | STNMC1Q01TDIF |  | SPI | WTI MV R PH ALARM | Y
39 | 400kV | STNMC1Q01TDIF |  | SPI | WTI MV Y PH ALARM | Y
40 | 400kV | STNMC1Q01TDIF |  | SPI | WTI MV B PH ALARM | Y
41 | 400kV | STNMC1Q01TDIF |  | SPI | WTI MV SPARE ICT ALARM | Y
42 | 400kV | STNMC1Q01TDIF |  | SPI | WTI IV R PH ALARM | Y
43 | 400kV | STNMC1Q01TDIF |  | SPI | WTI IV Y PH ALARM | Y
44 | 400kV | STNMC1Q01TDIF |  | SPI | WTI IV B PH ALARM | Y
45 | 400kV | STNMC1Q01TDIF |  | SPI | WTI IV SPARE ICT ALARM | Y
46 | 400kV | STNMC1Q01TDIF |  | SPI | BUCHHOLZ_n R PH ALARM | Y |  | Addition
47 | 400kV | STNMC1Q01TDIF |  | SPI | BUCHHOLZ_n Y PH ALARM | Y |  | Addition
48 | 400kV | STNMC1Q01TDIF |  | SPI | BUCHHOLZ_n B PH ALARM | Y |  | Addition
49 | 400kV | STNMC1Q01TDIF |  | SPI | BUCHHOLZ_n SPARE ICT TRIP | Y |  | Addition, BUCHHOLZ_n SPARE ICT ALARM
50 | 400kV | STNMC1Q01TDIF |  | SPI | BUCHHOLZ_n R PH TRIP | Y |  | Text correction
51 | 400kV | STNMC1Q01TDIF |  | SPI | BUCHHOLZ_n Y PH TRIP | Y |  | Text correction
52 | 400kV | STNMC1Q01TDIF |  | SPI | BUCHHOLZ_n B PH TRIP | Y |  | Text correction
53 | 400kV | STNMC1Q01TDIF |  | SPI | BUCHHOLZ_n SPARE ICT TRIP | Y |  | Text correction
54 | 400kV | STNMC1Q01TDIF |  | SPI | OSR_n R PH TRIP | Y |  | Text correction
55 | 400kV | STNMC1Q01TDIF |  | SPI | OSR_n Y PH TRIP | Y |  | Text correction
56 | 400kV | STNMC1Q01TDIF |  | SPI | OSR_n B PH TRIP | Y |  | Text correction
57 | 400kV | STNMC1Q01TDIF |  | SPI | OSR_n SPARE ICT TRIP | Y |  | Text correction
58 | 400kV | STNMC1Q01TDIF |  | SPI | PRD n R PH TRIP | Y |  | Text correction
59 | 400kV | STNMC1Q01TDIF |  | SPI | PRD nY PH TRIP | Y |  | Text correction
60 | 400kV | STNMC1Q01TDIF |  | SPI | PRD n B PH TRIP | Y |  | Text correction
61 | 400kV | STNMC1Q01TDIF |  | SPI | PRD n SPARE ICT TRIP | Y |  | Text correction
62 | 400kV | STNMC1Q01TDIF |  | SPI | LOW OIL LEVEL R PH | Y
63 | 400kV | STNMC1Q01TDIF |  | SPI | LOW OIL LEVEL Y PH | Y
64 | 400kV | STNMC1Q01TDIF |  | SPI | LOW OIL LEVEL B PH | Y
65 | 400kV | STNMC1Q01TDIF |  | SPI | LOW OIL LEVEL SPARE ICT | Y
66 | 400kV | STNMC1Q01TDIF |  | SPI | FIRE PROTECTION R PH OPERATED | Y
67 | 400kV | STNMC1Q01TDIF |  | SPI | FIRE PROTECTION Y PH OPERATED | Y
68 | 400kV | STNMC1Q01TDIF |  | SPI | FIRE PROTECTION B PH OPERATED | Y
69 | 400kV | STNMC1Q01TDIF |  | SPI | FIRE PROTECTION SPARE ICT OPERATED | Y
70 | 400kV | STNMC1Q01TDIF |  | SPI | TRIP RELAY 86 A HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
71 | 400kV | STNMC1Q01TDIF |  | SPI | TRIP RELAY 86 B HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
72 | 400kV | STNMC1Q01TDIF |  | SPI | GR A RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RET670, for SCADA to be configured from BCU
73 | 400kV | STNMC1Q01TDIF |  | SPI | GR B RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RET670, for SCADA to be configured from BCU
74 | 400kV | STNMC1Q01TDIF |  | SPI | REF RELAY FAIL | Y
75 | 400kV | STNMC1Q01TDIF |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
** It may be noted that the Body Protection alarms & trips have been Grouped into two separate relays Differential (Group A) & REF (Group B) relays. The hardwiring for same must be done accordingly and approved scheme shall be modified if required. Same is applicable for Reactor protection also.
76 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/OC4_1/OC4PTOC1/Str/general | SPI | TERTIARY 33kV PHASE OVERCURRENT START | Y |  | Addition
77 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/OC4_1/OC4PTOC1/Op/general | SPI | TERTIARY33kV PHASE OVERCURRENT TRIP | Y |  | Addition
78 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/EF4_1/EF4PTOC1/Str/general | SPI | TERTIARY 33kV PHASE EARTHFAULT START | Y |  | Addition
79 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/EF4_1/EF4PTOC1/Op/general | SPI | TERTIARY 33kV PHASE EARTHFAULT TRIP | Y |  | Addition
80 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/ROV2_1/ROV2PTOV1/Str/general | SPI | TERTIARY 33kV PHASE RESIDUAL OVERVOLTAGE START | Y |  | Addition
81 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/ROV2_1/ROV2PTOV1/OP/general | SPI | TERTIARY 33kV PHASE RESIDUAL OVERVOLTAGE TRIP | Y |  | Addition
82 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | TERTIARY 33kV 86 OPTD | Y |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
83 | 400kV | STNMC1Q01TDIF |  | SPI | TERTIARY TRAFO - BUCHHOLZ ALARM | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
84 | 400kV | STNMC1Q01TDIF |  | SPI | TERTIARY TRAFO - BUCHHOLZ TRIP | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
85 | 400kV | STNMC1Q01TDIF |  | SPI | TERTIARY TRAFO - WTI ALARM | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
86 | 400kV | STNMC1Q01TDIF |  | SPI | TERTIARY TRAFO - WTI TRIP | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
87 | 400kV | STNMC1Q01TDIF |  | SPI | TERTIARY TRAFO - OTI ALARM | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
88 | 400kV | STNMC1Q01TDIF |  | SPI | TERTIARY TRAFO - OTI TRIP | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
89 | 400kV | STNMC1Q01TDIF |  | SPI | TERTIARY TRAFO - PRD ALARM | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
90 | 400kV | STNMC1Q01TDIF |  | SPI | TERTIARY TRAFO - PRD TRIP | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
91 | 400kV | STNMC1Q01TDIF |  | SPI | TERTIARY 33KV_TC-1 FAULTY | Y |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
92 | 400kV | STNMC1Q01TDIF |  | SPI | TERTIARY 33KV_TC-2 FAULTY | Y |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
93 | 400kV | STNMC1Q01TDIF |  | SPI | TERTIARY 33kV CB ASSOCIATED ALARMS | Y |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
94 | 400kV | STNMC1Q01TDIF |  | SPI | RELAY IN TEST MODE | Y |  | Addition
95 | 400kV | STNMC1Q01TDIF |  | SPI | SETTINGS CHANGED | Y |  | Addition
96 | 400kV | STNMC1Q01TDIF |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
97 | 400kV | STNMC1Q01TDIF |  | CMD | DELUGE COMMAND |  | APPLICABLE FOR 3 PHASE TRANSFORMERS | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
98 | 400kV | STNMC1Q01TDIF |  | CMD | DELUGE COMMAND R PH |  | APPLICABLE FOR SINGLE PHASE TRANSFORMERS (If a dedicated IED is provided for spare transformer protection, only spare phase signals are required to be used) | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
99 | 400kV | STNMC1Q01TDIF |  | CMD | DELUGE COMMAND Y PH |  |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
100 | 400kV | STNMC1Q01TDIF |  | CMD | DELUGE COMMAND B PH |  |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
101 | 400kV | STNMC1Q01TDIF |  | CMD | DELUGE COMMAND SPARE |  |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
102 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL//EF4_1/EF4PTOC2/Str/general | SPI | NEUTRAL OVERCURRENT ALARM | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
103 | 400kV | STNMC1Q01TDIF | SS_BAY_DIFFERENTIAL//LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
104 | 400kV | STNMC1Q01TDIF |  | SPI | SPARE ALARM-2 | Y |  | Addition
105 | 400kV | STNMC1Q01TDIF |  | SPI | SPARE ALARM-3 | Y |  | Addition
106 | 400kV | STNMC1Q01TDIF |  | SPI | SPARE ALARM-4 | Y |  | Addition
107 | 400kV | STNMC1Q01TDIF |  | SPI | SPARE ALARM-5 | Y |  | Addition
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR ICT REF RELAYS
| IED name: | R_RET670_64
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 400kV | STNMC1Q01TREF | SS_BAY_REF/LD0/OEXPVPH1/Str/general | SPI | OVEREXCITATION MV START
2 | 400kV | STNMC1Q01TREF | SS_BAY_REF/LD0/OEXPVPH1/Alm/stVal | SPI | OVEREXCITATION MV ALARM | Y
3 | 400kV | STNMC1Q01TREF | SS_BAY_REF/LD0/OEXPVPH1/Op/general | SPI | OVEREXCITATION MV TRIP | Y
4 | 400kV | STNMC1Q01TREF | SS_BAY_REF/LD0/HZPDIF1/Alm/stVal | SPI | REF ALARM | Y
5 | 400kV | STNMC1Q01TREF | SS_BAY_REF/LD0/HZPDIF1/Op/general | SPI | REF TRIP | Y
6 | 400kV | STNMC1Q01TREF | SS_BAY_REF/LD0/SMPPTRC1/Op/general | SPI | REF RELAY GENERAL TRIP | Y
7 | 400kV | STNMC1Q01TREF | SS_BAY_REF/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
8 | 400kV | STNMC1Q01TREF | SS_BAY_REF/LD0/LPHD1/PhyHealth/stVal | SPI | REF IED UNHEALTHY | Y
9 | 400kV | STNMC1Q01TREF | SS_BAY_REF/LD0/SP16GGIO n/Ind n/stVal | SPI | OTI TRIP | Y | APPLICABLE FOR 3 PHASE TRANSFORMERS
10 | 400kV | STNMC1Q01TREF |  | SPI | WTI HV TRIP | Y
11 | 400kV | STNMC1Q01TREF |  | SPI | WTI MV TRIP | Y
12 | 400kV | STNMC1Q01TREF |  | SPI | WTI LV TRIP | Y
13 | 400kV | STNMC1Q01TREF |  | SPI | OSR 2 TRIP | Y
14 | 400kV | STNMC1Q01TREF |  | SPI | PRD 2 TRIP | Y
15 | 400kV | STNMC1Q01TREF |  | SPI | BUCCHOLZ_n ALARM | Y |  | Text correction
16 | 400kV | STNMC1Q01TREF |  | SPI | BUCCHOLZ_n TRIP | Y |  | Addition
17 | 400kV | STNMC1Q01TREF |  | SPI | OTI R PH TRIP | Y | APPLICABLE FOR SINGLE PHASE TRANSFORMERS (If a dedicated IED is provided for spare transformer protection, only spare phase signals are required to be used)
18 | 400kV | STNMC1Q01TREF |  | SPI | OTI Y PH TRIP | Y
19 | 400kV | STNMC1Q01TREF |  | SPI | OTI B PH TRIP | Y
20 | 400kV | STNMC1Q01TREF |  | SPI | OTI SPARE ICT TRIP | Y
21 | 400kV | STNMC1Q01TREF |  | SPI | WTI HV R PH TRIP | Y
22 | 400kV | STNMC1Q01TREF |  | SPI | WTI HV Y PH TRIP | Y
23 | 400kV | STNMC1Q01TREF |  | SPI | WTI HV B PH TRIP | Y
24 | 400kV | STNMC1Q01TREF |  | SPI | WTI HV SPARE ICT TRIP | Y
25 | 400kV | STNMC1Q01TREF |  | SPI | WTI MV R PH TRIP | Y
26 | 400kV | STNMC1Q01TREF |  | SPI | WTI MV Y PH TRIP | Y
27 | 400kV | STNMC1Q01TREF |  | SPI | WTI MV B PH TRIP | Y
28 | 400kV | STNMC1Q01TREF |  | SPI | WTI MV SPARE ICT TRIP | Y
29 | 400kV | STNMC1Q01TREF |  | SPI | WTI IV R PH TRIP | Y
30 | 400kV | STNMC1Q01TREF |  | SPI | WTI IV Y PH TRIP | Y
31 | 400kV | STNMC1Q01TREF |  | SPI | WTI IV B PH TRIP | Y
32 | 400kV | STNMC1Q01TREF |  | SPI | WTI IV SPARE ICT TRIP | Y
33 | 400kV | STNMC1Q01TREF |  | SPI | BUCCHOLZ R PH ALARM | Y
34 | 400kV | STNMC1Q01TREF |  | SPI | BUCCHOLZ Y PH ALARM | Y
35 | 400kV | STNMC1Q01TREF |  | SPI | BUCCHOLZ B PH ALARM | Y
36 | 400kV | STNMC1Q01TREF |  | SPI | BUCCHOLZ SPARE ICT ALARM | Y
37 | 400kV | STNMC1Q01TREF |  | SPI | OSR 2 R PH TRIP | Y
38 | 400kV | STNMC1Q01TREF |  | SPI | OSR 2 Y PH TRIP | Y
39 | 400kV | STNMC1Q01TREF |  | SPI | OSR 2 B PH TRIP | Y
40 | 400kV | STNMC1Q01TREF |  | SPI | OSR 2 SPARE ICT TRIP | Y
41 | 400kV | STNMC1Q01TREF |  | SPI | PRD 2 R PH TRIP | Y
42 | 400kV | STNMC1Q01TREF |  | SPI | PRD 2 Y PH TRIP | Y
43 | 400kV | STNMC1Q01TREF |  | SPI | PRD 2 B PH TRIP | Y
44 | 400kV | STNMC1Q01TREF |  | SPI | PRD 2 SPARE ICT TRIP | Y
45 | 400kV | STNMC1Q01TREF |  | SPI | DIFFERENTIAL RELAY FAIL | Y
46 | 400kV | STNMC1Q01TREF |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
47 | 400kV | STNMC1Q01TREF |  | SPI | RELAY IN TEST MODE | Y |  | Addition
48 | 400kV | STNMC1Q01TREF |  | SPI | SETTINGS CHANGED | Y |  | Addition
49 | 400kV | STNMC1Q01TREF |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
50 | 400kV | STNMC1Q01TREF |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
51 | 400kV | STNMC1Q01TREF |  | SPI | SPARE ALARM-2 | Y |  | Addition
52 | 400kV | STNMC1Q01TREF |  | SPI | SPARE ALARM-3 | Y |  | Addition
53 | 400kV | STNMC1Q01TREF |  | SPI | SPARE ALARM-4 | Y |  | Addition
54 | 400kV | STNMC1Q01TREF |  | SPI | SPARE ALARM-5 | Y |  | Addition
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR ICT BACKUP IMPEDANCE PROTECTION RELAY | [7 empty] | Additional Relay - Impedance Protection Signals are part of ICT REF PROTECTION RELAY
| IED name: | R_REL670_21T
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/ZMCAPDIS1/Str/phsA | SPI | BACKUP IMPEDANCE START, Z1 R PH
2 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/ZMCAPDIS1/Str/phsB | SPI | BACKUP IMPEDANCE START, Z1 Y PH
3 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMPE/LD0/ZMCAPDIS1/Str/phsC | SPI | BACKUP IMPEDANCE START, Z1 B PH
4 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS1.Str.general | SPI | BACKUP IMPEDANCE START |  |  | BACKUP IMPEDANCE ZONE-1 START | Agreed
5 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS1.Op.general | SPI | BACKUP IMPEDANCE ZONE-1 TRIP | Y
6 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/ZMCAPDIS2/Str/phsA | SPI | BACKUP IMPEDANCE START, Z2 R PH
7 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/ZMCAPDIS2/Str/phsB | SPI | BACKUP IMPEDANCE START, Z2 Y PH
8 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMPE/LD0/ZMCAPDIS2/Str/phsC | SPI | BACKUP IMPEDANCE START, Z2B PH
9 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS2.Str.general | SPI | BACKUP IMPEDANCE ZONE-2 START
10 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS2.Op.general | SPI | BACKUP IMPEDANCE ZONE-2 TRIP | Y
11 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS3.Str.general | SPI | BACKUP IMPEDANCE ZONE-3 START
12 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS3.Op.general | SPI | BACKUP IMPEDANCE ZONE-3 TRIP | Y
13 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS4.Str.general | SPI | BACKUP IMPEDANCE ZONE-4 START
14 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS4.Op.general | SPI | BACKUP IMPEDANCE ZONE-4 TRIP | Y
15 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SMPPTRC1/Op/general | SPI | BACKUP IMPEDANCE RELAY GENERAL TRIP | Y
16 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/OC4_1/OC4PTOC1/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 START |  |  | OC/EF PROTECTION SIGNALS ARE PART OF HV DIRECTIONAL OVERCURRENT & EARTHFAULT PROTECTION RELAY
17 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/OC4_1/OC4PTOC1/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 TRIP | Y
18 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/EF4_1/EF4PTOC1/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 START
19 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/EF4_1/EF4PTOC1/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 TRIP | Y
20 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/OC4_1/OC4PTOC2/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 START
21 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/OC4_1/OC4PTOC2/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 TRIP | Y
22 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/EF4_1/EF4PTOC2/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 START
23 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/EF4_1/EF4PTOC2/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 TRIP | Y
24 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SMPPTRC/*** | SPI | BACKUP IMPEDANCE GENERAL TRIP 3PH | Y
25 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SMPPTRC/*** | SPI | BACKUP IMPEDANCE GENERAL TRIP R PH | Y
26 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SMPPTRC/*** | SPI | BACKUP IMPEDANCE GENERAL TRIP Y PH | Y
27 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SMPPTRC/*** | SPI | BACKUP IMPEDANCE GENERAL TRIP B PH | Y
28 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
29 | 400kV | STNMC1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
30 | 400kV | STNMC1Q01THVBIMP |  | SPI | BACKUP IMPEDANCE IED UNHEALTHY | Y
31 | 400kV | STNMC1Q01THVBIMP |  | SPI | RELAY IN TEST MODE | Y
32 | 400kV | STNMC1Q01THVBIMP |  | SPI | SETTINGS CHANGED | Y
33 | 400kV | STNMC1Q01THVBIMP |  | SPI | DR MEMORY 80% FULL | Y
34 | 400kV | STNMC1Q01THVBIMP |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
35 | 400kV | STNMC1Q01THVBIMP |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
36 | 400kV | STNMC1Q01THVBIMP |  | SPI | SPARE ALARM-2 | Y
37 | 400kV | STNMC1Q01THVBIMP |  | SPI | SPARE ALARM-3 | Y
38 | 400kV | STNMC1Q01THVBIMP |  | SPI | SPARE ALARM-4 | Y
39 | 400kV | STNMC1Q01THVBIMP |  | SPI | SPARE ALARM-5 | Y
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR HV DIRECTIONAL OVERCURRENT AND EARTH FAULT RELAYS
| IED name: | R_REL670_HVBUP
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 400kV | STNMC1Q01THBU | SS_BAY_HV BACKUP OC EF/OC4_1/OC4PTOC1/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 START |  |  | Text correction
2 | 400kV | STNMC1Q01THBU | SS_BAY_HV BACKUP OC EFE/OC4_1/OC4PTOC1/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 TRIP | Y |  | Text correction
3 | 400kV | STNMC1Q01THBU | SS_BAY_HV BACKUP OC EF/EF4_1/EF4PTOC1/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 START |  |  | Text correction
4 | 400kV | STNMC1Q01THBU | SS_BAY_HV BACKUP OC EF/EF4_1/EF4PTOC1/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 TRIP | Y |  | Text correction
5 | 400kV | STNMC1Q01THBU | SS_BAY_HV BACKUP OC EF/OC4_1/OC4PTOC2/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 START |  | if Non Directional then name has to be replaced with Directional to Non-Directional | Addition
6 | 400kV | STNMC1Q01THBU | SS_BAY_HV BACKUP OC EF/OC4_1/OC4PTOC2/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 TRIP | Y |  | Addition
7 | 400kV | STNMC1Q01THBU | SS_BAY_HV BACKUP OC EF/EF4_1/EF4PTOC2/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 START |  |  | Addition
8 | 400kV | STNMC1Q01THBU | SS_BAY_HV BACKUP OC EF/EF4_1/EF4PTOC2/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 TRIP | Y |  | Addition
9 | 400kV | STNMC1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
10 | 400kV | STNMC1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/SMPPTRC1/Op/general | SPI | GENERAL TRIP | Y
11 | 400kV | STNMC1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
12 | 400kV | STNMC1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/LPHD1/PhyHealth/stVal | SPI | BACKUP OC/EF IED UNHEALTHY | Y
13 | 400kV | STNMC1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/SP16GGIO n/Ind n/stVal | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
14 | 400kV | STNMC1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
15 | 400kV | STNMC1Q01THBU |  | SPI | SETTINGS CHANGED | Y |  | Addition
16 | 400kV | STNMC1Q01THBU |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
17 | 400kV | STNMC1Q01THBU |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
18 | 400kV | STNMC1Q01THBU |  | SPI | SPARE ALARM-2 | Y |  | Addition
19 | 400kV | STNMC1Q01THBU |  | SPI | SPARE ALARM-3 | Y |  | Addition
20 | 400kV | STNMC1Q01THBU |  | SPI | SPARE ALARM-4 | Y |  | Addition
21 | 400kV | STNMC1Q01THBU |  | SPI | SPARE ALARM-5 | Y |  | Addition
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR LV DIRECTIONAL OVERCURRENT AND EARTH FAULT RELAYS
| IED name: | R_REL670_LVBUP
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 400kV | STNMC1Q01TLBU | SS_BAY_LV BACKUP OC EF/OC4_1/OC4PTOC1/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 START |  |  | Text correction
2 | 400kV | STNMC1Q01TLBU | SS_BAY_LV BACKUP OC EFE/OC4_1/OC4PTOC1/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 TRIP | Y |  | Text correction
3 | 400kV | STNMC1Q01TLBU | SS_BAY_LV BACKUP OC EF/EF4_1/EF4PTOC1/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 START |  |  | Text correction
4 | 400kV | STNMC1Q01TLBU | SS_BAY_LV BACKUP OC EF/EF4_1/EF4PTOC1/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 TRIP | Y |  | Text correction
5 | 400kV | STNMC1Q01TLBU | SS_BAY_LV BACKUP OC EF/OC4_1/OC4PTOC2/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 START |  | if Non Directional then name has to be replaced with Directional to Non-Directional | Addition
6 | 400kV | STNMC1Q01TLBU | SS_BAY_LV BACKUP OC EF/OC4_1/OC4PTOC2/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 TRIP | Y |  | Addition
7 | 400kV | STNMC1Q01TLBU | SS_BAY_LV BACKUP OC EF/EF4_1/EF4PTOC2/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 START |  |  | Addition
8 | 400kV | STNMC1Q01TLBU | SS_BAY_LV BACKUP OC EF/EF4_1/EF4PTOC2/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 TRIP | Y |  | Addition
9 | 400kV | STNMC1Q01TLBU | SS_BAY_LV BACKUP OC EF/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
10 | 400kV | STNMC1Q01TLBU | SS_BAY_LV BACKUP OC EF/LD0/SMPPTRC1/Op/general | SPI | GENERAL TRIP | Y
11 | 400kV | STNMC1Q01TLBU | SS_BAY_LV BACKUP OC EF/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
12 | 400kV | STNMC1Q01TLBU | SS_BAY_LV BACKUP OC EF/LD0/LPHD1/PhyHealth/stVal | SPI | BACKUP OC/EF IED UNHEALTHY | Y
13 | 400kV | STNMC1Q01TLBU | SS_BAY_LV BACKUP OC EF/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
14 | 400kV | STNMC1Q01TLBU |  | SPI | SETTINGS CHANGED | Y |  | Addition
15 | 400kV | STNMC1Q01TLBU |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
16 | 400kV | STNMC1Q01TLBU |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR REACTOR DIFFERENTIAL RELAYS
| IED name: | R_RET670_87R
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Op/general | SPI | DIFFERENTIAL PROTECTION TRIP | Y
2 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION RPH TRIP | Y
3 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION YPH TRIP | Y
4 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION BPH TRIP | Y
5 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/DifAlm/stVal | SPI | DIFFERENTIAL CURRENT ALARM
6 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/general | SPI | DIFFERENTIAL PROTECTION START
7 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsA | SPI | DIFFERENTIAL PROTECTION RPH START
8 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsB | SPI | DIFFERENTIAL PROTECTION YPH START
9 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsC | SPI | DIFFERENTIAL PROTECTION BPH START
10 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SMPPTRC1/Op/general | SPI | DIFFERENTIAL RELAY GENERAL TRIP | Y
11 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/OpRst/stVal | SPI | DIFFERENTIAL PROTECTION TRIP (RESTRAINED MODE) | Y |  | Addition
12 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/OpUnRst/stVal | SPI | DIFFERENTIAL PROTECTION TRIP (UNRESTRAINED MODE) | Y |  | Addition
13 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Blk2H/stVal | SPI | DIFFERENTIAL PROTECTION 2nd HARMONIC BLOCK |  |  | Addition
14 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Blk5H/stVal | SPI | DIFFERENTIAL PROTECTION 5th HARMONIC BLOCK |  |  | Addition
15 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | BUSBAR PROT OPTD | Y |  | Addition, Need to discuss | Only for DR in RET670, for SCADA to be configured from BBP relay
16 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
17 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/LPHD1/PhyHealth/stVal | SPI | DIFFRENTIAL IED UNHEALTHY | Y |  |  | *
18 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | OTI TRIP | Y | APPLICABLE FOR 3 PHASE REACTORS | Interchanged between Diff. & REF relays
19 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | WTI ALARM | Y |  | Already available
20 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | BUCCHOLZ-A TRIP | Y |  | Addition
21 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | BUCCHOLZ-B ALARM | Y |  | Addition
22 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | PRV-1 TRIP(NO) | Y |  | Text correction
23 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | FIRE PROTECTION OPERATED | Y |  | Already available
24 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | LOW OIL LEVEL ALARM | Y |  | Already available
25 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | PRV-1 TRIP(NC) | Y |  | Addition, Need to discuss | Yet to be finalized by PGCIL
26 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | FLOW SENSITIVE CONSERVATOR VALVE ALARM | Y |  | Addition
27 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | REACTOR MB ALARMS | Y |  | Addition
28 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | OTI R PH ALARM | Y | APPLICABLE FOR SINGLE PHASE REACTORS (If a dedicated IED is provided for spare reactor protection, only spare phase signals are required to be used)
29 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | OTI Y PH ALARM | Y
30 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | OTI B PH ALARM | Y
31 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | OTI SPARE PH ALARM | Y
32 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | WTI R PH ALARM | Y
33 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | WTI Y PH ALARM | Y
34 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | WTI B PH ALARM | Y
35 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | WTI SPARE PH ALARM | Y
36 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | BUCCHOLZ_n R PH ALARM | Y |  | Interchanged between Diff. & REF relays
37 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | BUCCHOLZ_n Y PH ALARM | Y |  | Interchanged between Diff. & REF relays
38 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | BUCCHOLZ_n B PH ALARM | Y |  | Interchanged between Diff. & REF relays
39 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | BUCCHOLZ_n SPARE PH ALARM | Y |  | Interchanged between Diff. & REF relays
40 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | BUCCHOLZ_n R PH TRIP | Y |  | Text correction
41 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | BUCCHOLZ_n Y PH TRIP | Y |  | Text correction
42 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | BUCCHOLZ_n B PH TRIP | Y |  | Text correction
43 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | BUCCHOLZ_n SPARE PH TRIP | Y |  | Text correction
44 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | OSR R PH TRIP | Y
45 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | OSR Y PH TRIP | Y
46 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | OSR B PH TRIP | Y
47 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | OSR SPARE PH TRIP | Y
48 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | PRD R PH TRIP | Y |  |  | Yet to be finalized by PGCIL
49 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | PRD Y PH TRIP | Y |  |  | Yet to be finalized by PGCIL
50 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | PRD B PH TRIP | Y |  |  | Yet to be finalized by PGCIL
51 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | PRD SPARE PH TRIP | Y
52 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | LOW OIL LEVEL R PH | Y
53 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | LOW OIL LEVEL Y PH | Y
54 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | LOW OIL LEVEL B PH | Y
55 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | LOW OIL LEVEL SPARE PH | Y
56 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | FIRE PROTECTION R PH OPERATED | Y
57 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | FIRE PROTECTION Y PH OPERATED | Y
58 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | FIRE PROTECTION B PH OPERATED | Y
59 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | FIRE PROTECTION SPARE ICT OPERATED | Y
60 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | TRIP RELAY 86 A HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
61 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | TRIP RELAY 86 B HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
62 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | GR A RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RET670, for SCADA to be configured from BBP relay
63 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | GR B RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RET670, for SCADA to be configured from BBP relay
64 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | GR A RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Available in RET670 (Sig. 62)
65 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | GR B RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Available in RET670 (Sig. 63)
66 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | REF RELAY FAIL | Y
67 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | RELAY IN TEST MODE | Y |  | Addition
68 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | SETTINGS CHANGED | Y |  | Addition
69 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
70 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
71 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
72 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | SPARE ALARM-2 | Y |  | Addition
73 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | SPARE ALARM-3 | Y |  | Addition
74 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | SPARE ALARM-4 | Y |  | Addition
75 | 400kV | STNMC1Q01LRDIF /STNMC1Q01BRDIF |  | SPI | SPARE ALARM-5 | Y |  | Addition
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR REACTOR REF RELAYS
| IED name: | R_RET670_64R
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF | SS_BAY_REF/LD0/HZPDIF1/Alm/stVal | SPI | REF ALARM | Y
2 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF | SS_BAY_REF/LD0/HZPDIF1/Op/general | SPI | REF TRIP | Y
3 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF | SS_BAY_REF/LD0/SMPPTRC1/Op/general | SPI | REF RELAY GENERAL TRIP | Y
4 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF | SS_BAY_REF/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
5 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF | SS_BAY_REF/LD0/LPHD1/PhyHealth/stVal | SPI | REF IED UNHEALTHY | Y
6 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF | SS_BAY_REF/LD0/SP16GGIO n/Ind n/stVal | SPI | OTI ALARM | Y | APPLICABLE FOR 3 PHASE REACTORS | Interchanged between Diff. & REF relays
7 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | WTI TRIP | Y |  | Already available
8 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | BUCCHOLZ-A ALARM | Y |  | Addition
9 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | BUCCHOLZ-B TRIP | Y |  | Addition
10 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | PRV-2 TRIP | Y |  | Addition
11 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | FIRE PROTECTION OPERATED | Y |  | Addition
12 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | HIGH LEVEL OIL ALARM | Y |  | Addition
13 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | 86B TRIP RELAY SUPERVSION ALARM | Y |  | Addition, Need to discuss
14 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | REACTOR MB ALARMS | Y |  | Addition
15 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | OTI R PH TRIP | Y | APPLICABLE FOR SINGLE PHASE REACTORS (If a dedicated IED is provided for spare Reactor protection, only spare phase signals are required to be used)
16 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | OTI Y PH TRIP | Y
17 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | OTI B PH TRIP | Y
18 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | OTI SPARE PH TRIP | Y
19 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | WTI R PH TRIP | Y
20 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | WTI Y PH TRIP | Y
21 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | WTI B PH TRIP | Y
22 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | WTI SPARE PH TRIP | Y
23 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | BUCCHOLZ R PH ALARM | Y
24 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | BUCCHOLZ Y PH ALARM | Y
25 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | BUCCHOLZ B PH ALARM | Y
26 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | BUCCHOLZ SPARE PH ALARM | Y
27 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | DIFFERENTIAL RELAY FAIL | Y
28 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | RELAY IN TEST MODE | Y |  | Addition
29 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | SETTINGS CHANGED | Y |  | Addition
30 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
31 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
32 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | SPARE ALARM-2 | Y |  | Addition
33 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | SPARE ALARM-3 | Y |  | Addition
34 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | SPARE ALARM-4 | Y |  | Addition
35 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | SPARE ALARM-5 | Y |  | Addition
36 | 400kV | STNMC1Q01LRREF /STNMC1Q01BRREF |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR REACTOR BACKUP IMPEDANCE PROTECTION RELAY
| IED name: | R_REL670_21R
SL. NO. | Voltage Level | ` | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/LD0.ZMHPDIS1.Str.general | SPI | BACKUP IMPEDANCE START
2 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/LD0.ZMHPDIS1.Op.general | SPI | BACKUP IMPEDANCE TRIP | Y
3 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/LD0/SMPPTRC1/Op/general | SPI | BACKUP IMPEDANCE RELAY GENERAL TRIP | Y
4 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/OC4_1/OC4PTOC1/Str/general | SPI | BACKUP OVERCURRENT START
5 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/OC4_1/OC4PTOC1/Op/general | SPI | BACKUP OVERCURRENT TRIP | Y
6 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/EF4_1/EF4PTOC1/Str/general | SPI | BACKUP EARTHFAULT START
7 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/EF4_1/EF4PTOC1/Op/general | SPI | BACKUP EARTHFAULT TRIP | Y
8 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
9 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
10 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP | SS_BAY_BUP IMPEDANCE/LD0/LPHD1/PhyHealth/stVal | SPI | BACKUP IMPEDANCE IED UNHEALTHY | Y
11 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP | SS_BAY_HV BACKUP OC EF/LD0/LPHD1/PhyHealth/stVal | SPI | NGR BUCHHOLZ ALARM | Y | For Line Reactor NGR associated alarms | Addition
12 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | NGR BUCHHOLZ TRIP | Y |  | Addition
13 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | NGR OTI ALARM | Y |  | Addition
14 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | NGR OTI TRIP | Y |  | Addition
15 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | NGR WTI ALARM | Y |  | Addition
16 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | NGR WTI TRIP | Y |  | Addition
17 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | NGR OSR TRIP | Y |  | Addition
18 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | NGR CB ASSOCIATED ALARMS | Y | All NGC CB associated alarms to be monitored | Addition
19 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | NGR BYPASS ISOLATOR ASSOCIATED ALARMS | Y | All NGR Bypass Isolator associated alarms to be monitored | Addition
20 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | BACKUP IMPEDANCE IED UNHEALTHY | Y |  | Addition
21 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | CMD | NGR BYPASS COMMAND | Y |  | Addition
22 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | RELAY IN TEST MODE | Y |  | Addition
23 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | SETTINGS CHANGED | Y |  | Addition
24 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | DR MEMMORY 80% FULL | Y |  | Addition
25 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
26 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
27 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | SPARE ALARM-2 | Y |  | Addition
28 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | SPARE ALARM-3 | Y |  | Addition
29 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | SPARE ALARM-4 | Y |  | Addition
30 | 400kV | STNMC1Q01LRBIMP /STNMC1Q01LRBIMP |  | SPI | SPARE ALARM-5 | Y |  | Addition
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR BUSBAR PROTECTION RELAYS (DECENTRALIZED) - REB 500
| IED name: | BB_REB500_87B
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/BCZ_PDIF1/DifAlm | SPI | BUSBAR CHECKZONE ALARM | Y |  | Addition
2 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/BCZ_PDIF1/Op/general | SPI | BUSBAR CHECKZONE TRIP | Y |  | Addition
3 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/CALH1/GrAlm2/stVal | SPI | BUSBAR CT CIRCUIT ERROR | Y |  |  | Agreed
4 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF1/Op/PhsA | SPI | BUSBAR ZONE 1 TRIP R- PHASE | Y |  | Addition, BUSBAR TRIP R- PHASE is configurable (Zone1/2 phasewise trip signal is not configurable)
5 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF1/Op/PhsB | SPI | BUSBAR ZONE 1 TRIP Y- PHASE | Y |  | Addition, BUSBAR TRIP Y- PHASE Is configurable (Zone1/2 phasewise trip signal is not configurable)
6 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF1/Op/PhsC | SPI | BUSBAR ZONE 1 TRIP B- PHASE | Y |  | Addition, BUSBAR TRIP B- PHASE Is configurable (Zone1/2 phasewise trip signal is not configurable)
7 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF1/Op/general | SPI | BUSBAR ZONE 1 TRIP | Y
8 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/BZ_PDIF1/Blk | SPI | BUSBAR ZONE 1 BLOCKED | Y
9 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | BREAKER FAILURE - BUSBAR 1 BLOCKED | Y |  | Addition, Need to discuss (Signal not configurable), Sig. 8 (BUSBAR ZONE 1 BLOCKED) is common blocking signal which will active when busbar blocked from external switch, Isolator intermidiate status, CT Circuit error conditions)
10 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF1/DifAlm | SPI | BUSBAR ZONE-1 CT CIRCUIT ERROR | Y |  | BUSBAR CT CIRCUIT ERROR is configured in Signal No.-03 (Zone1/2 CT CIRCUIT signal not configurable)
11 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | BUSBAR ZONE 1 BLOCKED EXTERNAL BY SWITCH | Y
12 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF2/Op/PhsA | SPI | BUSBAR ZONE 2 TRIP R- PHASE | Y |  | Addition, BUSBAR TRIP R- PHASE is configurable (Zone1/2 phasewise trip signal is not configurable)
13 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF2/Op/PhsB | SPI | BUSBAR ZONE 2 TRIP Y- PHASE | Y |  | Addition, BUSBAR TRIP Y- PHASE Is configurable (Zone1/2 phasewise trip signal is not configurable)
14 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF2/Op/PhsC | SPI | BUSBAR ZONE 2 TRIP B- PHASE | Y |  | Addition, BUSBAR TRIP B- PHASE Is configurable (Zone1/2 phasewise trip signal is not configurable)
15 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF2/Op/general | SPI | BUSBAR ZONE 2 TRIP | Y
16 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/BZ_PDIF2/Blk | SPI | BUSBAR ZONE 2 BLOCKED | Y
17 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | BREAKER FAILURE - BUSBAR 2 BLOCKED | Y |  | Addition, Need to discuss (Signal not configurable), Sig. 15 (BUSBAR ZONE 2 BLOCKED) is common blocking signal which will active when busbar blocked from external switch, Isolator intermidiate status, CT Circuit error conditions)
18 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/BBP_PDIF2/DifAlm | SPI | BUSBAR ZONE-2 CT CIRCUIT ERROR | Y |  | BUSBAR CT CIRCUIT ERROR is configured in Signal No.-03 (Zone1/2 CT CIRCUIT signal not configurable)
19 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | BUSBAR ZONE 2 BLOCKED EXTERNAL BY SWITCH | Y
20 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/CALH1/GrAlm1/stVal | SPI | ISOLATOR IN INTERMEDIATE STATUS | Y | TO BE USED RELATES TO STATUS OF SWITCHING ELEMENT
21 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/PTRC/Tr/general | SPI | BAY N TRIP | Y | For each Bays
22 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB0 n/LPHD n/PhyHealth/stVal | SPI | BUSBAR BLOCKED DUE TO COMMUNICATION ERROR_Bay_n | Y | For each Bays
23 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/GAPC/Ind08/stVal | SPI | BAY_N_BREAKER FAILURE R-PH INITIATION | Y | For each Bays | Addition
24 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/GAPC/Ind09/stVal | SPI | BAY_N_BREAKER FAILURE Y-PH INITIATION | Y | For each Bays | Addition
25 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/GAPC/Ind10/stVal | SPI | BAY_N_BREAKER FAILURE B-PH INITIATION | Y | For each Bays | Addition
26 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/GAPC/Ind11/stVal | SPI | BAY_N_BREAKER FAILURE 3PH INITIATION | Y | For each Bays | Addition
27 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/GAPC/Ind04/stVal | SPI | BAY_N_EXTERNAL BUSBAR ZONE n | Y | For signals where BB tripped through External Tripping commands(GD, Half Dia) | Addition
28 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/RBRF/OpIn/general | SPI | BAY_N_BREAKER FAILURE RETRIP | Y | For each Bays | Addition
29 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/RBRF/OpEx/general | SPI | BAY_N_BREAKER FAILURE BACKTRIP | Y | For each Bays | Addition
30 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/RBRF/OpIn/PhsA | SPI | BAY_N_BREAKER FAILURE RPH- RETRIP | Y | For each Bays | Addition
31 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/RBRF/OpIn/PhsB | SPI | BAY_N_BREAKER FAILURE YPH- RETRIP | Y | For each Bays | Addition
32 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB0/BP_n/RBRF/OpIn/PhsC | SPI | BAY_N_BREAKER FAILURE BPH- RETRIP | Y | For each Bays | Addition
33 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/LPHD1/PhyHealth/stVal | SPI | BBP CENTRAL UNIT IED UNHEALTHY | Y
34 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
35 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SETTINGS CHANGED | Y |  | Addition, Need to discuss (Signal not configurable)
36 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme | Addition
37 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-1 | Y | ** 10 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
38 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-2 | Y |  | Addition
39 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-3 | Y |  | Addition
40 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-4 | Y |  | Addition
41 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-5 | Y |  | Addition
42 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-6 | Y |  | Addition
43 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-7 | Y |  | Addition
44 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-8 | Y |  | Addition
45 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-9 | Y |  | Addition
46 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-10 | Y |  | Addition
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 10 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR BUSBAR PROTECTION RELAYS (CENTRALIZED) - REB 670
| IED name: | BB_REB670_87B
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/BBS/BZBSPDIF1/Op/general | SPI | BUSBAR ZONE 1 TRIP | Y | BBS - Single Phase & BBT-Three Phase Variant. STNMD1BBM1R/Y/B if phasewise Busbar IEDs are deployed.
2 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/BBS/BZBSPDIF2/Op/general | SPI | BUSBAR ZONE 2 TRIP | Y
3 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/BBS/BZBSPDIF1/OpnCTAlm/stVal | SPI | BUSBAR ZONE 1 CT CIRCUIT ERROR | Y
4 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/BBS/BZBSPDIF2/OpnCTAlm/stVal | SPI | BUSBAR ZONE 2 CT CIRCUIT ERROR | Y
5 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/LD0/SP16GGIO n /Ind n/stVal | SPI | BUSBAR ZONE 1 BLOCKED EXTERNAL BY SWITCH | Y
6 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/LD0/SP16GGIO n /Ind n/stVal | SPI | BUSBAR ZONE 2 BLOCKED EXTERNAL BY SWITCH | Y
7 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/LD0/SP16GGIO n /Ind n/stVal | SPI | BUSBAR ZONE 1 PROTECTION BLOCKED | Y
8 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/LD0/SP16GGIO n /Ind n/stVal | SPI | BUSBAR ZONE 2 PROTECTION BLOCKED | Y
9 | 400kV | STNMB1BBM1 /STNMB1BBM2 | SS_BAY_BUSBAR/BBS6/BCZPDIF1/Op/general | SPI | BUSBAR CHECKZONE TRIP | Y
10 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/BBS/BBSPTRC n/Tr/general | SPI | BAY n TRIP | Y | **** If Bay Breaker Failure function internally utilised then BFP related Initiation, Retrip, Backtrip & other signal refered with Standalone LBB relay.
11 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/LD0/SP16GGIO n/Ind n/stVal | SPI | BAY n BREAKER FAILURE BACKUP TRIP | Y | For each bay signals to be configured and reported | Addition
12 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/LD0/SP16GGIO n/Ind n/stVal | SPI | LCC BUSBAR GAS ZONE TRIP | Y | If Applicable for GIS | Addition
13 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
14 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/LD0/LPHD1/PhyHealth/stVal | SPI | BBP IED UNHEALTHY | Y
15 | 400kV | STNMC1BBM1 /STNMC1BBM2 | SS_BAY_BUSBAR/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
16 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SETTINGS CHANGED | Y |  | Addition
17 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | DR MEMMORY 80% FULL | Y |  | Addition
18 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-1 | Y | ** 10 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
19 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-2 | Y |  | Addition
20 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-3 | Y |  | Addition
21 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-4 | Y |  | Addition
22 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-5 | Y |  | Addition
23 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-6 | Y |  | Addition
24 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-7 | Y |  | Addition
25 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-8 | Y |  | Addition
26 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-9 | Y |  | Addition
27 | 400kV | STNMC1BBM1 /STNMC1BBM2 |  | SPI | SPARE ALARM-10 | Y |  | Addition
28 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | BUSBAR ZONE 1 TRIP R- PHASE | Y |  | Addition
29 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | BUSBAR ZONE 1 TRIP Y- PHASE | Y |  | Addition
30 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | BUSBAR ZONE 1 TRIP B- PHASE | Y |  | Addition
31 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | BUSBAR ZONE 2 TRIP R- PHASE | Y |  | Addition
32 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | BUSBAR ZONE 2 TRIP Y- PHASE | Y |  | Addition
33 | 765kV | STNMB1BBM1 /STNMB1BBM2 |  | SPI | BUSBAR ZONE 2 TRIP B- PHASE | Y |  | Addition
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 10 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR BREAKER FAILURE PROTECTION RELAY
| IED name: | R_RELAY NAME_50BFR
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/GGIO n/ST/ Ind n | SPI | BREAKER FAILURE PROTECTION START | Y
2 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/CCRBRF1/OpEx/general | SPI | BREAKER FAILURE BACKUP TRIP | Y |  | Text correction
3 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/CCRBRF1/OpIn/general | SPI | BREAKER FAILURE RETRIP | Y
4 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/CCRBRF1/OpIn/PhsA | SPI | BREAKER FAILURE RETRIP RPH | Y |  | Addition
5 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/CCRBRF1/OpIn/PhsB | SPI | BREAKER FAILURE RETRIP YPH | Y |  | Addition
6 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/CCRBRF1/OpIn/PhsC | SPI | BREAKER FAILURE RETRIP BPH | Y |  | Addition
7 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
8 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/LPHD1/PhyHealth/stVal | SPI | BFP IED UNHEALTHY | Y
9 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | BREAKER FAILURE R-PHASE INITIATION FROM M1/M2 | Y |  | Addition
10 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | BREAKER FAILURE Y-PHASE INITIATION FROM M1/M2 | Y |  | Addition
11 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | BREAKER FAILURE B-PHASE INITIATION FROM M1/M2 | Y |  | Addition
12 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | BREAKER FAILURE 3-PHASE INITIATION FROM 86A/86B/BB | Y |  | Addition
13 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | BREAKER FAILURE FROM LCC (If applicable) | Y | Applicable for GIS LCC | Addition
14 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | IV GR-A INT TRIP RELAY OPTD (If applicable) | Y | Applicable for ICT Bays incomers | Addition
15 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | IV GR-B INT TRIP RELAY OPTD (If applicable) | Y |  | Addition
16 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
17 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | SETTINGS CHANGED | Y |  | Addition
18 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | DR MEMMORY 80% FULL | Y |  | Addition
19 | 400kV | STNMC1Q01BFR | SS_BAY_BREAKER FAILURE/LD0/SP16GGIO n/Ind n/stVal | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
20 | 400kV | STNMC1Q01BFR |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
21 | 400kV | STNMC1Q01BFR |  | SPI | SPARE ALARM-2 | Y |  | Addition
22 | 400kV | STNMC1Q01BFR |  | SPI | SPARE ALARM-3 | Y |  | Addition
23 | 400kV | STNMC1Q01BFR |  | SPI | SPARE ALARM-4 | Y |  | Addition
24 | 400kV | STNMC1Q01BFR |  | SPI | SPARE ALARM-5 | Y |  | Addition
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR BAY CONTROL UNIT
| IED name: | R_REC670_BCU
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | ADDITIONAL REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/QCBAY1/LocSwPos/stVal | INT | BCU IN LOCAL/ REMOTE
2 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/Op/general | SPI | CLOSE COMMAND FROM BCU FOR AUTORECLOSE |  | FOR BCUs HAVING AUTORECLSOURE FUNCTION INBUILT
3 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | GR-A TRIP RELAY FAULTY | Y |  |  | Addition
4 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | GR-B TRIP RELAY FAULTY | Y |  |  | Addition
5 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | DT RECEIVE CHANNEL-1 | Y |  |  | Addition, Available in REL670 | Only for DR in REL670, for SCADA to be configured from BCU
6 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | DT RECEIVE CHANNEL-2 | Y |  |  | Addition, Available in REL670 | Only for DR in REL670, for SCADA to be configured from BCU
7 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/AutoRecSt/StVal | SPI | AUTORECLOSE FUNCTION ON | Y |  |  | Addition
8 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/AutoRecSt/StVal | SPI | AUTORECLOSE FUNCTION OFF | Y |  |  | Addition
9 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | START AUTORECLOSE FUNCTION | Y |  |  | Addition
10 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/BlkRec/stVal | SPI | BLOCK AUTORECLOSE FUNCTION | Y
11 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/Prp3PhOp/stVal | SPI | PREPARE 3PH TRIP AUTORECLOSE | Y
12 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/RdyRec/stVal | SPI | AUTORECLOSE FUNCTION READY |  |  |  | Text correction
13 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/ActRec/stVal | SPI | AUTORECLOSE IN PROGRESS | Y |  |  | Text correction
14 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/SucRec/stVal | SPI | AUTORECLOSE SUCCESSFUL | Y |  |  | Text correction
15 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/UnsRec/stVal | SPI | AUTORECLOSE UNSUCCESSFUL | Y |  |  | Text correction
16 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SXCBR1/Pos/stVal | DPI | BAY_CB R PH POSITION
17 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SXCBR2/Pos/stVal | DPI | BAY_CB Y PH POSITION
18 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SXCBR3/Pos/stVal | DPI | BAY_CB B PH POSITION
19 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI1/Pos/stVal | DPI | BAY_CB POSITION
20 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI1/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI1/Pos/ctlOperOn for Close | CMD | BAY_CB_COMMAND |  | CLOSE / OPEN
21 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO1/EnaOpn/stVal | SPI | BAY_CB_OPEN PERMITTED OR ENABLED
22 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO1/EnaCls/stVal | SPI | BAY_CB_CLOSE PERMITTED OR ENABLED
23 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI2/Pos/stVal | DPI | BAY_89A_ISOLATOR POSITION
24 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI2/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI2/Pos/ctlOperOn for Close | CMD | BAY_89A_ISO COMMAND |  | CLOSE / OPEN
25 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO2/EnaOpn/stVal | SPI | BAY_89A_ISO OPEN PERMITTED OR ENABLED
26 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO2/EnaCls/stVal | SPI | BAY_89A_ISO CLOSE PERMITTED OR ENABLED
27 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI3/Pos/stVal | DPI | BAY_89AE/AE1_ISOLATOR POSITION
28 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI3/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI3/Pos/ctlOperOn for Close | CMD | BAY_89AE/AE1_ISO COMMAND |  | CLOSE / OPEN
29 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO3/EnaOpn/stVal | SPI | BAY_89AE/AE1_ISO OPEN PERMITTED OR ENABLED
30 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO3/EnaCls/stVal | SPI | BAY_89AE/AE1_ISO CLOSE PERMITTED OR ENABLED
31 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI4/Pos/stVal | DPI | BAY_89B_ISOLATOR POSITION
32 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI4/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI4/Pos/ctlOperOn for Close | CMD | BAY_89B_ISO COMMAND |  | CLOSE / OPEN
33 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO4/EnaOpn/stVal | SPI | BAY_89B_ISO OPEN PERMITTED OR ENABLED
34 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO4/EnaCls/stVal | SPI | BAY_89B_ISO CLOSE PERMITTED OR ENABLED
35 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI5/Pos/stVal | DPI | BAY_89BE/BE1_ISOLATOR POSITION
36 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI5/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI5/Pos/ctlOperOn for Close | CMD | BAY_89BE/BE1_ISO COMMAND |  | CLOSE / OPEN
37 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO5/EnaOpn/stVal | SPI | BAY_89BE/BE1_ISO OPEN PERMITTED OR ENABLED
38 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO5/EnaCls/stVal | SPI | BAY_89BE/BE1_ISO CLOSE PERMITTED OR ENABLED
39 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI6/Pos/stVal | DPI | BAY_89L/T/BR_ISOLATOR POSITION |  |  | FOR 3 PHASE TRANSFORMERS & REACTORS CSWI6 MAY BE USED FOR 89T/BR, BUT FOR SINGLE PHASE TRANSFORMERS & REACTORS SAME HAS BEEN SEPARATELY MENTIONED
40 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI6/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI6/Pos/ctlOperOn for Close | CMD | BAY_89L/T/BR_ISO COMMAND |  | CLOSE / OPEN
41 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO6/EnaOpn/stVal | SPI | BAY_89L/T/BR_ISO OPEN PERMITTED OR ENABLED
42 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO6/EnaCls/stVal | SPI | BAY_89L/T/BR_ISO CLOSE PERMITTED OR ENABLED
43 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI7/Pos/stVal | DPI | BAY_89LE/TE/BRE_ISOLATOR POSITION |  |  | FOR 3 PHASE TRANSFORMERS & REACTORS CSWI7 MAY BE USED FOR 89TE/BRE, BUT FOR SINGLE PHASE PHASE TRANSFORMERS & REACTORS SAME HAS BEEN SEPARATELY MENTIONED
44 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI7/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI7/Pos/ctlOperOn for Close | CMD | BAY_89LE/TE/BRE_ISO COMMAND |  | CLOSE / OPEN
45 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO7/EnaOpn/stVal | SPI | BAY_89LE/TE/BRE_ISO OPEN PERMITTED OR ENABLED
46 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO7/EnaCls/stVal | SPI | BAY_89LE/TE/BRE_ISO CLOSE PERMITTED OR ENABLED
47 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI8/Pos/stVal | DPI | BAY_89LR/89C_ISOLATOR POSITION |  |  | FOR 3 PHASE LINE REACTORS CSWI8 MAY BE USED FOR 89LR, BUT FOR SINGLE PHASE LINE REACTORS SAME HAS BEEN SEPARATELY MENTIONED
48 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI8/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI8/Pos/ctlOperOn for Close | CMD | BAY_89LR/89C_ISO COMMAND |  | CLOSE / OPEN
49 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO8/EnaOpn/stVal | SPI | BAY_89LR/89C_ISO OPEN PERMITTED OR ENABLED
50 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO8/EnaCls/stVal | SPI | BAY_89LR/89C_ISO CLOSE PERMITTED OR ENABLED
51 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI9/Pos/stVal | DPI | BAY_89LRE_ISOLATOR POSITION |  |  | FOR 3 PHASE LINE REACTORS CSWI9 MAY BE USED FOR 89LRE, BUT FOR SINGLE PHASE LINE REACTORS SAME HAS BEEN SEPARATELY MENTIONED
52 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI9/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI9/Pos/ctlOperOn for Close | CMD | BAY_89LRE_ISO COMMAND |  | CLOSE / OPEN
53 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO9/EnaOpn/stVal | SPI | BAY_89LRE_ISO OPEN PERMITTED OR ENABLED
54 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO9/EnaCls/stVal | SPI | BAY_89LRE_ISO CLOSE PERMITTED OR ENABLED
55 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI10/Pos/stVal | DPI | BAY_89BRS1&2_ISOLATOR POSITION |  |  | FOR 3 PHASE BUS & LINE REACTORS CSWI10 MAY BE USED FOR 89BRS1&2, BUT FOR SINGLE PHASE TRANSFORMERS SAME HAS BEEN SEPARATELY MENTIONED
56 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI10Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI10/Pos/ctlOperOn for Close | CMD | BAY_89BRS1&2_ISO COMMAND |  | CLOSE / OPEN
57 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO10/EnaOpn/stVal | SPI | BAY_89BRS1&2_ISO OPEN PERMITTED OR ENABLED
58 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO10/EnaCls/stVal | SPI | BAY_89BRS1&2_ISO CLOSE PERMITTED OR ENABLED
59 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI11/Pos/stVal | DPI | BAY_89BRS1E_ISOLATOR POSITION |  |  | FOR 3 PHASE TRANSFORMERS & REACTORS CSWI11 MAY BE USED FOR 89BRS1E, BUT FOR SINGLE PHASE TRANSFORMERS SAME HAS BEEN SEPARATELY MENTIONED
60 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI11/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI11/Pos/ctlOperOn for Close | CMD | BAY_89BRS1E_ISO COMMAND |  | CLOSE / OPEN
61 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO11/EnaOpn/stVal | SPI | BAY_89BRS1E_ISO OPEN PERMITTED OR ENABLED
62 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO11/EnaCls/stVal | SPI | BAY_89BRS1E_ISO CLOSE PERMITTED OR ENABLED
63 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI12/Pos/stVal | DPI | BAY_89AE2/BE2_ISOLATOR POSITION |  |  | USED FOR BUS EARTH SWITCH OF ISOLATOR, WHEN BUS EARTH SWITCH (89AE2/BE2) IS PROVIDED
64 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI12/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI12/Pos/ctlOperOn for Close | CMD | BAY_89AE2/BE2_ISO COMMAND |  | CLOSE / OPEN
65 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO12/EnaOpn/stVal | SPI | BAY_89AE2/BE2_ISO OPEN PERMITTED OR ENABLED
66 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO12/EnaCls/stVal | SPI | BAY_89AE2/BE2_ISO CLOSE PERMITTED OR ENABLED
THE LOGICAL NODE INSTANCE NUMBER (SCSWIn/SCILOn) FOR BUS EARTH SWITCHES, ISOLATOR & EARTHSWITCHES FOR 3 PH/1PH REACTORS & ITCs, e.g 89 BR, BRE, LR, LRE, RS1, RS2, RS1E, 89T,TE, 89AE2, 89BE2 MAY BE ASSIGNED AS PER AVAILABILITY
67 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
68 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/LPHD1/PhyHealth/stVal | SPI | BCU UNHEALTHY | Y
69 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/SES_1/SESRSYN2/Rel/stVal | SPI | CONDITIONS OK FOR SYNCHRONIZATION
70 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI |  |  |  | APPLICABLE FOR ONE AND HALF CIRCUIT BREAKER
71 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | SPRING DISCHARGED | Y | FOR SPRING MECHANISM CBs | ANNUNCIATION FOR CIRCUIT BREAKER
72 | 400kV | STNMC1Q01BNMBCU |  | SPI | AC MOTOR SUPPLY FAIL | Y
73 | 400kV | STNMC1Q01BNMBCU |  | SPI | SF6 GAS LOW | Y
74 | 400kV | STNMC1Q01BNMBCU |  | SPI | OPERATION LOCKED OUT | Y
75 | 400kV | STNMC1Q01BNMBCU |  | SPI | CB READY FOR AUTORECLOSURE | Y
76 | 400kV | STNMC1Q01BNMBCU |  | SPI | DC SUPPLY FAIL | Y
77 | 400kV | STNMC1Q01BNMBCU |  | SPI | TC-1 FAIL | Y
78 | 400kV | STNMC1Q01BNMBCU |  | SPI | TC-2 FAIL | Y
79 | 400kV | STNMC1Q01BNMBCU |  | SPI | TRIP RELAY 86 A FAULTY (SUPERVISION) | Y |  |  | Addition
80 | 400kV | STNMC1Q01BNMBCU |  | SPI | TRIP RELAY 86 B FAULTY (SUPERVISION) | Y |  |  | Addition
81 | 400kV | STNMC1Q01BNMBCU |  | SPI | TC-1 FAULTY R-PH | Y |  |  | Addition
82 | 400kV | STNMC1Q01BNMBCU |  | SPI | TC-1 FAULTY Y-PH | Y |  |  | Addition
83 | 400kV | STNMC1Q01BNMBCU |  | SPI | TC-1 FAULTY B-PH | Y |  |  | Addition
84 | 400kV | STNMC1Q01BNMBCU |  | SPI | TC-2 FAULTY R-PH | Y |  |  | Addition
85 | 400kV | STNMC1Q01BNMBCU |  | SPI | TC-2 FAULTY Y-PH | Y |  |  | Addition
86 | 400kV | STNMC1Q01BNMBCU |  | SPI | TC-2 FAULTY B-PH | Y |  |  | Addition
87 | 400kV | STNMC1Q01BNMBCU |  | SPI | DT RECEIVE CH-1 | Y |  |  | Available in REC670 (Sig. 5) | Agreed
88 | 400kV | STNMC1Q01BNMBCU |  | SPI | DT RECEIVE CH-2 | Y |  |  | Available in REC670 (Sig. 6) | Agreed
89 | 400kV | STNMC1Q01BNMBCU |  | SPI | CB MANUAL TRIP CMD | Y |  |  | Addition
90 | 400kV | STNMC1Q01BNMBCU |  | SPI | CB MANUAL CLOSE CMD | Y |  |  | Addition
91 | 400kV | STNMC1Q01BNMBCU |  | SPI | START A/R | Y |  |  | Addition
92 | 400kV | STNMC1Q01BNMBCU |  | SPI | BLOCK A/R | Y |  |  | Addition
93 | 400kV | STNMC1Q01BNMBCU |  | SPI | PREPARE 3PH TRIP | Y |  |  | Addition, Available in REC670 (Sig. 11) | Agreed
94 | 400kV | STNMC1Q01BNMBCU |  | SPI | BUSBAR PROTN OPTD | Y |  |  | Addition
95 | 400kV | STNMC1Q01BNMBCU |  | SPI | S.A. COUNTER R-PH | Y |  |  | Addition | As per CRP scheme will be configured in BCU/Protection relay
96 | 400kV | STNMC1Q01BNMBCU |  | SPI | S.A. COUNTER Y-PH | Y |  |  | Addition | As per CRP scheme will be configured in BCU/Protection relay
97 | 400kV | STNMC1Q01BNMBCU |  | SPI | S.A. COUNTER B-PH | Y |  |  | Addition | As per CRP scheme will be configured in BCU/Protection relay
98 | 400kV | STNMC1Q01BNMBCU |  | SPI | INCOMER DC-1 FAIL | Y |  |  | Addition
99 | 400kV | STNMC1Q01BNMBCU |  | SPI | INCOMER DC-2 FAIL | Y |  |  | Addition
100 | 400kV | STNMC1Q01BNMBCU |  | SPI | POLE DISCREPANCY RELAY OPTD | Y
101 | 400kV | STNMC1Q01BNMBCU |  | SPI | COMPRESSOR SUPPLY FAIL | Y | FOR HYDRAULLIC MECHANISM CBs
102 | 400kV | STNMC1Q01BNMBCU |  | SPI | AIR PRESSURE LOW | Y
103 | 400kV | STNMC1Q01BNMBCU |  | SPI | COMPRESSOR RUN TIME SUPERVISION | Y
104 | 400kV | STNMC1Q01BNMBCU |  | SPI | CB R-PH RECLOSE ALARM | Y |  |  | Addition
105 | 400kV | STNMC1Q01BNMBCU |  | SPI | CB Y-PH RECLOSE ALARM | Y |  |  | Addition
106 | 400kV | STNMC1Q01BNMBCU |  | SPI | CB B-PH RECLOSE ALARM | Y |  |  | Addition
107 | 400kV | STNMC1Q01BNMBCU |  | SPI | CSD OPERATION LIMIT ALARM WHEN OPENING | Y |  |  | Addition
108 | 400kV | STNMC1Q01BNMBCU |  | SPI | CSD OPERATION LIMIT ALARM WHEN CLOSING | Y |  |  | Addition
109 | 400kV | STNMC1Q01BNMBCU |  | SPI | CSD GROUP ALARM | Y |  |  | Addition
110 | 400kV | STNMC1Q01BNMBCU |  | SPI | CSD RESERVED | Y |  |  | Addition
111 | 400kV | STNMC1Q01BNMBCU |  | SPI | CSD SYNCHROTEQ IN LOCAL MODE | Y |  |  | Addition
112 | 400kV | STNMC1Q01BNMBCU |  | SPI | CSD CB INTERFACE ALARM | Y |  |  | Addition
113 | 400kV | STNMC1Q01BNMBCU |  | SPI | CSD SENSOR ALARM | Y |  |  | Addition
114 | 400kV | STNMC1Q01BNMBCU |  | SPI | CSD IN | Y |  |  | Addition
115 | 400kV | STNMC1Q01BNMBCU |  | SPI | CSD BYPASS | Y |  |  | Addition
116 | 400kV | STNMC1Q01BNMBCU |  | SPI | CSD FAIL | Y
117 | 400kV | STNMC1Q01BNMBCU |  | SPI | ICT/REACTOR-n R PH OUT OF SERVICE |  | Single phase ICT/Reactor OUT of service & Spare reactor out of service information |  | Addition
118 | 400kV | STNMC1Q01BNMBCU |  | SPI | ICT/REACTOR-n Y PH OUT OF SERVICE |  |  |  | Addition
119 | 400kV | STNMC1Q01BNMBCU |  | SPI | ICT/REACTOR-n B PH OUT OF SERVICE | Y |  |  | Addition
120 | 400kV | STNMC1Q01BNMBCU |  | SPI | ICT/REACTOR SPARE PH IN SERVICE IN ICT/REACTOR-N | Y |  |  | Addition
121 | 765kV | STNMB1Q01BNMBCU |  | SPI | BUS-1 VT RESET |  | VT SELECTION FOR TRANSFORMER & REACTOR
122 | 765kV | STNMB1Q01BNMBCU |  | SPI | BUS-2 VT RESET
123 | 765kV | STNMB1Q01BNMBCU |  | SPI | LINE VT RESET
124 | 765kV | STNMB1Q01BNMBCU |  | SPI | BUS-1 VT SELECTED
125 | 765kV | STNMB1Q01BNMBCU |  | SPI | BUS-2 VT SELECTED
126 | 765kV | STNMB1Q01BNMBCU |  | SPI | LINE VTSELECTED
127 | 400kV | STNMC1Q01BNMBCU |  | SPI | GAS COMPARTMENT n Alarm Stage n | Y | Stage 1 to n as per scheme | ANNUNCIATION FOR GIS BAYS
128 | 400kV | STNMC1Q01BNMBCU |  | SPI | LCC PANEL AC SUPPLY FAIL | Y
129 | 400kV | STNMC1Q01BNMBCU |  | SPI | LCC PANEL DC SUPPLY FAIL | Y
130 | 400kV | STNMC1Q01BNMBCU |  | SPI | SELECTOR SWITCH POSITION LOCAL/REMOTE | Y
131 | 400kV | STNMC1Q01BNMBCU |  | SPI | BUS VT MCB TRIP | Y |  | FOR BCUs HAVING BUS VT INPUT
132 | 400kV | STNMC1Q01BNMBCU |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
133 | 400kV | STNMC1Q01BNMBCU |  | SPI | RELAY IN TEST MODE | Y |  |  | Addition
134 | 400kV | STNMC1Q01BNMBCU |  | SPI | SETTINGS CHANGED | Y |  |  | Addition
135 | 400kV | STNMC1Q01BNMBCU |  | SPI | DR MEMMORY 80% FULL | Y |  |  | Addition
136 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/MON/CMMXU1/A/phsA/cVal/mag | AI | CURRENT L1 |  |  |  | Addition
137 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/MON/CMMXU1/A/phsB/cVal/mag | AI | CURRENT L2 |  |  |  | Addition
138 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/MON/CMMXU1/A/phsC/cVal/mag | AI | CURRENT L3 |  |  |  | Addition
139 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/MON/VMMXU1/PPV/phsAB/cVal/mag | AI | VOLTAGE U12 |  |  |  | Addition
140 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/MON/VMMXU1/PPV/phsBC/cVal/mag | AI | VOLTAGE U23 |  |  |  | Addition
141 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/MON/VMMXU1/PPV/phsCA/cVal/mag | AI | VOLTAGE U31 |  |  |  | Addition
142 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/MON/CVMMXN1/Watt/mag | AI | ACTIVE POWER (P) |  |  |  | Addition
143 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/MON/CVMMXN1/VolAmpr/mag | AI | REACTIVE POWER (Q) |  |  |  | Addition
144 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/MON/CVMMXN1/PwrFact/mag | AI | POWER FACTOR (PF) |  |  |  | Addition
145 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/MON/CVMMXN1/PwrFact/mag | AI | FREQUENCY (HZ) |  |  |  | Addition
146 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCUMON/L4UFCNTn/CntVal/actVal | AI | S.A. COUNTER R-PH |  |  |  | Available in REC670 (Sig. 95) | Agreed
147 | 400kV | STNMC1Q01BNMBCU |  | AI | S.A. COUNTER Y-PH |  |  |  | Available in REC670 (Sig. 95) | Agreed
148 | 400kV | STNMC1Q01BNMBCU |  | AI | S.A. COUNTER B-PH |  |  |  | Available in REC670 (Sig. 95) | Agreed
149 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/MON/MVGAPC/AnIn_n/mag | AI | TAP POSITION R PH |  |  |  | Addition
150 | 400kV | STNMC1Q01BNMBCU |  | AI | TAP POSITION Y PH |  |  |  | Addition
151 | 400kV | STNMC1Q01BNMBCU |  | AI | TAP POSITION B PH |  |  |  | Addition
152 | 400kV | STNMC1Q01BNMBCU |  | AI | WTI HV R PH |  |  |  | Addition
153 | 400kV | STNMC1Q01BNMBCU |  | AI | WTI IV R PH |  |  |  | Addition
154 | 400kV | STNMC1Q01BNMBCU |  | AI | WTI LV R PH |  |  |  | Addition
155 | 400kV | STNMC1Q01BNMBCU |  | AI | OTI R PH |  |  |  | Addition
156 | 400kV | STNMC1Q01BNMBCU |  | AI | WTI HV Y PH |  |  |  | Addition
157 | 400kV | STNMC1Q01BNMBCU |  | AI | WTI IV Y PH |  |  |  | Addition
158 | 400kV | STNMC1Q01BNMBCU |  | AI | WTI LV Y PH |  |  |  | Addition
159 | 400kV | STNMC1Q01BNMBCU |  | AI | OTI Y PH |  |  |  | Addition
160 | 400kV | STNMC1Q01BNMBCU |  | AI | WTI HV B PH |  |  |  | Addition
161 | 400kV | STNMC1Q01BNMBCU |  | AI | WTI IV B PH |  |  |  | Addition
162 | 400kV | STNMC1Q01BNMBCU |  | AI | WTI LV B PH |  |  |  | Addition
163 | 400kV | STNMC1Q01BNMBCU |  | AI | OTI B PH |  |  |  | Addition
164 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCUMON/L4UFCNTn/CntVal/actVal | AI | BREAKER R-PHASE OPERATION COUNTER |  |  |  | Addition
165 | 400kV | STNMC1Q01BNMBCU |  | AI | BREAKER Y-PHASE OPERATION COUNTER |  |  |  | Addition
166 | 400kV | STNMC1Q01BNMBCU |  | AI | BREAKER B-PHASE OPERATION COUNTER |  |  |  | Addition
167 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | RPH MOG LOW OIL LEVEL ALARM | Y |  | FOR 3Phase TRANSFORMER, INPUTS CAN BE DISTRIBUTED TO ANY IED. BUTSIGNAL SHOULD BE AS PER TRANSFORMER AVIALABLE SIGNAL | Addition
168 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH MOG LOW OIL LEVEL ALARM | Y |  |  | Addition
169 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH MOG LOW OIL LEVEL ALARM | Y |  |  | Addition
170 | 400kV | STNMC1Q01BNMBCU |  | SPI | SP-PH MOG LOW OIL LEVEL ALARM | Y |  |  | Addition
171 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH MOG HIGH OIL LEVEL ALARM | Y |  |  | Addition
172 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH MOG HIGH OIL LEVEL ALARM | Y |  |  | Addition
173 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH MOG HIGH OIL LEVEL ALARM | Y |  |  | Addition
174 | 400kV | STNMC1Q01BNMBCU |  | SPI | SP-PH MOG HIGH OIL LEVEL ALARM | Y |  |  | Addition
175 | 400kV | STNMC1Q01BNMBCU |  | SPI | R-PH OIL FLOW SENSITIVE VALVE ALARM | Y |  |  | Addition
176 | 400kV | STNMC1Q01BNMBCU |  | SPI | Y-PH OIL FLOW SENSITIVE VALVE ALARM | Y |  |  | Addition
177 | 400kV | STNMC1Q01BNMBCU |  | SPI | B-PH OIL FLOW SENSITIVE VALVE ALARM | Y |  |  | Addition
178 | 400kV | STNMC1Q01BNMBCU |  | SPI | SP-PH OIL FLOW SENSITIVE VALVE ALARM | Y |  |  | Addition
179 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH PUMP FAIL - BANK A | Y |  |  | Addition
180 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH PUMP FAIL - BANK B | Y |  |  | Addition
181 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH PUMP FAIL - BANK C | Y |  |  | Addition
182 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH PUMP FAIL - BANK D | Y |  |  | Addition
183 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH PUMP FAIL - BANK A | Y |  |  | Addition
184 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH PUMP FAIL - BANK B | Y |  |  | Addition
185 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH PUMP FAIL - BANK C | Y |  |  | Addition
186 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH PUMP FAIL - BANK D | Y |  |  | Addition
187 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH PUMP FAIL - BANK A | Y |  |  | Addition
188 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH PUMP FAIL - BANK B | Y |  |  | Addition
189 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH PUMP FAIL - BANK C | Y |  |  | Addition
190 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH PUMP FAIL - BANK D | Y |  |  | Addition
191 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH PUMP FAIL - BANK A | Y |  |  | Addition
192 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH PUMP FAIL - BANK B | Y |  |  | Addition
193 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH PUMP FAIL - BANK C | Y |  |  | Addition
194 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH PUMP FAIL - BANK D | Y |  |  | Addition
195 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH THERMAL OVERLOAD TRIP - BANK A | Y |  |  | Addition
196 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH THERMAL OVERLOAD TRIP - BANK B | Y |  |  | Addition
197 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH THERMAL OVERLOAD TRIP - BANK C | Y |  |  | Addition
198 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH THERMAL OVERLOAD TRIP - BANK D | Y |  |  | Addition
199 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH THERMAL OVERLOAD TRIP - BANK A | Y |  |  | Addition
200 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH THERMAL OVERLOAD TRIP - BANK B | Y |  |  | Addition
201 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH THERMAL OVERLOAD TRIP - BANK C | Y |  |  | Addition
202 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH THERMAL OVERLOAD TRIP - BANK D | Y |  |  | Addition
203 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH THERMAL OVERLOAD TRIP - BANK A | Y |  |  | Addition
204 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH THERMAL OVERLOAD TRIP - BANK B | Y |  |  | Addition
205 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH THERMAL OVERLOAD TRIP - BANK C | Y |  |  | Addition
206 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH THERMAL OVERLOAD TRIP - BANK D | Y |  |  | Addition
207 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH THERMAL OVERLOAD TRIP - BANK A | Y |  |  | Addition
208 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH THERMAL OVERLOAD TRIP - BANK B | Y |  |  | Addition
209 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH THERMAL OVERLOAD TRIP - BANK C | Y |  |  | Addition
210 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH THERMAL OVERLOAD TRIP - BANK D | Y |  |  | Addition
211 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH LOW OIL FLOW/REVERSE FLOW - BANK A | Y |  |  | Addition
212 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH LOW OIL FLOW/REVERSE FLOW - BANK B | Y |  |  | Addition
213 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH LOW OIL FLOW/REVERSE FLOW - BANK C | Y |  |  | Addition
214 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH LOW OIL FLOW/REVERSE FLOW - BANK D | Y |  |  | Addition
215 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH LOW OIL FLOW/REVERSE FLOW - BANK A | Y |  |  | Addition
216 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH LOW OIL FLOW/REVERSE FLOW - BANK B | Y |  |  | Addition
217 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH LOW OIL FLOW/REVERSE FLOW - BANK C | Y |  |  | Addition
218 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH LOW OIL FLOW/REVERSE FLOW - BANK D | Y |  |  | Addition
219 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH LOW OIL FLOW/REVERSE FLOW - BANK A | Y |  |  | Addition
220 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH LOW OIL FLOW/REVERSE FLOW - BANK B | Y |  |  | Addition
221 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH LOW OIL FLOW/REVERSE FLOW - BANK C | Y |  |  | Addition
222 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH LOW OIL FLOW/REVERSE FLOW - BANK D | Y |  |  | Addition
223 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH LOW OIL FLOW/REVERSE FLOW - BANK A | Y |  |  | Addition
224 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH LOW OIL FLOW/REVERSE FLOW - BANK B | Y |  |  | Addition
225 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH LOW OIL FLOW/REVERSE FLOW - BANK C | Y |  |  | Addition
226 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH LOW OIL FLOW/REVERSE FLOW - BANK D | Y |  |  | Addition
227 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH COOLER CONTROL SUPPLY FAIL | Y |  |  | Addition
228 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH COOLER CONTROL SUPPLY FAIL | Y |  |  | Addition
229 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH COOLER CONTROL SUPPLY FAIL | Y |  |  | Addition
230 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH COOLER CONTROL SUPPLY FAIL | Y |  |  | Addition
231 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH SUPPLY CHANGE OVER FAIL | Y |  |  | Addition
232 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH SUPPLY CHANGE OVER FAIL | Y |  |  | Addition
233 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH SUPPLY CHANGE OVER FAIL | Y |  |  | Addition
234 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH SUPPLY CHANGE OVER FAIL | Y |  |  | Addition
235 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH SUPPLY - A FAIL | Y |  |  | Addition
236 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH SUPPLY - A FAIL | Y |  |  | Addition
237 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH SUPPLY - A FAIL | Y |  |  | Addition
238 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH SUPPLY - A FAIL | Y |  |  | Addition
239 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH SUPPLY - B FAIL | Y |  |  | Addition
240 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH SUPPLY - B FAIL | Y |  |  | Addition
241 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH SUPPLY - B FAIL | Y |  |  | Addition
242 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH SUPPLY - B FAIL | Y |  |  | Addition
243 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH OLTC MOTOR OVERLOAD | Y |  |  | Addition
244 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH TAP CHANGE IN PROGRESS | Y |  |  | Addition
245 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH TAP CHANGE IN COMPLETE | Y |  |  | Addition
246 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH OLTC IN LOCAL | Y |  |  | Addition
247 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH OLTC IN REMOTE | Y |  |  | Addition
248 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH TAP CHANGE CONTROL SUPPLY FAIL | Y |  |  | Addition
249 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH LOWEST POSITION REACHDED | Y |  |  | Addition
250 | 400kV | STNMC1Q01BNMBCU |  | SPI | RPH HIGHESHT POSITION REACHDED | Y |  |  | Addition
251 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SPC1CGGIO n/ctlOpen | CMD | RPH OLTC RAISE COMMAND | Y |  |  | Addition
252 | 400kV | STNMC1Q01BNMBCU |  | CMD | RPH OLTC LOWER COMMAND | Y |  |  | Addition
253 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | YPH OLTC MOTOR OVERLOAD | Y |  |  | Addition
254 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH TAP CHANGE IN PROGRESS | Y |  |  | Addition
255 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH TAP CHANGE IN COMPLETE | Y |  |  | Addition
256 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH OLTC IN LOCAL | Y |  |  | Addition
257 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH OLTC IN REMOTE | Y |  |  | Addition
258 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH TAP CHANGE CONTROL SUPPLY FAIL | Y |  |  | Addition
259 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH LOWEST POSITION REACHDED | Y |  |  | Addition
260 | 400kV | STNMC1Q01BNMBCU |  | SPI | YPH HIGHESHT POSITION REACHDED | Y |  |  | Addition
261 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SPC1CGGIO n/ctlOpen | CMD | YPH OLTC RAISE COMMAND | Y |  |  | Addition
262 | 400kV | STNMC1Q01BNMBCU |  | CMD | YPH OLTC LOWER COMMAND | Y |  |  | Addition
263 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | BPH OLTC MOTOR OVERLOAD | Y |  |  | Addition
264 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH TAP CHANGE IN PROGRESS | Y |  |  | Addition
265 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH TAP CHANGE IN COMPLETE | Y |  |  | Addition
266 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH OLTC IN LOCAL | Y |  |  | Addition
267 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH OLTC IN REMOTE | Y |  |  | Addition
268 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH TAP CHANGE CONTROL SUPPLY FAIL | Y |  |  | Addition
269 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH LOWEST POSITION REACHDED | Y |  |  | Addition
270 | 400kV | STNMC1Q01BNMBCU |  | SPI | BPH HIGHESHT POSITION REACHDED | Y |  |  | Addition
271 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SPC1CGGIO n/ctlOpen | CMD | BPH OLTC RAISE COMMAND | Y |  |  | Addition
272 | 400kV | STNMC1Q01BNMBCU |  | CMD | BPH OLTC LOWER COMMAND | Y |  |  | Addition
273 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | SPH OLTC MOTOR OVERLOAD | Y |  |  | Addition
274 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH TAP CHANGE IN PROGRESS | Y |  |  | Addition
275 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH TAP CHANGE IN COMPLETE | Y |  |  | Addition
276 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH OLTC IN LOCAL | Y |  |  | Addition
277 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH OLTC IN REMOTE | Y |  |  | Addition
278 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH TAP CHANGE CONTROL SUPPLY FAIL | Y |  |  | Addition
279 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH LOWEST POSITION REACHDED | Y |  |  | Addition
280 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPH HIGHESHT POSITION REACHDED | Y |  |  | Addition
281 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SPC1CGGIO n/ctlOpen | CMD | SPH OLTC RAISE COMMAND | Y |  |  | Addition
282 | 400kV | STNMC1Q01BNMBCU |  | CMD | SPH OLTC LOWER COMMAND | Y |  |  | Addition
283 | 400kV | STNMC1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database |  | Addition
284 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPARE ALARM-2 | Y |  |  | Addition
285 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPARE ALARM-3 | Y |  |  | Addition
286 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPARE ALARM-4 | Y |  |  | Addition
287 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPARE ALARM-5 | Y |  |  | Addition
288 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPARE ALARM-6 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database |  | Addition
289 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPARE ALARM-7 | Y |  |  | Addition
290 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPARE ALARM-8 | Y |  |  | Addition
291 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPARE ALARM-9 | Y |  |  | Addition
292 | 400kV | STNMC1Q01BNMBCU |  | SPI | SPARE ALARM-10 | Y |  |  | Addition
ADDITIONAL SIGNAL FOR CB TROUBLE ETC AS PER SCHEME
** 10 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
NOTE 1: The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified.
NOTE 2: If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.
NOTE 3: The characters "STNM" stand for Substation Name with maximum 4 characters, this code will be given by POWERGRID for each project.
NOTE 4: The characters "Q01" stand for Bay Number, this will be vary based on Bay number eg. Q01 for BAY01, Q02 for BAY02 etc…
NOTE 5: The characters "BNM" stand for Bay Name, this will be vary based on Bay name eg. L for LINE, BR for BUSREACTOR, LR for LINEREACTOR, TIE for TIE & ICT fo ICT bay.
REQUIRED SIGNALS FOR LINE DIFFERENTAIL cum DISTANCE RELAYS
| IED name: | R_REL670_21M1
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/OV2_1/OV2PTOV1/Str/general | SPI | OVERVOLATGE STAGE 1 START
2 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/OV2_1/OV2PTOV1/Op/general | SPI | OVERVOLATGE STAGE 1 TRIP | Y
3 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/OV2PTOV2/Str/general | SPI | OVER VOLTAGE STAGE-2 START | Y |  | Addition
4 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/OV2_1/OV2PTOV2/Op/general | SPI | OVERVOLATGE STAGE 2 TRIP | Y
5 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/EF4_1/EF4PTOC1/Str/general | SPI | DEF START
6 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/EF4_1/EF4PTOC1/Op/general | SPI | DEF TRIP | Y
7 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/STBPTOC1/Op/general | SPI | STUB PROTECTION OPERATED | Y | Applicable for One and Half CB Busbar system
8 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCVPSOF1/Op/general | SPI | SOTF OPERATED | Y
9 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Str/general | SPI | START, Z1
10 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/general | SPI | START, Z2
11 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsA | SPI | START, Z2 R PH
12 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsB | SPI | START, Z2 Y PH
13 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsC | SPI | START, Z2 B PH
14 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS3/Str/general | SPI | START, Z3
15 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS4/Str/general | SPI | START, Z4(REVERSE) |  | ** Whichever the zone choses as Reverse | Text correction
16 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS5/Str/general | SPI | START, Z5
17 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/general | SPI | GENERAL TRIP, Z1 | Y
18 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsA | SPI | TRIP, Z1 R PH | Y
19 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsB | SPI | TRIP, Z1 Y PH | Y
20 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsC | SPI | TRIP, Z1 B PH | Y
21 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/general | SPI | GENERAL TRIP, Z2 | Y
22 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsA | SPI | TRIP, Z2 R PH | Y
23 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsB | SPI | TRIP, Z2 Y PH | Y
24 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsC | SPI | TRIP, Z2 B PH | Y
25 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS3/Op/general | SPI | GENERAL TRIP, Z3 | Y
26 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS4/Op/general | SPI | GENERAL TRIP, Z4(REVERSE) | Y | ** Whichever the zone choses as Reverse | Text correction
27 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS5/Op/general | SPI | GENERAL TRIP, Z5 | Y
28 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/ProTx/stVal | SPI | CARRIER SEND | Y
29 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/ProRx/stVal | SPI | CARRIER RECEIVE | Y
30 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/Op/general | SPI | CARRIER AIDED SCHEME OPERATED | Y
31 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMRPSB1/Str/general | SPI | POWER SWING DETECTED | Y
32 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMRPSB1/BlkZn/stVal | SPI | POWER SWING BLOCKING | Y
33 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SMPPTRC1/Op/general | SPI | DISTANCE RELAY GENERAL TRIP | Y
34 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | R PHASE FAULT | Y |  | Addition
35 | 400kV | STNMC1Q01LM1DIF |  | SPI | Y PHASE FAULT | Y |  | Addition
36 | 400kV | STNMC1Q01LM1DIF |  | SPI | B PHASE FAULT | Y |  | Addition
37 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltDiskm/mag | DINT | FAULT LOCATOR DISTANCE
38 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltZ/cVal.mag | DINT | FAULT LOCATOR IMPEDANCE
39 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
40 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/BRCPTOC1/Op/general | SPI | BROKEN CONDUCTOR ALARM | Y
41 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
42 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/LPHD1/PhyHealth/stVal | SPI | M1 IED UNHEALTHY | Y
43 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | START AR TO BCU |  |  | Text correction
44 | 400kV | STNMC1Q01LM1DIF |  | SPI | BLOCK AR TO BCU |  |  | Text correction
45 | 400kV | STNMC1Q01LM1DIF |  | SPI | LINE ISOLATOR OPEN FOR STUB ACTIVATION |  | Applicable for One and Half CB Busbar system
46 | 400kV | STNMC1Q01LM1DIF |  | SPI | DT SEND CH 1 | Y
47 | 400kV | STNMC1Q01LM1DIF |  | SPI | DT SEND CH 2 | Y
48 | 400kV | STNMC1Q01LM1DIF |  | SPI | DT RECEIVE CH 1 | Y |  |  | Only for DR in RED670, for SCADA to be configured from BCU
49 | 400kV | STNMC1Q01LM1DIF |  | SPI | DT RECEIVE CH 2 | Y |  |  | Only for DR in RED670, for SCADA to be configured from BCU
50 | 400kV | STNMC1Q01LM1DIF |  | SPI | TRIP RELAY 86 A HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
51 | 400kV | STNMC1Q01LM1DIF |  | SPI | TRIP RELAY 86 B HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
52 | 400kV | STNMC1Q01LM1DIF |  | SPI | GR A RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RED670, for SCADA to be configured from BCU
53 | 400kV | STNMC1Q01LM1DIF |  | SPI | GR B RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RED670, for SCADA to be configured from BCU
54 | 400kV | STNMC1Q01LM1DIF |  | SPI | CARRIER RECEIVE CH-1 | Y
55 | 400kV | STNMC1Q01LM1DIF |  | SPI | CARRIER RECEIVE CH-2 | Y
56 | 400kV | STNMC1Q01LM1DIF |  | SPI | CARRIER CHANNEL 1 OUT OF SERVICE | Y
57 | 400kV | STNMC1Q01LM1DIF |  | SPI | CARRIER CHANNEL 2 OUT OF SERVICE | Y
58 | 400kV | STNMC1Q01LM1DIF |  | SPI | CARRIER CHANNEL 1 FAIL | Y
59 | 400kV | STNMC1Q01LM1DIF |  | SPI | CARRIER CHANNEL 2 FAIL | Y
60 | 400kV | STNMC1Q01LM1DIF |  | SPI | MAIN 2/1 RELAY FAIL | Y
61 | 400kV | STNMC1Q01LM1DIF |  | SPI | CB CLOSE COMMAND FOR SOTF INITIATION |  |  | Text correction
62 | 400kV | STNMC1Q01LM1DIF |  | SPI | BCU RELAY FAIL | Y
63 | 400kV | STNMC1Q01LM1DIF |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
64 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsA | SPI | START, Z1 R PH |  |  | Addition
65 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsB | SPI | START, Z1 Y PH |  |  | Addition
66 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsC | SPI | START, Z1 B PH |  |  | Addition
67 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP 3PH | Y |  | Addition
68 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP R PH | Y |  | Addition
69 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP Y PH | Y |  | Addition
70 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP B PH | Y |  | Addition
71 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | PREPARE 3-PH TRIP FROM TIE BCU | Y |  | Addition, Available in BCU | It is also required in RED670
72 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | PREPARE 3-PH TRIP FROM MAIN BCU | Y |  | Addition, Available in BCU | It is also required in RED670
73 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | MAIN/ TIE CB AR OPTD | Y |  | Addition, Available in BCU | Only for DR in RED670, for SCADA to be configured from BCU
74 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | MAIN/TIE LBB PROTECTION OPERATED | Y |  | Addition, Available in BBP | Only for DR in RED670, for SCADA to be configured from LBB/BBP relay
75 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | BUSBAR M1/M2 OPTD | Y |  | Addition, Available in BBP | Only for DR in RED670, for SCADA to be configured from BBP relay
76 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | GROUP RELAY 86A OPTD | Y |  | Available in REL670 (Sig. 52) | Agreed
77 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/EchoWei/stVal | SPI | WEAK INFEED ECHO SEND | Y |  | Addition
78 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/EchoWeiOp/stVal | SPI | WEAK INFEED TRIP | Y |  | Addition
79 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/RvABlk/stVal | SPI | CURRENT REVERSAL DETECTED | Y |  | Addition
80 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
81 | 400kV | STNMC1Q01LM1DIF |  | SPI | SETTINGS CHANGED | Y |  | Addition
82 | 400kV | STNMC1Q01LM1DIF |  | SPI | DR MEMMORY 80% FULL | Y |  | Addition
83 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltDiskm/mag | AI | DISTANCE MEASUREMENT IN KM | Y |  | Available in REL670 (Sig. 37) | Agreed
84 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltZ/cVal/mag | AI | DISTANCE MEASUREMENT IN IMPEDANCE | Y |  | Available in REL670 (Sig. 38) | Agreed
85 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/MON/L4UFCNTn/CntVal/actVal | AI | CH-1 Code-1 Tx (MAIN-1 CARRIER RECEIVE CHANNEL-1) |  |  | CH-1 Code-1 Tx (MAIN-1 CARRIER SEND CHANNEL-1)
86 | 400kV | STNMC1Q01LM1DIF |  | AI | CH-1 Code-1 Rx (MAIN-1 CARRIER SEND CHANNEL-1) |  |  | CH-1 Code-1 Rx (MAIN-1 CARRIER RECEIVE CHANNEL-1)
87 | 400kV | STNMC1Q01LM1DIF |  | AI | CH-1 Code-2 Tx (MAIN-2 CARRIER RECEIVE CHANNEL-1) |  |  | CH-1 Code-2 Tx (MAIN-2 CARRIER SEND CHANNEL-1)
88 | 400kV | STNMC1Q01LM1DIF |  | AI | CH-1 Code-2 Rx (MAIN-2 CARRIER SEND CHANNEL-1) |  |  | CH-1 Code-2 Rx (MAIN-2 CARRIER RECEIVE CHANNEL-1)
89 | 400kV | STNMC1Q01LM1DIF |  | AI | CH-2 Code-2 Tx (MAIN-2 CARRIER RECEIVE CHANNEL-2) |  |  | CH-2 Code-2 Tx (MAIN-2 CARRIER SEND CHANNEL-2)
90 | 400kV | STNMC1Q01LM1DIF |  | AI | CH-2 Code-2 Rx (MAIN-2 CARRIER SEND CHANNEL-2) |  |  | CH-2 Code-2 Rx (MAIN-2 CARRIER RECEIVECHANNEL-2)
91 | 400kV | STNMC1Q01LM1DIF |  | AI | CH-2 Code-1 Tx (MAIN-1 CARRIER RECEIVE CHANNEL-2) |  |  | CH-2 Code-1 Tx (MAIN-1 CARRIER SEND CHANNEL-2)
92 | 400kV | STNMC1Q01LM1DIF |  | AI | CH-2 Code-1 Rx (MAIN-1 CARRIER SEND CHANNEL-2) |  |  | CH-2 Code-1 Rx (MAIN-1 CARRIER RECEIVE CHANNEL-2)
93 | 400kV | STNMC1Q01LM1DIF |  | AI | CH-1 Code-3 Tx (DT RECEIVE CHANNEL-1) |  |  | CH-1 Code-3 Tx (DT SEND CHANNEL-1)
94 | 400kV | STNMC1Q01LM1DIF |  | AI | CH-1 Code-3 Rx (DT SEND CHANNEL-1) |  |  | CH-1 Code-3 Rx (DT RECEIVE CHANNEL-1)
95 | 400kV | STNMC1Q01LM1DIF |  | AI | CH-2 Code-3 Tx (DT RECEIVE CHANNEL-2) |  |  | CH-2 Code-3 Tx (DT SEND CHANNEL-2)
96 | 400kV | STNMC1Q01LM1DIF |  | AI | CH-2 Code-3 Rx (DT SEND CHANNEL-2) |  |  | CH-2 Code-3 Rx (DT RECEIVE CHANNEL-2)
97 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
98 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-2 | Y |  | Addition
99 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-3 | Y |  | Addition
100 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-4 | Y |  | Addition
101 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-5 | Y |  | Addition
102 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Op/general | SPI | DIFFERENTIAL PROTECTION TRIP | Y | Line Differential protection, 3 CT sets, 2-3 line ends Variant
103 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Op/general | SPI |  | Y | Line Differential protection, 6 CT sets, 3-5 line ends Variant
104 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Op/phsA | SPI | DIFFERENTIAL PROTECTION RPH TRIP | Y | Line Differential protection, 3 CT sets, 2-3 line ends Variant
105 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Op/phsA | SPI |  | Y | Line Differential protection, 6 CT sets, 3-5 line ends Variant
106 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Op/phsB | SPI | DIFFERENTIAL PROTECTION YPH TRIP | Y | Line Differential protection, 3 CT sets, 2-3 line ends Variant
107 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Op/phsB | SPI |  | Y | Line Differential protection, 6 CT sets, 3-5 line ends Variant
108 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Op/phsC | SPI | DIFFERENTIAL PROTECTION BPH TRIP | Y | Line Differential protection, 3 CT sets, 2-3 line ends Variant
109 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Op/phsC | SPI |  | Y | Line Differential protection, 6 CT sets, 3-5 line ends Variant
110 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Str/general | SPI | DIFFERENTIAL PROTECTION START |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
111 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Str/general | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
112 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Str/phsA | SPI | DIFFERENTIAL PROTECTION RPH START |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
113 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Str/phsA | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
114 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Str/phsB | SPI | DIFFERENTIAL PROTECTION YPH START |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
115 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Str/phsB | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
116 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Str/phsC | SPI | DIFFERENTIAL PROTECTION BPH START |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
117 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Str/phsC | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
102 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/OpnCTAlm/stVal | SPI | DIFFERENTIAL PROTECTION OCT ALARM |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
103 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/OpnCTAlm/stVal | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
104 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/StrRst/stVal | SPI | DIFFERENTIAL PROTECTION OPTD (RESTRAINED MODE) |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
105 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/StrRst/stVal | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
106 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/StrUnRst/stVal | SPI | DIFFERENTIAL PROTECTION OPTD (UNRESTRAINED MODE) |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
107 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/StrUnRst/stVal | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
108 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Blk2H/stVal | SPI | DIFFERENTIAL PROTECTION 2nd HARMONIC BLOCK |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant | Applicable for Line cum Transformer bay
109 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Blk2H/stVal | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
110 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Blk5H/stVal | SPI | DIFFERENTIAL PROTECTION 5th HARMONIC BLOCK |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant | Applicable for Line cum Transformer bay
111 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Blk5H/stVal | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
112 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION COMMUNICATION FAIL
113 | 400kV | STNMC1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | REMOTE END INTERTRIP RECEIVE
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME

## SIGNAL STANDARDIZATION FOR 220
ABB SCADA SIGNAL LIST FOR VARIOUS PROTECTION & CONTROL SIGNALS - REV03 (220kV)
REQUIRED SIGNALS FOR DISTANCE RELAYS
| IED name: | R_REL670_21M1
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/OV2PTOV1/Str/general | SPI | OVER VOLTAGE STAGE-1 START | Y
2 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/OV2PTOV1/Op/general | SPI | OVER VOLTAGE STAGE-1 TRIP | Y
3 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/OV2PTOV2/Str/general | SPI | OVER VOLTAGE STAGE-2 START | Y |  | Addition
4 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/OV2PTOV2/Op/general | SPI | OVER VOLTAGE STAGE-2 TRIP | Y
5 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/EF4_1/EF4PTOC1/Str/general | SPI | DEF START
6 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/EF4_1/EF4PTOC1/Op/general | SPI | DEF TRIP | Y
7 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/STBPTOC1/Op/general | SPI | STUB PROTECTION OPERATED | Y | Applicable for One and Half CB Busbar system
8 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCVPSOF1/Op/general | SPI | SOTF OPERATED | Y
9 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Str/general | SPI | START, Z1
10 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/general | SPI | START, Z2
11 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsA | SPI | START, Z2 R PH
12 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsB | SPI | START, Z2 Y PH
13 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsC | SPI | START, Z2 B PH
14 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS3/Str/general | SPI | START, Z3
15 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS4/Str/general | SPI | START, Z4(REVERSE) |  | ** Whichever the zone choses as Reverse | Text correction
16 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS5/Str/general | SPI | START, Z5
17 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/general | SPI | GENERAL TRIP, Z1 | Y
18 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsA | SPI | TRIP, Z1 R PH | Y
19 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsB | SPI | TRIP, Z1 Y PH | Y
20 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsC | SPI | TRIP, Z1 B PH | Y
21 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/general | SPI | GENERAL TRIP, Z2 | Y
22 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsA | SPI | TRIP, Z2 R PH | Y
23 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsB | SPI | TRIP, Z2 Y PH | Y
24 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsC | SPI | TRIP, Z2 B PH | Y
25 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS3/Op/general | SPI | GENERAL TRIP, Z3 | Y
26 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS4/Op/general | SPI | GENERAL TRIP, Z4(REVERSE) | Y | ** Whichever the zone choses as Reverse | Text correction
27 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS5/Op/general | SPI | GENERAL TRIP, Z5 | Y
28 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/ProTx/stVal | SPI | CARRIER SEND | Y
29 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/ProRx/stVal | SPI | CARRIER RECEIVE | Y
30 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/Op/general | SPI | CARRIER AIDED SCHEME OPERATED | Y
31 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMRPSB1/Str/general | SPI | POWER SWING DETECTED | Y
32 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMRPSB1/BlkZn/stVal | SPI | POWER SWING BLOCKING | Y
33 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SMPPTRC1/Op/general | SPI | DISTANCE RELAY GENERAL TRIP | Y
34 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | R PHASE FAULT |  |  | Addition
35 | 220kV | STNMD1Q01M1DIS |  | SPI | Y PHASE FAULT |  |  | Addition
36 | 220kV | STNMD1Q01M1DIS |  | SPI | B PHASE FAULT | Y |  | Addition
37 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltDiskm/mag | DINT | FAULT LOCATOR DISTANCE
38 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltZ/cVal.mag | DINT | FAULT LOCATOR IMPEDANCE
39 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
40 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/BRCPTOC1/Op/general | SPI | BROKEN CONDUCTOR ALARM | Y
41 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
42 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/LPHD1/PhyHealth/stVal | SPI | M1 IED UNHEALTHY | Y
43 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | START AR TO BCU |  |  | Text correction
44 | 220kV | STNMD1Q01M1DIS |  | SPI | BLOCK AR TO BCU |  |  | Text correction
45 | 220kV | STNMD1Q01M1DIS |  | SPI | LINE ISOLATOR OPEN FOR STUB ACTIVATION |  | Applicable for One and Half CB Busbar system
46 | 220kV | STNMD1Q01M1DIS |  | SPI | DT SEND CH 1 | Y
47 | 220kV | STNMD1Q01M1DIS |  | SPI | DT SEND CH 2 | Y
48 | 220kV | STNMD1Q01M1DIS |  | SPI | DT RECEIVE CH 1 | Y |  |  | Only for DR in REL670, for SCADA to be configured from BCU
49 | 220kV | STNMD1Q01M1DIS |  | SPI | DT RECEIVE CH 2 | Y |  |  | Only for DR in REL670, for SCADA to be configured from BCU
50 | 220kV | STNMD1Q01M1DIS |  | SPI | TRIP RELAY 86 A HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
51 | 220kV | STNMD1Q01M1DIS |  | SPI | TRIP RELAY 86 B HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
52 | 220kV | STNMD1Q01M1DIS |  | SPI | GR A RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in REL670, for SCADA to be configured from BCU
53 | 220kV | STNMD1Q01M1DIS |  | SPI | GR B RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in REL670, for SCADA to be configured from BCU
54 | 220kV | STNMD1Q01M1DIS |  | SPI | CARRIER RECEIVE CH-1 | Y
55 | 220kV | STNMD1Q01M1DIS |  | SPI | CARRIER RECEIVE CH-2 | Y
56 | 220kV | STNMD1Q01M1DIS |  | SPI | CARRIER CHANNEL 1 OUT OF SERVICE | Y
57 | 220kV | STNMD1Q01M1DIS |  | SPI | CARRIER CHANNEL 2 OUT OF SERVICE | Y
58 | 220kV | STNMD1Q01M1DIS |  | SPI | CARRIER CHANNEL 1 FAIL | Y
59 | 220kV | STNMD1Q01M1DIS |  | SPI | CARRIER CHANNEL 2 FAIL | Y
60 | 220kV | STNMD1Q01M1DIS |  | SPI | MAIN 2/1 RELAY FAIL | Y
61 | 220kV | STNMD1Q01M1DIS |  | SPI | CB CLOSE COMMAND FOR SOTF INITIATION | Y |  | Text correction
62 | 220kV | STNMD1Q01M1DIS |  | SPI | BCU RELAY FAIL | Y
63 | 220kV | STNMD1Q01M1DIS |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
64 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsA | SPI | START, Z1 R PH |  |  | Addition
65 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsB | SPI | START, Z1 Y PH |  |  | Addition
66 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsC | SPI | START, Z1 B PH |  |  | Addition
67 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP 3PH | Y |  | Addition
68 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP R PH | Y |  | Addition
69 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP Y PH | Y |  | Addition
70 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP B PH | Y |  | Addition
71 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | PREPARE 3-PH TRIP FROM TIE BCU | Y |  | Addition, Available in BCU | It is also required in REL670
72 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | PREPARE 3-PH TRIP FROM MAIN BCU | Y |  | Addition, Available in BCU | It is also required in REL670
73 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | MAIN/ TIE CB AR OPTD | Y |  | Addition, Available in BCU | Only for DR in REL670, for SCADA to be configured from BCU
74 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | MAIN/ TIE LBB PROTECTION OPERATED | Y |  | Addition, Available in BBP | Only for DR in REL670, for SCADA to be configured from LBB/BBP relay
75 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | BUSBAR M1/M2 OPTD | Y |  | Addition, Available in BBP | Only for DR in REL670, for SCADA to be configured from BBP relay
76 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | GROUP RELAY 86A OPTD | Y |  | Available in REL670 (Sig. 52) | Agreed
77 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/EchoWei/stVal | SPI | WEAK INFEED ECHO SEND | Y |  | Addition
78 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/EchoWeiOp/stVal | SPI | WEAK INFEED TRIP | Y |  | Addition
79 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/RvABlk/stVal | SPI | CURRENT REVERSAL DETECTED | Y |  | Addition
80 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
81 | 220kV | STNMD1Q01M1DIS |  | SPI | SETTINGS CHANGED | Y |  | Addition
82 | 220kV | STNMD1Q01M1DIS |  | SPI | DR MEMMORY 80% FULL | Y |  | Addition
83 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltDiskm/mag | AI | DISTANCE MEASUREMENT IN KM | Y |  | Available in REL670 (Sig. 37) | Agreed
84 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltZ/cVal/mag | AI | DISTANCE MEASUREMENT IN IMPEDANCE | Y |  | Available in REL670 (Sig. 38) | Agreed
85 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/MON/L4UFCNTn/CntVal/actVal | AI | CH-1 Code-1 Tx |  |  | CH-1 Code-1 Tx (MAIN-1 CARRIER SEND CHANNEL-1)
86 | 220kV | STNMD1Q01M1DIS |  | AI | CH-1 Code-1 Rx |  |  | CH-1 Code-1 Rx (MAIN-1 CARRIER RECEIVE CHANNEL-1)
87 | 220kV | STNMD1Q01M1DIS |  | AI | CH-1 Code-2 Tx |  |  | CH-1 Code-2 Tx (MAIN-2 CARRIER SEND CHANNEL-1)
88 | 220kV | STNMD1Q01M1DIS |  | AI | CH-1 Code-2 Rx |  |  | CH-1 Code-2 Rx (MAIN-2 CARRIER RECEIVE CHANNEL-1)
89 | 220kV | STNMD1Q01M1DIS |  | AI | CH-2 Code-2 Tx |  |  | CH-2 Code-2 Tx (MAIN-2 CARRIER SEND CHANNEL-2)
90 | 220kV | STNMD1Q01M1DIS |  | AI | CH-2 Code-2 Rx |  |  | CH-2 Code-2 Rx (MAIN-2 CARRIER RECEIVECHANNEL-2)
91 | 220kV | STNMD1Q01M1DIS |  | AI | CH-2 Code-1 Tx |  |  | CH-2 Code-1 Tx (MAIN-1 CARRIER SEND CHANNEL-2)
92 | 220kV | STNMD1Q01M1DIS |  | AI | CH-2 Code-1 Rx |  |  | CH-2 Code-1 Rx (MAIN-1 CARRIER RECEIVE CHANNEL-2)
93 | 220kV | STNMD1Q01M1DIS |  | AI | CH-1 Code-3 Tx |  |  | CH-1 Code-3 Tx (DT SEND CHANNEL-1)
94 | 220kV | STNMD1Q01M1DIS |  | AI | CH-1 Code-3 Rx |  |  | CH-1 Code-3 Rx (DT RECEIVE CHANNEL-1)
95 | 220kV | STNMD1Q01M1DIS |  | AI | CH-2 Code-3 Tx |  |  | CH-2 Code-3 Tx (DT SEND CHANNEL-2)
96 | 220kV | STNMD1Q01M1DIS |  | AI | CH-2 Code-3 Rx |  |  | CH-2 Code-3 Rx (DT RECEIVE CHANNEL-2)
97 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
98 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-2 | Y |  | Addition
99 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-3 | Y |  | Addition
100 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-4 | Y |  | Addition
101 | 220kV | STNMD1Q01M1DIS | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-5 | Y |  | Addition
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR ICT DIFFERENTIAL RELAYS
| IED name: | R_RET670_87T
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/OEXPVPH1/Str/general | SPI | OVEREXCITATION HV START | Y
2 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/OEXPVPH1/Alm/stVal | SPI | OVEREXCITATION HV ALARM | Y
3 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/OEXPVPH1/Op/general | SPI | OVEREXCITATION HV TRIP | Y
4 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/DifAlm/stVal | SPI | DIFFERENTIAL CURRENT ALARM | Y
5 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/general | SPI | DIFFERENTIAL PROTECTION START | Y
6 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsA | SPI | DIFFERENTIAL PROTECTION RPH START | Y
7 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsB | SPI | DIFFERENTIAL PROTECTION YPH START | Y
8 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsC | SPI | DIFFERENTIAL PROTECTION BPH START | Y
9 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Op/general | SPI | DIFFERENTIAL PROTECTION TRIP | Y
10 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION RPH TRIP | Y
11 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION YPH TRIP | Y
12 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION BPH TRIP | Y
13 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/OpRst/stVal | SPI | DIFFERENTIAL PROTECTION TRIP (RESTRAINED MODE) | Y
14 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/OpUnRst/stVal | SPI | DIFFERENTIAL PROTECTION TRIP (UNRESTRAINED MODE) | Y
15 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Blk2H/stVal | SPI | DIFFERENTIAL PROTECTION 2nd HARMONIC BLOCK
16 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Blk5H/stVal | SPI | DIFFERENTIAL PROTECTION 5th HARMONIC BLOCK
17 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SMPPTRC1/Op/general | SPI | DIFFERENTIAL RELAY GENERAL TRIP | Y
18 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
19 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/LPHD1/PhyHealth/stVal | SPI | DIFFRENTIAL IED UNHEALTHY | Y
20 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | OTI ALARM | Y | APPLICABLE FOR 3 PHASE TRANSFORMERS
21 | 220kV | STNMD1Q01TDIF |  | SPI | WTI HV ALARM | Y
22 | 220kV | STNMD1Q01TDIF |  | SPI | WTI IV ALARM | Y
23 | 220kV | STNMD1Q01TDIF |  | SPI | WTI MV ALARM | Y
24 | 220kV | STNMD1Q01TDIF |  | SPI | BUCCHOLZ_n ALARM | Y |  | Addition
25 | 220kV | STNMD1Q01TDIF |  | SPI | BUCCHOLZ_n TRIP | Y |  | Text correction
26 | 220kV | STNMD1Q01TDIF |  | SPI | OSR _n TRIP | Y |  | Text correction
27 | 220kV | STNMD1Q01TDIF |  | SPI | PRD _n TRIP | Y |  | Text correction
28 | 220kV | STNMD1Q01TDIF |  | SPI | FIRE PROTECTION OPERATED | Y
29 | 220kV | STNMD1Q01TDIF |  | SPI | LOW OIL LEVEL | Y
30 | 220kV | STNMD1Q01TDIF |  | SPI | OTI R PH ALARM | Y | APPLICABLE FOR SINGLE PHASE TRANSFORMERS (If a dedicated IED is provided for spare transformer protection, only spare phase signals are required to be used)
31 | 220kV | STNMD1Q01TDIF |  | SPI | OTI Y PH ALARM | Y
32 | 220kV | STNMD1Q01TDIF |  | SPI | OTI B PH ALARM | Y
33 | 220kV | STNMD1Q01TDIF |  | SPI | OTI SPARE ICT ALARM | Y
34 | 220kV | STNMD1Q01TDIF |  | SPI | WTI HV R PH ALARM | Y
35 | 220kV | STNMD1Q01TDIF |  | SPI | WTI HV Y PH ALARM | Y
36 | 220kV | STNMD1Q01TDIF |  | SPI | WTI HV B PH ALARM | Y
37 | 220kV | STNMD1Q01TDIF |  | SPI | WTI HV SPARE ICT ALARM | Y
38 | 220kV | STNMD1Q01TDIF |  | SPI | WTI MV R PH ALARM | Y
39 | 220kV | STNMD1Q01TDIF |  | SPI | WTI MV Y PH ALARM | Y
40 | 220kV | STNMD1Q01TDIF |  | SPI | WTI MV B PH ALARM | Y
41 | 220kV | STNMD1Q01TDIF |  | SPI | WTI MV SPARE ICT ALARM | Y
42 | 220kV | STNMD1Q01TDIF |  | SPI | WTI IV R PH ALARM | Y
43 | 220kV | STNMD1Q01TDIF |  | SPI | WTI IV Y PH ALARM | Y
44 | 220kV | STNMD1Q01TDIF |  | SPI | WTI IV B PH ALARM | Y
45 | 220kV | STNMD1Q01TDIF |  | SPI | WTI IV SPARE ICT ALARM | Y
46 | 220kV | STNMD1Q01TDIF |  | SPI | BUCHHOLZ_n R PH ALARM | Y |  | Addition
47 | 220kV | STNMD1Q01TDIF |  | SPI | BUCHHOLZ_n Y PH ALARM | Y |  | Addition
48 | 220kV | STNMD1Q01TDIF |  | SPI | BUCHHOLZ_n B PH ALARM | Y |  | Addition
49 | 220kV | STNMD1Q01TDIF |  | SPI | BUCHHOLZ_n SPARE ICT TRIP | Y |  | Addition, BUCHHOLZ_n SPARE ICT ALARM
50 | 220kV | STNMD1Q01TDIF |  | SPI | BUCHHOLZ_n R PH TRIP | Y |  | Text correction
51 | 220kV | STNMD1Q01TDIF |  | SPI | BUCHHOLZ_n Y PH TRIP | Y |  | Text correction
52 | 220kV | STNMD1Q01TDIF |  | SPI | BUCHHOLZ_n B PH TRIP | Y |  | Text correction
53 | 220kV | STNMD1Q01TDIF |  | SPI | BUCHHOLZ_n SPARE ICT TRIP | Y |  | Text correction
54 | 220kV | STNMD1Q01TDIF |  | SPI | OSR_n R PH TRIP | Y |  | Text correction
55 | 220kV | STNMD1Q01TDIF |  | SPI | OSR_n Y PH TRIP | Y |  | Text correction
56 | 220kV | STNMD1Q01TDIF |  | SPI | OSR_n B PH TRIP | Y |  | Text correction
57 | 220kV | STNMD1Q01TDIF |  | SPI | OSR_n SPARE ICT TRIP | Y |  | Text correction
58 | 220kV | STNMD1Q01TDIF |  | SPI | PRD n R PH TRIP | Y |  | Text correction
59 | 220kV | STNMD1Q01TDIF |  | SPI | PRD nY PH TRIP | Y |  | Text correction
60 | 220kV | STNMD1Q01TDIF |  | SPI | PRD n B PH TRIP | Y |  | Text correction
61 | 220kV | STNMD1Q01TDIF |  | SPI | PRD n SPARE ICT TRIP | Y |  | Text correction
62 | 220kV | STNMD1Q01TDIF |  | SPI | LOW OIL LEVEL R PH | Y
63 | 220kV | STNMD1Q01TDIF |  | SPI | LOW OIL LEVEL Y PH | Y
64 | 220kV | STNMD1Q01TDIF |  | SPI | LOW OIL LEVEL B PH | Y
65 | 220kV | STNMD1Q01TDIF |  | SPI | LOW OIL LEVEL SPARE ICT | Y
66 | 220kV | STNMD1Q01TDIF |  | SPI | FIRE PROTECTION R PH OPERATED | Y
67 | 220kV | STNMD1Q01TDIF |  | SPI | FIRE PROTECTION Y PH OPERATED | Y
68 | 220kV | STNMD1Q01TDIF |  | SPI | FIRE PROTECTION B PH OPERATED | Y
69 | 220kV | STNMD1Q01TDIF |  | SPI | FIRE PROTECTION SPARE ICT OPERATED | Y
70 | 220kV | STNMD1Q01TDIF |  | SPI | TRIP RELAY 86 A HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
71 | 220kV | STNMD1Q01TDIF |  | SPI | TRIP RELAY 86 B HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
72 | 220kV | STNMD1Q01TDIF |  | SPI | GR A RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RET670, for SCADA to be configured from BCU
73 | 220kV | STNMD1Q01TDIF |  | SPI | GR B RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RET670, for SCADA to be configured from BCU
74 | 220kV | STNMD1Q01TDIF |  | SPI | REF RELAY FAIL | Y
75 | 220kV | STNMD1Q01TDIF |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
** It may be noted that the Body Protection alarms & trips have been Grouped into two separate relays Differential (Group A) & REF (Group B) relays. The hardwiring for same must be done accordingly and approved scheme shall be modified if required. Same is applicable for Reactor protection also.
76 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/OC4_1/OC4PTOC1/Str/general | SPI | TERTIARY 33kV PHASE OVERCURRENT START | Y |  | Addition
77 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/OC4_1/OC4PTOC1/Op/general | SPI | TERTIARY33kV PHASE OVERCURRENT TRIP | Y |  | Addition
78 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/EF4_1/EF4PTOC1/Str/general | SPI | TERTIARY 33kV PHASE EARTHFAULT START | Y |  | Addition
79 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/EF4_1/EF4PTOC1/Op/general | SPI | TERTIARY 33kV PHASE EARTHFAULT TRIP | Y |  | Addition
80 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/ROV2_1/ROV2PTOV1/Str/general | SPI | TERTIARY 33kV PHASE RESIDUAL OVERVOLTAGE START | Y |  | Addition
81 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/ROV2_1/ROV2PTOV1/OP/general | SPI | TERTIARY 33kV PHASE RESIDUAL OVERVOLTAGE TRIP | Y |  | Addition
82 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | TERTIARY 33kV 86 OPTD | Y |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
83 | 220kV | STNMD1Q01TDIF |  | SPI | TERTIARY TRAFO - BUCHHOLZ ALARM | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
84 | 220kV | STNMD1Q01TDIF |  | SPI | TERTIARY TRAFO - BUCHHOLZ TRIP | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
85 | 220kV | STNMD1Q01TDIF |  | SPI | TERTIARY TRAFO - WTI ALARM | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
86 | 220kV | STNMD1Q01TDIF |  | SPI | TERTIARY TRAFO - WTI TRIP | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
87 | 220kV | STNMD1Q01TDIF |  | SPI | TERTIARY TRAFO - OTI ALARM | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
88 | 220kV | STNMD1Q01TDIF |  | SPI | TERTIARY TRAFO - OTI TRIP | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
89 | 220kV | STNMD1Q01TDIF |  | SPI | TERTIARY TRAFO - PRD ALARM | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
90 | 220kV | STNMD1Q01TDIF |  | SPI | TERTIARY TRAFO - PRD TRIP | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
91 | 220kV | STNMD1Q01TDIF |  | SPI | TERTIARY 33KV_TC-1 FAULTY | Y |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
92 | 220kV | STNMD1Q01TDIF |  | SPI | TERTIARY 33KV_TC-2 FAULTY | Y |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
93 | 220kV | STNMD1Q01TDIF |  | SPI | TERTIARY 33kV CB ASSOCIATED ALARMS | Y |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
94 | 220kV | STNMD1Q01TDIF |  | SPI | RELAY IN TEST MODE | Y |  | Addition
95 | 220kV | STNMD1Q01TDIF |  | SPI | SETTINGS CHANGED | Y |  | Addition
96 | 220kV | STNMD1Q01TDIF |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
97 | 220kV | STNMD1Q01TDIF |  | CMD | DELUGE COMMAND |  | APPLICABLE FOR 3 PHASE TRANSFORMERS | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
98 | 220kV | STNMD1Q01TDIF |  | CMD | DELUGE COMMAND R PH |  | APPLICABLE FOR SINGLE PHASE TRANSFORMERS (If a dedicated IED is provided for spare transformer protection, only spare phase signals are required to be used) | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
99 | 220kV | STNMD1Q01TDIF |  | CMD | DELUGE COMMAND Y PH |  |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
100 | 220kV | STNMD1Q01TDIF |  | CMD | DELUGE COMMAND B PH |  |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
101 | 220kV | STNMD1Q01TDIF |  | CMD | DELUGE COMMAND SPARE |  |  | Addition, This signal can be moved to BCU, Need to discuss | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
102 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL//EF4_1/EF4PTOC2/Str/general | SPI | NEUTRAL OVERCURRENT ALARM | Y |  | Addition | As per the CRP scheme this will be configured in Main BCU/Aux. BCU
103 | 220kV | STNMD1Q01TDIF | SS_BAY_DIFFERENTIAL//LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
104 | 220kV | STNMD1Q01TDIF |  | SPI | SPARE ALARM-2 | Y |  | Addition
105 | 220kV | STNMD1Q01TDIF |  | SPI | SPARE ALARM-3 | Y |  | Addition
106 | 220kV | STNMD1Q01TDIF |  | SPI | SPARE ALARM-4 | Y |  | Addition
107 | 220kV | STNMD1Q01TDIF |  | SPI | SPARE ALARM-5 | Y |  | Addition
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR ICT REF RELAYS
| IED name: | R_RET670_64
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 220kV | STNMD1Q01TREF | SS_BAY_REF/LD0/OEXPVPH1/Str/general | SPI | OVEREXCITATION MV START
2 | 220kV | STNMD1Q01TREF | SS_BAY_REF/LD0/OEXPVPH1/Alm/stVal | SPI | OVEREXCITATION MV ALARM | Y
3 | 220kV | STNMD1Q01TREF | SS_BAY_REF/LD0/OEXPVPH1/Op/general | SPI | OVEREXCITATION MV TRIP | Y
4 | 220kV | STNMD1Q01TREF | SS_BAY_REF/LD0/HZPDIF1/Alm/stVal | SPI | REF ALARM
5 | 220kV | STNMD1Q01TREF | SS_BAY_REF/LD0/HZPDIF1/Op/general | SPI | REF TRIP | Y
6 | 220kV | STNMD1Q01TREF | SS_BAY_REF/LD0/SMPPTRC1/Op/general | SPI | REF RELAY GENERAL TRIP | Y
7 | 220kV | STNMD1Q01TREF | SS_BAY_REF/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
8 | 220kV | STNMD1Q01TREF | SS_BAY_REF/LD0/LPHD1/PhyHealth/stVal | SPI | REF IED UNHEALTHY | Y
9 | 220kV | STNMD1Q01TREF | SS_BAY_REF/LD0/SP16GGIO n/Ind n/stVal | SPI | OTI TRIP | Y | APPLICABLE FOR 3 PHASE TRANSFORMERS
10 | 220kV | STNMD1Q01TREF |  | SPI | WTI HV TRIP | Y
11 | 220kV | STNMD1Q01TREF |  | SPI | WTI MV TRIP | Y
12 | 220kV | STNMD1Q01TREF |  | SPI | WTI LV TRIP | Y
13 | 220kV | STNMD1Q01TREF |  | SPI | OSR 2 TRIP | Y
14 | 220kV | STNMD1Q01TREF |  | SPI | PRD 2 TRIP | Y
15 | 220kV | STNMD1Q01TREF |  | SPI | BUCCHOLZ_n ALARM | Y |  | Text correction
16 | 220kV | STNMD1Q01TREF |  | SPI | BUCCHOLZ_n TRIP | Y |  | Addition
17 | 220kV | STNMD1Q01TREF |  | SPI | OTI R PH TRIP | Y | APPLICABLE FOR SINGLE PHASE TRANSFORMERS (If a dedicated IED is provided for spare transformer protection, only spare phase signals are required to be used)
18 | 220kV | STNMD1Q01TREF |  | SPI | OTI Y PH TRIP | Y
19 | 220kV | STNMD1Q01TREF |  | SPI | OTI B PH TRIP | Y
20 | 220kV | STNMD1Q01TREF |  | SPI | OTI SPARE ICT TRIP | Y
21 | 220kV | STNMD1Q01TREF |  | SPI | WTI HV R PH TRIP | Y
22 | 220kV | STNMD1Q01TREF |  | SPI | WTI HV Y PH TRIP | Y
23 | 220kV | STNMD1Q01TREF |  | SPI | WTI HV B PH TRIP | Y
24 | 220kV | STNMD1Q01TREF |  | SPI | WTI HV SPARE ICT TRIP | Y
25 | 220kV | STNMD1Q01TREF |  | SPI | WTI MV R PH TRIP | Y
26 | 220kV | STNMD1Q01TREF |  | SPI | WTI MV Y PH TRIP | Y
27 | 220kV | STNMD1Q01TREF |  | SPI | WTI MV B PH TRIP | Y
28 | 220kV | STNMD1Q01TREF |  | SPI | WTI MV SPARE ICT TRIP | Y
29 | 220kV | STNMD1Q01TREF |  | SPI | WTI IV R PH TRIP | Y
30 | 220kV | STNMD1Q01TREF |  | SPI | WTI IV Y PH TRIP | Y
31 | 220kV | STNMD1Q01TREF |  | SPI | WTI IV B PH TRIP | Y
32 | 220kV | STNMD1Q01TREF |  | SPI | WTI IV SPARE ICT TRIP | Y
33 | 220kV | STNMD1Q01TREF |  | SPI | BUCCHOLZ R PH ALARM | Y
34 | 220kV | STNMD1Q01TREF |  | SPI | BUCCHOLZ Y PH ALARM | Y
35 | 220kV | STNMD1Q01TREF |  | SPI | BUCCHOLZ B PH ALARM | Y
36 | 220kV | STNMD1Q01TREF |  | SPI | BUCCHOLZ SPARE ICT ALARM | Y
37 | 220kV | STNMD1Q01TREF |  | SPI | OSR 2 R PH TRIP | Y
38 | 220kV | STNMD1Q01TREF |  | SPI | OSR 2 Y PH TRIP | Y
39 | 220kV | STNMD1Q01TREF |  | SPI | OSR 2 B PH TRIP | Y
40 | 220kV | STNMD1Q01TREF |  | SPI | OSR 2 SPARE ICT TRIP | Y
41 | 220kV | STNMD1Q01TREF |  | SPI | PRD 2 R PH TRIP | Y
42 | 220kV | STNMD1Q01TREF |  | SPI | PRD 2 Y PH TRIP | Y
43 | 220kV | STNMD1Q01TREF |  | SPI | PRD 2 B PH TRIP | Y
44 | 220kV | STNMD1Q01TREF |  | SPI | PRD 2 SPARE ICT TRIP | Y
45 | 220kV | STNMD1Q01TREF |  | SPI | DIFFERENTIAL RELAY FAIL | Y
46 | 220kV | STNMD1Q01TREF |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
47 | 220kV | STNMD1Q01TREF |  | SPI | RELAY IN TEST MODE | Y |  | Addition
48 | 220kV | STNMD1Q01TREF |  | SPI | SETTINGS CHANGED | Y |  | Addition
49 | 220kV | STNMD1Q01TREF |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
50 | 220kV | STNMD1Q01TREF |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
51 | 220kV | STNMD1Q01TREF |  | SPI | SPARE ALARM-2 | Y |  | Addition
52 | 220kV | STNMD1Q01TREF |  | SPI | SPARE ALARM-3 | Y |  | Addition
53 | 220kV | STNMD1Q01TREF |  | SPI | SPARE ALARM-4 | Y |  | Addition
54 | 220kV | STNMD1Q01TREF |  | SPI | SPARE ALARM-5 | Y |  | Addition
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR REACTOR ICT IMPEDANCE PROTECTION RELAY | [7 empty] | Additional Relay - The Impedance Preotection is not applicable for 220kV Voltage
| IED name: | R_REL670_21T
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/ZMCAPDIS1/Str/phsA | SPI | BACKUP IMPEDANCE START, Z1 R PH
2 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/ZMCAPDIS1/Str/phsB | SPI | BACKUP IMPEDANCE START, Z1 Y PH
3 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMPE/LD0/ZMCAPDIS1/Str/phsC | SPI | BACKUP IMPEDANCE START, Z1 B PH
4 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS1.Str.general | SPI | BACKUP IMPEDANCE START |  |  | BACKUP IMPEDANCE ZONE-1 START | Agreed
5 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS1.Op.general | SPI | BACKUP IMPEDANCE ZONE-1 TRIP | Y
6 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/ZMCAPDIS2/Str/phsA | SPI | BACKUP IMPEDANCE START, Z2 R PH
7 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/ZMCAPDIS2/Str/phsB | SPI | BACKUP IMPEDANCE START, Z2 Y PH
8 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMPE/LD0/ZMCAPDIS2/Str/phsC | SPI | BACKUP IMPEDANCE START, Z2B PH
9 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS2.Str.general | SPI | BACKUP IMPEDANCE ZONE-2 START
10 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS2.Op.general | SPI | BACKUP IMPEDANCE ZONE-2 TRIP | Y
11 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS3.Str.general | SPI | BACKUP IMPEDANCE ZONE-3 START
12 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS3.Op.general | SPI | BACKUP IMPEDANCE ZONE-3 TRIP | Y
13 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS4.Str.general | SPI | BACKUP IMPEDANCE ZONE-4 START
14 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0.ZMHPDIS4.Op.general | SPI | BACKUP IMPEDANCE ZONE-4 TRIP | Y
15 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SMPPTRC1/Op/general | SPI | BACKUP IMPEDANCE RELAY GENERAL TRIP | Y
16 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/OC4_1/OC4PTOC1/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 START
17 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/OC4_1/OC4PTOC1/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 TRIP | Y
18 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/EF4_1/EF4PTOC1/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 START
19 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/EF4_1/EF4PTOC1/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 TRIP | Y
20 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/OC4_1/OC4PTOC2/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 START
21 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/OC4_1/OC4PTOC2/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 TRIP | Y
22 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/EF4_1/EF4PTOC2/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 START
23 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/EF4_1/EF4PTOC2/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 TRIP | Y
24 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SMPPTRC/*** | SPI | BACKUP IMPEDANCE GENERAL TRIP 3PH | Y
25 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SMPPTRC/*** | SPI | BACKUP IMPEDANCE GENERAL TRIP R PH | Y
26 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SMPPTRC/*** | SPI | BACKUP IMPEDANCE GENERAL TRIP Y PH | Y
27 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SMPPTRC/*** | SPI | BACKUP IMPEDANCE GENERAL TRIP B PH | Y
28 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
29 | 220kV | STNMD1Q01THVBIMP | SS_BAY_HV BACKUP IMP/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
30 | 220kV | STNMD1Q01THVBIMP |  | SPI | BACKUP IMPEDANCE IED UNHEALTHY | Y
31 | 220kV | STNMD1Q01THVBIMP |  | SPI | RELAY IN TEST MODE | Y
32 | 220kV | STNMD1Q01THVBIMP |  | SPI | SETTINGS CHANGED | Y
33 | 220kV | STNMD1Q01THVBIMP |  | SPI | DR MEMORY 80% FULL | Y
34 | 220kV | STNMD1Q01THVBIMP |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
35 | 220kV | STNMD1Q01THVBIMP |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
36 | 220kV | STNMD1Q01THVBIMP |  | SPI | SPARE ALARM-2 | Y
37 | 220kV | STNMD1Q01THVBIMP |  | SPI | SPARE ALARM-3 | Y
38 | 220kV | STNMD1Q01THVBIMP |  | SPI | SPARE ALARM-4 | Y
39 | 220kV | STNMD1Q01THVBIMP |  | SPI | SPARE ALARM-5 | Y
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR HV DIRECTIONAL OVERCURRENT AND EARTH FAULT RELAYS
| IED name: | R_REL670_HVBUP
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 220kV | STNMD1Q01THBU | SS_BAY_HV BACKUP OC EF/OC4_1/OC4PTOC1/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 START |  |  | Text correction
2 | 220kV | STNMD1Q01THBU | SS_BAY_HV BACKUP OC EFE/OC4_1/OC4PTOC1/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 TRIP | Y |  | Text correction
3 | 220kV | STNMD1Q01THBU | SS_BAY_HV BACKUP OC EF/EF4_1/EF4PTOC1/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 START |  |  | Text correction
4 | 220kV | STNMD1Q01THBU | SS_BAY_HV BACKUP OC EF/EF4_1/EF4PTOC1/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 TRIP | Y |  | Text correction
5 | 220kV | STNMD1Q01THBU | SS_BAY_HV BACKUP OC EF/OC4_1/OC4PTOC2/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 START |  | if Non Directional then name has to be replaced with Directional to Non-Directional | Addition
6 | 220kV | STNMD1Q01THBU | SS_BAY_HV BACKUP OC EF/OC4_1/OC4PTOC2/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 TRIP | Y |  | Addition
7 | 220kV | STNMD1Q01THBU | SS_BAY_HV BACKUP OC EF/EF4_1/EF4PTOC2/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 START |  |  | Addition
8 | 220kV | STNMD1Q01THBU | SS_BAY_HV BACKUP OC EF/EF4_1/EF4PTOC2/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 TRIP | Y |  | Addition
9 | 220kV | STNMD1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
10 | 220kV | STNMD1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/SMPPTRC1/Op/general | SPI | GENERAL TRIP | Y
11 | 220kV | STNMD1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
12 | 220kV | STNMD1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/LPHD1/PhyHealth/stVal | SPI | BACKUP OC/EF IED UNHEALTHY | Y
13 | 220kV | STNMD1Q01THBU | SS_BAY_HV BACKUP OC EF/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y
14 | 220kV | STNMD1Q01THBU |  | SPI | SETTINGS CHANGED | Y |  | Addition
15 | 220kV | STNMD1Q01THBU |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
16 | 220kV | STNMD1Q01THBU |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme | Addition
17 | 220kV | STNMD1Q01THBU |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
18 | 220kV | STNMD1Q01THBU |  | SPI | SPARE ALARM-2 | Y |  | Addition
19 | 220kV | STNMD1Q01THBU |  | SPI | SPARE ALARM-3 | Y |  | Addition
20 | 220kV | STNMD1Q01THBU |  | SPI | SPARE ALARM-4 | Y |  | Addition
21 | 220kV | STNMD1Q01THBU |  | SPI | SPARE ALARM-5 | Y |  | Addition
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR LV DIRECTIONAL OVERCURRENT AND EARTH FAULT RELAYS
| IED name: | R_REL670_LVBUP
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 220kV | STNMD1Q01TLBU | SS_BAY_LV BACKUP OC EF/OC4_1/OC4PTOC1/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 START |  |  | Text correction
2 | 220kV | STNMD1Q01TLBU | SS_BAY_LV BACKUP OC EFE/OC4_1/OC4PTOC1/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-1 TRIP | Y |  | Text correction
3 | 220kV | STNMD1Q01TLBU | SS_BAY_LV BACKUP OC EF/EF4_1/EF4PTOC1/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 START |  |  | Text correction
4 | 220kV | STNMD1Q01TLBU | SS_BAY_LV BACKUP OC EF/EF4_1/EF4PTOC1/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-1 TRIP | Y |  | Text correction
5 | 220kV | STNMD1Q01TLBU | SS_BAY_LV BACKUP OC EF/OC4_1/OC4PTOC2/Str/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 START |  | if Non Directional then name has to be replaced with Directional to Non-Directional | Addition
6 | 220kV | STNMD1Q01TLBU | SS_BAY_LV BACKUP OC EF/OC4_1/OC4PTOC2/Op/general | SPI | DIRECTIONAL OVERCURRENT STAGE-2 TRIP | Y |  | Addition
7 | 220kV | STNMD1Q01TLBU | SS_BAY_LV BACKUP OC EF/EF4_1/EF4PTOC2/Str/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 START |  |  | Addition
8 | 220kV | STNMD1Q01TLBU | SS_BAY_LV BACKUP OC EF/EF4_1/EF4PTOC2/Op/general | SPI | DIRECTIONAL EARTHFAULT STAGE-2 TRIP | Y |  | Addition
9 | 220kV | STNMD1Q01TLBU | SS_BAY_LV BACKUP OC EF/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
10 | 220kV | STNMD1Q01TLBU | SS_BAY_LV BACKUP OC EF/LD0/SMPPTRC1/Op/general | SPI | GENERAL TRIP | Y
11 | 220kV | STNMD1Q01TLBU | SS_BAY_LV BACKUP OC EF/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
12 | 220kV | STNMD1Q01TLBU | SS_BAY_LV BACKUP OC EF/LD0/LPHD1/PhyHealth/stVal | SPI | BACKUP OC/EF IED UNHEALTHY | Y
13 | 220kV | STNMD1Q01TLBU | SS_BAY_LV BACKUP OC EF/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
14 | 220kV | STNMD1Q01TLBU |  | SPI | SETTINGS CHANGED | Y |  | Addition
15 | 220kV | STNMD1Q01TLBU |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
16 | 220kV | STNMD1Q01TLBU |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME
REQUIRED SIGNALS FOR REACTOR DIFFERENTIAL RELAYS
| IED name: | R_RET670_87R
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Op/general | SPI | DIFFERENTIAL PROTECTION TRIP | Y
2 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION RPH TRIP | Y
3 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION YPH TRIP | Y
4 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION BPH TRIP | Y
5 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/DifAlm/stVal | SPI | DIFFERENTIAL CURRENT ALARM
6 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/general | SPI | DIFFERENTIAL PROTECTION START
7 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsA | SPI | DIFFERENTIAL PROTECTION RPH START
8 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsB | SPI | DIFFERENTIAL PROTECTION YPH START
9 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Str/PhsC | SPI | DIFFERENTIAL PROTECTION BPH START
10 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SMPPTRC1/Op/general | SPI | DIFFERENTIAL RELAY GENERAL TRIP | Y
11 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/OpRst/stVal | SPI | DIFFERENTIAL PROTECTION TRIP (RESTRAINED MODE) | Y |  | Addition
12 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/OpUnRst/stVal | SPI | DIFFERENTIAL PROTECTION TRIP (UNRESTRAINED MODE) | Y |  | Addition
13 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Blk2H/stVal | SPI | DIFFERENTIAL PROTECTION 2nd HARMONIC BLOCK |  |  | Addition
14 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/TnWPDIF1/Blk5H/stVal | SPI | DIFFERENTIAL PROTECTION 5th HARMONIC BLOCK |  |  | Addition
15 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | BUSBAR PROT OPTD | Y |  | Addition, Need to discuss | Only for DR in RET670, for SCADA to be configured from BBP relay
16 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | TIME SYNCHRONIZATION ERROR | Y
17 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/LPHD1/PhyHealth/stVal | SPI | DIFFERENTIAL IED UNHEALTHY | Y |  |  | *
18 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF | SS_BAY_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | OTI TRIP | Y | APPLICABLE FOR 3 PHASE REACTORS | Interchanged between Diff. & REF relays
19 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | WTI ALARM | Y |  | Already available
20 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | BUCCHOLZ-A TRIP | Y |  | Addition
21 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | BUCCHOLZ-B ALARM | Y |  | Addition
22 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | PRV-1 TRIP(NO) | Y |  | Text correction
23 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | FIRE PROTECTION OPERATED | Y |  | Already available
24 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | LOW OIL LEVEL ALARM | Y |  | Already available
25 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | PRV-1 TRIP(NC) | Y |  | Addition, Need to discuss | Yet to be finalized by PGCIL
26 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | FLOW SENSITIVE CONSERVATOR VALVE ALARM | Y |  | Addition
27 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | REACTOR MB ALARMS | Y |  | Addition
28 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | OTI R PH ALARM | Y | APPLICABLE FOR SINGLE PHASE REACTORS (If a dedicated IED is provided for spare reactor protection, only spare phase signals are required to be used)
29 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | OTI Y PH ALARM | Y
30 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | OTI B PH ALARM | Y
31 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | OTI SPARE PH ALARM | Y
32 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | WTI R PH ALARM | Y
33 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | WTI Y PH ALARM | Y
34 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | WTI B PH ALARM | Y
35 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | WTI SPARE PH ALARM | Y
36 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | BUCCHOLZ_n R PH ALARM | Y |  | Interchanged between Diff. & REF relays
37 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | BUCCHOLZ_n Y PH ALARM | Y |  | Interchanged between Diff. & REF relays
38 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | BUCCHOLZ_n B PH ALARM | Y |  | Interchanged between Diff. & REF relays
39 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | BUCCHOLZ_n SPARE PH ALARM | Y |  | Interchanged between Diff. & REF relays
40 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | BUCCHOLZ_n R PH TRIP | Y |  | Text correction
41 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | BUCCHOLZ_n Y PH TRIP | Y |  | Text correction
42 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | BUCCHOLZ_n B PH TRIP | Y |  | Text correction
43 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | BUCCHOLZ_n SPARE PH TRIP | Y |  | Text correction
44 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | OSR R PH TRIP | Y
45 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | OSR Y PH TRIP | Y
46 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | OSR B PH TRIP | Y
47 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | OSR SPARE PH TRIP | Y
48 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | PRD R PH TRIP | Y |  |  | Yet to be finalized by PGCIL
49 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | PRD Y PH TRIP | Y |  |  | Yet to be finalized by PGCIL
50 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | PRD B PH TRIP | Y |  |  | Yet to be finalized by PGCIL
51 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | PRD SPARE PH TRIP | Y
52 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | LOW OIL LEVEL R PH | Y
53 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | LOW OIL LEVEL Y PH | Y
54 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | LOW OIL LEVEL B PH | Y
55 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | LOW OIL LEVEL SPARE PH | Y
56 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | FIRE PROTECTION R PH OPERATED | Y
57 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | FIRE PROTECTION Y PH OPERATED | Y
58 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | FIRE PROTECTION B PH OPERATED | Y
59 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | FIRE PROTECTION SPARE ICT OPERATED | Y
60 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | TRIP RELAY 86 A HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
61 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | TRIP RELAY 86 B HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
62 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | GR A RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RET670, for SCADA to be configured from BBP relay
63 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | GR B RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RET670, for SCADA to be configured from BBP relay
64 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | GR A RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Available in RET670 (Sig. 62)
65 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | GR B RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Available in RET670 (Sig. 63)
66 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | REF RELAY FAIL | Y
67 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | RELAY IN TEST MODE | Y |  | Addition
68 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | SETTINGS CHANGED | Y |  | Addition
69 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
70 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
71 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
72 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | SPARE ALARM-2 | Y |  | Addition
73 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | SPARE ALARM-3 | Y |  | Addition
74 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | SPARE ALARM-4 | Y |  | Addition
75 | 220kV | STNMD1Q01LRDIF /STNMD1Q01BRDIF |  | SPI | SPARE ALARM-5 | Y |  | Addition
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR REACTOR REF RELAYS
| IED name: | R_RET670_64R
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF | SS_BAY_REF/LD0/HZPDIF1/Alm/stVal | SPI | REF ALARM
2 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF | SS_BAY_REF/LD0/HZPDIF1/Op/general | SPI | REF TRIP | Y
3 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF | SS_BAY_REF/LD0/SMPPTRC1/Op/general | SPI | REF RELAY GENERAL TRIP | Y
4 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF | SS_BAY_REF/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
5 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF | SS_BAY_REF/LD0/LPHD1/PhyHealth/stVal | SPI | REF IED UNHEALTHY | Y
6 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF | SS_BAY_REF/LD0/SP16GGIO n/Ind n/stVal | SPI | OTI ALARM | Y | APPLICABLE FOR 3 PHASE REACTORS | Interchanged between Diff. & REF relays
7 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | WTI TRIP | Y |  | Already available
8 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | BUCCHOLZ-A ALARM | Y |  | Addition
9 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | BUCCHOLZ-B TRIP | Y |  | Addition
10 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | PRV-2 TRIP | Y |  | Addition
11 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | FIRE PROTECTION OPERATED | Y |  | Addition
12 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | HIGH LEVEL OIL ALARM | Y |  | Addition
13 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | 86B TRIP RELAY SUPERVSION ALARM | Y |  | Addition, Need to discuss
14 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | REACTOR MB ALARMS | Y |  | Addition
15 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | OTI R PH TRIP | Y | APPLICABLE FOR SINGLE PHASE REACTORS (If a dedicated IED is provided for spare Reactor protection, only spare phase signals are required to be used)
16 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | OTI Y PH TRIP | Y
17 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | OTI B PH TRIP | Y
18 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | OTI SPARE PH TRIP | Y
19 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | WTI R PH TRIP | Y
20 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | WTI Y PH TRIP | Y
21 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | WTI B PH TRIP | Y
22 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | WTI SPARE PH TRIP | Y
23 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | BUCCHOLZ R PH ALARM | Y
24 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | BUCCHOLZ Y PH ALARM | Y
25 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | BUCCHOLZ B PH ALARM | Y
26 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | BUCCHOLZ SPARE PH ALARM | Y
27 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | DIFFERENTIAL RELAY FAIL | Y
28 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | RELAY IN TEST MODE | Y |  | Addition
29 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | SETTINGS CHANGED | Y |  | Addition
30 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | DR MEMORY 80% FULL | Y |  | Addition
31 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
32 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | SPARE ALARM-2 | Y |  | Addition
33 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | SPARE ALARM-3 | Y |  | Addition
34 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | SPARE ALARM-4 | Y |  | Addition
35 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | SPARE ALARM-5 | Y |  | Addition
36 | 220kV | STNMD1Q01LRREF /STNMD1Q01BRREF |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR REACTOR BACKUP IMPEDANCE PROTECTION RELAY
| IED name: | R_REL670_21R
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP | SS_BAY_HV BACKUP OC EF/LD0.ZMHPDIS1.Str.general | SPI | BACKUP IMPEDANCE START
2 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP | SS_BAY_HV BACKUP OC EF/LD0.ZMHPDIS1.Op.general | SPI | BACKUP IMPEDANCE TRIP | Y
3 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP | SS_BAY_HV BACKUP OC EF/LD0/SMPPTRC1/Op/general | SPI | BACKUP IMPEDANCE RELAY GENERAL TRIP | Y
4 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP | SS_BAY_HV BACKUP OC EF/OC4_1/OC4PTOC1/Str/general | SPI | BACKUP OVERCURRENT START |  | No of stage Overcurrent need to be monitored
5 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP | SS_BAY_HV BACKUP OC EF/OC4_1/OC4PTOC1/Op/general | SPI | BACKUP OVERCURRENT TRIP | Y
6 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP | SS_BAY_HV BACKUP OC EF/EF4_1/EF4PTOC1/Str/general | SPI | BACKUP EARTHFAULT START
7 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP | SS_BAY_HV BACKUP OC EF/EF4_1/EF4PTOC1/Op/general | SPI | BACKUP EARTHFAULT TRIP | Y
8 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP | SS_BAY_HV BACKUP OC EF/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
9 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP | SS_BAY_HV BACKUP OC EF/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
10 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP | SS_BAY_HV BACKUP OC EF/LD0/LPHD1/PhyHealth/stVal | SPI | BACKUP IMPEDANCE IED UNHEALTHY | Y
11 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP | SS_BAY_HV BACKUP OC EF/LD0/LPHD1/PhyHealth/stVal | SPI | NGR BUCHHOLZ ALARM | Y | For Line Reactor NGR associated alarms | Addition
12 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | NGR BUCHHOLZ TRIP | Y |  | Addition
13 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | NGR OTI ALARM | Y |  | Addition
14 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | NGR OTI TRIP | Y |  | Addition
15 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | NGR WTI ALARM | Y |  | Addition
16 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | NGR WTI TRIP | Y |  | Addition
17 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | NGR OSR TRIP | Y |  | Addition
18 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | NGR CB ASSOCIATED ALARMS | Y | All NGC CB associated alarms to be monitored | Addition
19 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | NGR BYPASS ISOLATOR ASSOCIATED ALARMS | Y | All NGR Bypass Isolator associated alarms to be monitored | Addition
20 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | BACKUP IMPEDANCE IED UNHEALTHY | Y |  | Addition
21 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | CMD | NGR BYPASS COMMAND | Y |  | Addition
22 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | RELAY IN TEST MODE | Y |  | Addition
23 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | SETTINGS CHANGED | Y |  | Addition
24 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | DR MEMMORY 80% FULL | Y |  | Addition
25 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
26 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
27 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | SPARE ALARM-2 | Y |  | Addition
28 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | SPARE ALARM-3 | Y |  | Addition
29 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | SPARE ALARM-4 | Y |  | Addition
30 | 220kV | STNMD1Q01LRBIMP /STNMD1Q01BRBIMP |  | SPI | SPARE ALARM-5 | Y |  | Addition
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR BUSBAR PROTECTION RELAYS (DECENTRALIZED) - REB 500
| IED name: | BB_REB500_87B
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BCZ_PDIF1/DifAlm | SPI | BUSBAR CHECKZONE ALARM | Y |  | Addition
2 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BCZ_PDIF1/Op/general | SPI | BUSBAR CHECKZONE TRIP | Y |  | Addition
3 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/CALH1/GrAlm2/stVal | SPI | BUSBAR CT CIRCUIT ERROR | Y |  |  | Agreed
4 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BBP_PDIF1/Op/PhsA | SPI | BUSBAR ZONE 1 TRIP R- PHASE | Y |  | Addition, BUSBAR TRIP R- PHASE is configurable (Zone1/2/3 phasewise trip signal is not configurable)
5 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BBP_PDIF1/Op/PhsB | SPI | BUSBAR ZONE 1 TRIP Y- PHASE | Y |  | Addition, BUSBAR TRIP Y- PHASE Is configurable (Zone1/2/3 phasewise trip signal is not configurable)
6 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BBP_PDIF1/Op/PhsC | SPI | BUSBAR ZONE 1 TRIP B- PHASE | Y |  | Addition, BUSBAR TRIP B- PHASE Is configurable (Zone1/2/3 phasewise trip signal is not configurable)
7 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BBP_PDIF1/Op/general | SPI | BUSBAR ZONE 1 TRIP | Y
8 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BZ_PDIF1/Blk | SPI | BUSBAR ZONE 1 BLOCKED | Y
9 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | BREAKER FAILURE - BUSBAR 1 BLOCKED | Y |  | Addition, Need to discuss (Signal not configurable), Sig. 8 (BUSBAR ZONE 1 BLOCKED) is common blocking signal which will active when busbar blocked from external switch, Isolator intermidiate status, CT Circuit error conditions)
10 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BBP_PDIF1/DifAlm | SPI | BUSBAR ZONE-1 CT CIRCUIT ERROR | Y |  | BUSBAR CT CIRCUIT ERROR is configured in Signal No.-03 (Zone1/2/3 CT CIRCUIT signal not configurable)
11 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | BUSBAR ZONE 1 BLOCKED EXTERNAL BY SWITCH | Y
12 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BBP_PDIF2/Op/PhsA | SPI | BUSBAR ZONE 2 TRIP R- PHASE | Y |  | Addition, BUSBAR TRIP R- PHASE is configurable (Zone1/2/3 phasewise trip signal is not configurable)
13 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BBP_PDIF2/Op/PhsB | SPI | BUSBAR ZONE 2 TRIP Y- PHASE | Y |  | Addition, BUSBAR TRIP Y- PHASE Is configurable (Zone1/2/3 phasewise trip signal is not configurable)
14 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BBP_PDIF2/Op/PhsC | SPI | BUSBAR ZONE 2 TRIP B- PHASE | Y |  | Addition, BUSBAR TRIP B- PHASE Is configurable (Zone1/2/3 phasewise trip signal is not configurable)
15 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BBP_PDIF2/Op/general | SPI | BUSBAR ZONE 2 TRIP | Y
16 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BZ_PDIF2/Blk | SPI | BUSBAR ZONE 2 BLOCKED | Y
17 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | BREAKER FAILURE - BUSBAR 2 BLOCKED | Y |  | Addition, Need to discuss (Signal not configurable), Sig. 15 (BUSBAR ZONE 2 BLOCKED) is common blocking signal which will active when busbar blocked from external switch, Isolator intermidiate status, CT Circuit error conditions)
18 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BBP_PDIF2/DifAlm | SPI | BUSBAR ZONE-2 CT CIRCUIT ERROR | Y |  | BUSBAR CT CIRCUIT ERROR is configured in Signal No.-03 (Zone1/2/3 CT CIRCUIT signal not configurable)
19 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | BUSBAR ZONE 2 BLOCKED EXTERNAL BY SWITCH | Y
20 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BBP_PDIF3/Op/PhsA | SPI | BUSBAR ZONE 3 TRIP R- PHASE | Y |  | Addition, BUSBAR TRIP R- PHASE is configurable (Zone1/2/3 phasewise trip signal is not configurable)
21 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BBP_PDIF3/Op/PhsB | SPI | BUSBAR ZONE 3 TRIP Y- PHASE | Y |  | Addition, BUSBAR TRIP Y- PHASE Is configurable (Zone1/2/3 phasewise trip signal is not configurable)
22 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BBP_PDIF3/Op/PhsC | SPI | BUSBAR ZONE 3 TRIP B- PHASE | Y |  | Addition, BUSBAR TRIP B- PHASE Is configurable (Zone1/2/3 phasewise trip signal is not configurable)
23 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BBP_PDIF3/Op/general | SPI | BUSBAR ZONE 3 TRIP | Y
24 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BZ_PDIF3/Blk | SPI | BUSBAR ZONE 3 BLOCKED | Y
25 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | BREAKER FAILURE - BUSBAR 3 BLOCKED | Y |  | Addition, Need to discuss (Signal not configurable), Sig. 16 (BUSBAR ZONE 3 BLOCKED) is common blocking signal which will active when busbar blocked from external switch, Isolator intermidiate status, CT Circuit error conditions)
26 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/BBP_PDIF3/DifAlm | SPI | BUSBAR ZONE-3 CT CIRCUIT ERROR | Y |  | BUSBAR CT CIRCUIT ERROR is configured in Signal No.-03 (Zone1/2/3 CT CIRCUIT signal not configurable)
27 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | BUSBAR ZONE 3 BLOCKED EXTERNAL BY SWITCH | Y
28 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/CALH1/GrAlm1/stVal | SPI | ISOLATOR IN INTERMEDIATE STATUS | Y | TO BE USED RELATES TO STATUS OF SWITCHING ELEMENT | Addition | 0
29 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB0/BP_n/PTRC/Tr/general | SPI | BAY N TRIP | Y | For each Bays | Addition
30 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB0 n/LPHD n/PhyHealth/stVal | SPI | BUSBAR BLOCKED DUE TO COMMUNICATION ERROR_Bay_n | Y | For each Bays | Addition
31 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB0/BP_n/GAPC/Ind08/stVal | SPI | BAY_N_BREAKER FAILURE R-PH INITIATION | Y | For each Bays | Addition
32 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB0/BP_n/GAPC/Ind09/stVal | SPI | BAY_N_BREAKER FAILURE Y-PH INITIATION | Y | For each Bays | Addition
33 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB0/BP_n/GAPC/Ind10/stVal | SPI | BAY_N_BREAKER FAILURE B-PH INITIATION | Y | For each Bays | Addition
34 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB0/BP_n/GAPC/Ind11/stVal | SPI | BAY_N_BREAKER FAILURE 3PH INITIATION | Y | For each Bays | Addition
35 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB0/BP_n/GAPC/Ind04/stVal | SPI | BAY_N_EXTERNAL BUSBAR ZONE n | Y | For signals where BB tripped through External Tripping commands(GD, Half Dia) | Addition
36 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB0/BP_n/RBRF/OpIn/general | SPI | BAY_N_BREAKER FAILURE RETRIP | Y | For each Bays | Addition
37 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB0/BP_n/RBRF/OpEx/general | SPI | BAY_N_BREAKER FAILURE BACKTRIP | Y | For each Bays | Addition
38 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB0/BP_n/RBRF/OpIn/PhsA | SPI | BAY_N_BREAKER FAILURE RPH- RETRIP | Y | For each Bays | Addition
39 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB0/BP_n/RBRF/OpIn/PhsB | SPI | BAY_N_BREAKER FAILURE YPH- RETRIP | Y | For each Bays | Addition
40 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB0/BP_n/RBRF/OpIn/PhsC | SPI | BAY_N_BREAKER FAILURE BPH- RETRIP | Y | For each Bays | Addition
41 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/LPHD1/PhyHealth/stVal | SPI | BBP CENTRAL UNIT IED UNHEALTHY | Y
42 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/ABB00/GGIO1/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
43 | 220kV | STNMD1BBM1 |  | SPI | SETTINGS CHANGED | Y |  | Addition, Signal not configurable
44 | 220kV | STNMD1BBM1 |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme | Addition
45 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
46 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-2 | Y |  | Addition
47 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-3 | Y |  | Addition
48 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-4 | Y |  | Addition
49 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-5 | Y |  | Addition
50 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-6 | Y |  | Addition
51 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-7 | Y |  | Addition
52 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-8 | Y |  | Addition
53 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-9 | Y |  | Addition
54 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-10 | Y |  | Addition
55 | 220kV | STNMD1BBM1 |  | SPI | ZONE-1 AND ZONE-2 INTERCONNECTED | Y |  | Addition, Signal not configurable
56 | 220kV | STNMD1BBM1 |  | SPI | ZONE-1 AND ZONE-3 INTERCONNECTED | Y |  | Addition, Signal not configurable
57 | 220kV | STNMD1BBM1 |  | SPI | ZONE-2 AND ZONE-3 INTERCONNECTED | Y |  | Addition, Signal not configurable
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 10 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR BUSBAR PROTECTION RELAYS (CENTRALIZED) - REB 670
| IED name: | BB_REB670_87B
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/BBS/BZBSPDIF1/Op/general | SPI | BUSBAR ZONE 1 TRIP | Y | BBS - Single Phase & BBT-Three Phase Variant. STNMD1BBM1R/Y/B if phasewise Busbar IEDs are deployed.
2 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/BBS/BZBSPDIF2/Op/general | SPI | BUSBAR ZONE 2 TRIP | Y
3 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/BBS/BBSPDIF1/Op/general | SPI | BUSBAR ZONE 3 TRIP | Y
4 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/BBS/BZBSPDIF1/OpnCTAlm/stVal | SPI | BUSBAR ZONE 1 CT CIRCUIT ERROR | Y
5 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/BBS/BZBSPDIF2/OpnCTAlm/stVal | SPI | BUSBAR ZONE 2 CT CIRCUIT ERROR | Y
6 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/BBS/BBSPDIF1/OpnCTAlm/stVal | SPI | BUSBAR ZONE 3 CT CIRCUIT ERROR | Y
7 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/LD0/SP16GGIO n /Ind n/stVal | SPI | BUSBAR ZONE 1 BLOCKED EXTERNAL BY SWITCH | Y
8 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/LD0/SP16GGIO n /Ind n/stVal | SPI | BUSBAR ZONE 2 BLOCKED EXTERNAL BY SWITCH | Y
9 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/LD0/SP16GGIO n /Ind n/stVal | SPI | BUSBAR ZONE 3 BLOCKED EXTERNAL BY SWITCH | Y
10 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/LD0/SP16GGIO n /Ind n/stVal | SPI | BUSBAR ZONE 1 PROTECTION BLOCKED | Y
11 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/LD0/SP16GGIO n /Ind n/stVal | SPI | BUSBAR ZONE 2 PROTECTION BLOCKED | Y
12 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/LD0/SP16GGIO n /Ind n/stVal | SPI | BUSBAR ZONE 3 PROTECTION BLOCKED | Y
13 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/BBS6/BCZPDIF1/Op/general | SPI | BUSBAR CHECKZONE TRIP | Y
14 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/BBS/BBSPTRC n/Tr/general | SPI | BAY n TRIP | Y | **** If Bay Breaker Failure function internally utilised then BFP related Initiation, Retrip, Backtrip & other signal refered with Standalone LBB relay.
15 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/LD0/SP16GGIO n/Ind n/stVal | SPI | BAY n BREAKER FAILURE BACKUP TRIP | Y | For each bay signals to be configured and reported | Addition
16 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/LD0/SP16GGIO n/Ind n/stVal | SPI | LCC BUSBAR GAS ZONE TRIP | Y | IF Applicable for GIS | Addition
17 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
18 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/LD0/LPHD1/PhyHealth/stVal | SPI | BBP IED UNHEALTHY | Y
19 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
20 | 220kV | STNMD1BBM1 |  | SPI | SETTINGS CHANGED | Y |  | Addition
21 | 220kV | STNMD1BBM1 |  | SPI | DR MEMMORY 80% FULL | Y |  | Addition
22 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
23 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-2 | Y |  | Addition
24 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-3 | Y |  | Addition
25 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-4 | Y |  | Addition
26 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-5 | Y |  | Addition
27 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-6 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
28 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-7 | Y |  | Addition
29 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-8 | Y |  | Addition
30 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-9 | Y |  | Addition
31 | 220kV | STNMD1BBM1 |  | SPI | SPARE ALARM-10 | Y |  | Addition
32 | 220kV | STNMD1BBM1 |  | SPI | BUSBAR ZONE 1 TRIP R- PHASE | Y |  | Addition
33 | 220kV | STNMD1BBM1 |  | SPI | BUSBAR ZONE 1 TRIP Y- PHASE | Y |  | Addition
34 | 220kV | STNMD1BBM1 |  | SPI | BUSBAR ZONE 1 TRIP B- PHASE | Y |  | Addition
35 | 220kV | STNMD1BBM1 |  | SPI | BUSBAR ZONE 2 TRIP R- PHASE | Y |  | Addition
36 | 220kV | STNMD1BBM1 |  | SPI | BUSBAR ZONE 2 TRIP Y- PHASE | Y |  | Addition
37 | 220kV | STNMD1BBM1 |  | SPI | BUSBAR ZONE 2 TRIP B- PHASE | Y |  | Addition
38 | 220kV | STNMD1BBM1 |  | SPI | BUSBAR ZONE 3 TRIP R- PHASE | Y |  | Addition
39 | 220kV | STNMD1BBM1 |  | SPI | BUSBAR ZONE 3 TRIP Y- PHASE | Y |  | Addition
40 | 220kV | STNMD1BBM1 |  | SPI | BUSBAR ZONE 3 TRIP B- PHASE | Y |  | Addition
41 | 220kV | STNMD1BBM1 | SS_BAY_BUSBAR/LD0/SP16GGIO n/Ind n/stVal | SPI | ZONE-1 AND ZONE-2 INTERCONNECTED | Y |  | Addition
42 | 220kV | STNMD1BBM1 |  | SPI | ZONE-1 AND ZONE-3 INTERCONNECTED | Y |  | Addition
43 | 220kV | STNMD1BBM1 |  | SPI | ZONE-2 AND ZONE-3 INTERCONNECTED | Y |  | Addition
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 10 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR BREAKER FAILURE PROTECTION RELAY
| IED name: | R_RELAY NAME_50BFR
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILURE/LD0/GGIO n/ST/ Ind n | SPI | BREAKER FAILURE PROTECTION START | Y
2 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILURE/LD0/CCRBRF1/OpEx/general | SPI | BREAKER FAILURE BACKUP TRIP | Y |  | Text correction
3 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILURE/LD0/CCRBRF1/OpIn/general | SPI | BREAKER FAILURE RETRIP | Y
4 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILURE/LD0/CCRBRF1/OpIn/PhsA | SPI | BREAKER FAILURE RETRIP RPH | Y |  | Addition
5 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILURE/LD0/CCRBRF1/OpIn/PhsB | SPI | BREAKER FAILURE RETRIP YPH | Y |  | Addition
6 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILURE/LD0/CCRBRF1/OpIn/PhsC | SPI | BREAKER FAILURE RETRIP BPH | Y |  | Addition
7 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILURE/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
8 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILURE/LD0/LPHD1/PhyHealth/stVal | SPI | BFP IED UNHEALTHY | Y
9 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | BREAKER FAILURE R-PHASE INITIATION FROM M1/M2 | Y |  | Addition
10 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | BREAKER FAILURE Y-PHASE INITIATION FROM M1/M2 | Y |  | Addition
11 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | BREAKER FAILURE B-PHASE INITIATION FROM M1/M2 | Y |  | Addition
12 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | BREAKER FAILURE 3-PHASE INITIATION FROM 86A/86B/BB | Y |  | Addition
13 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | BREAKER FAILURE FROM LCC (If applicable) | Y | If applicable for GIS LCC | Addition
14 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | IV GR-A INT TRIP RELAY OPTD (If applicable) | Y |  | Addition
15 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | IV GR-B INT TRIP RELAY OPTD (If applicable) | Y |  | Addition
16 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
17 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | SETTINGS CHANGED | Y |  | Addition
18 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILUR/LD0/SP16GGIO n/Ind n/stVal | SPI | DR MEMMORY 80% FULL | Y |  | Addition
19 | 220kV | STNMD1Q1BFR | SS_BAY_BREAKER FAILURE/LD0/SP16GGIO n/Ind n/stVal | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
20 | 220kV | STNMD1Q1BFR |  | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
21 | 220kV | STNMD1Q1BFR |  | SPI | SPARE ALARM-2 | Y |  | Addition
22 | 220kV | STNMD1Q1BFR |  | SPI | SPARE ALARM-3 | Y |  | Addition
23 | 220kV | STNMD1Q1BFR |  | SPI | SPARE ALARM-4 | Y |  | Addition
24 | 220kV | STNMD1Q1BFR |  | SPI | SPARE ALARM-5 | Y |  | Addition
ANY ADDITIONAL SIGNAL AS PER SCHEME
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
REQUIRED SIGNALS FOR BAY CONTROL UNIT
| IED name: | R_REC670_BCU
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | ADDITIONAL REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/QCBAY1/LocSwPos/stVal | INT | BCU IN LOCAL/ REMOTE |  | *
2 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/Op/general | SPI | CLOSE COMMAND FROM BCU FOR AUTORECLOSE |  | FOR BCUs HAVING AUTORECLSOURE FUNCTION INBUILT
3 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | GR-A TRIP RELAY FAULTY | Y |  |  | Addition
4 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | GR-B TRIP RELAY FAULTY | Y |  |  | Addition
5 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | DT RECEIVE CHANNEL-1 | Y |  |  | Addition, Available in REL670 | Only for DR in REL670, for SCADA to be configured from BCU
6 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | DT RECEIVE CHANNEL-2 | Y |  |  | Addition, Available in REL670 | Only for DR in REL670, for SCADA to be configured from BCU
7 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/AutoRecSt/StVal | SPI | AUTORECLOSE FUNCTION ON | Y |  |  | Addition
8 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/AutoRecSt/StVal | SPI | AUTORECLOSE FUNCTION OFF | Y |  |  | Addition
9 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | START AUTORECLOSE FUNCTION | Y |  |  | Addition
10 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/BlkRec/stVal | SPI | BLOCK AUTORECLOSE FUNCTION | Y
11 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/Prp3PhOp/stVal | SPI | PREPARE 3PH TRIP AUTORECLOSE | Y
12 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/RdyRec/stVal | SPI | AUTORECLOSE FUNCTION READY |  |  |  | Text correction
13 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/ActRec/stVal |  | AUTORECLOSE IN PROGRESS | Y |  |  | Text correction
14 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/SucRec/stVal |  | AUTORECLOSE SUCCESSFUL | Y |  |  | Text correction
15 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SMBRREC1/UnsRec/stVal |  | AUTORECLOSE UNSUCCESSFUL | Y |  |  | Text correction
16 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SXCBR1/Pos/stVal | DPI | BAY_CB R PH POSITION
17 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SXCBR2/Pos/stVal | DPI | BAY_CB Y PH POSITION
18 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SXCBR3/Pos/stVal | DPI | BAY_CB B PH POSITION
19 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI1/Pos/stVal | DPI | BAY_CB POSITION
20 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI1/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI1/Pos/ctlOperOn for Close | CMD | BAY_CB_COMMAND |  | CLOSE / OPEN
21 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO1/EnaOpn/stVal | SPI | BAY_CB_OPEN PERMITTED OR ENABLED
22 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO1/EnaCls/stVal | SPI | BAY_CB_CLOSE PERMITTED OR ENABLED
23 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI2/Pos/stVal | DPI | BAY_89A_ISOLATOR POSITION
24 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI2/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI2/Pos/ctlOperOn for Close | CMD | BAY_89A_ISO COMMAND |  | CLOSE / OPEN
25 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO2/EnaOpn/stVal | SPI | BAY_89A_ISO OPEN PERMITTED OR ENABLED
26 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO2/EnaCls/stVal | SPI | BAY_89A_ISO CLOSE PERMITTED OR ENABLED
27 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI3/Pos/stVal | DPI | BAY_89AE_ISOLATOR POSITION
28 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI3/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI3/Pos/ctlOperOn for Close | CMD | BAY_89AE_ISO COMMAND |  | CLOSE / OPEN
29 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO3/EnaOpn/stVal | SPI | BAY_89AE_ISO OPEN PERMITTED OR ENABLED
30 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO3/EnaCls/stVal | SPI | BAY_89AE_ISO CLOSE PERMITTED OR ENABLED
31 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI4/Pos/stVal | DPI | BAY_89B_ISOLATOR POSITION
32 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI4/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI4/Pos/ctlOperOn for Close | CMD | BAY_89B_ISO COMMAND |  | CLOSE / OPEN
33 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO4/EnaOpn/stVal | SPI | BAY_89B_ISO OPEN PERMITTED OR ENABLED
34 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO4/EnaCls/stVal | SPI | BAY_89B_ISO CLOSE PERMITTED OR ENABLED
35 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI5/Pos/stVal | DPI | BAY_89AE_ISOLATOR POSITION
36 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI5/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI5/Pos/ctlOperOn for Close | CMD | BAY_89AE_ISO COMMAND |  | CLOSE / OPEN
37 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO5/EnaOpn/stVal | SPI | BAY_89AE_ISO OPEN PERMITTED OR ENABLED
38 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO5/EnaCls/stVal | SPI | BAY_89AE_ISO CLOSE PERMITTED OR ENABLED
39 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI6/Pos/stVal | DPI | BAY_89L/T/BR_ISOLATOR POSITION
40 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI6/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI6/Pos/ctlOperOn for Close | CMD | BAY_89L/T/BR_ISO COMMAND |  | CLOSE / OPEN
41 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO6/EnaOpn/stVal | SPI | BAY_89L/T/BR_ISO OPEN PERMITTED OR ENABLED
42 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO6/EnaCls/stVal | SPI | BAY_89L/T/BR_ISO CLOSE PERMITTED OR ENABLED
43 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI7/Pos/stVal | DPI | BAY_89LE/TE/BRE_ISOLATOR POSITION
44 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI7/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI7/Pos/ctlOperOn for Close | CMD | BAY_89LE/TE/BRE_ISO COMMAND |  | CLOSE / OPEN
45 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO7/EnaOpn/stVal | SPI | BAY_89LE/TE/BRE_ISO OPEN PERMITTED OR ENABLED
46 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO7/EnaCls/stVal | SPI | BAY_89LE/TE/BRE_ISO CLOSE PERMITTED OR ENABLED
47 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI8/Pos/stVal | DPI | BAY_89C_ISOLATOR POSITION
48 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI8/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI8/Pos/ctlOperOn for Close | CMD | BAY_89C_ISO COMMAND |  | CLOSE / OPEN
49 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO8/EnaOpn/stVal | SPI | BAY_89C_ISO OPEN PERMITTED OR ENABLED
50 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO8/EnaCls/stVal | SPI | BAY_89C_ISO CLOSE PERMITTED OR ENABLED
51 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI9/Pos/stVal | DPI | BAY_89AE2/BE2_ISOLATOR POSITION |  |  | USED FOR BUS EARTH SWITCH OF ISOLATOR, WHEN BUS EARTH SWITCH (89AE2/BE2) IS PROVIDED
52 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCSWI9/Pos/ctlOperOff for Open SS_BAY_BCU/LD0/SCSWI9/Pos/ctlOperOn for Close | CMD | BAY_89AE2/BE2_ISO COMMAND |  | CLOSE / OPEN
53 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO9/EnaOpn/stVal | SPI | BAY_89AE2/BE2_ISO OPEN PERMITTED OR ENABLED
54 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SCILO9/EnaCls/stVal | SPI | BAY_89AE2/BE2_ISO CLOSE PERMITTED OR ENABLED
THE LOGICAL NODE INSTANCE NUMBER (SCSWIn/SCILOn) FOR BUS EARTH SWITCHES MAY BE ASSIGNED AS PER AVAILABILITY
55 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
56 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/LPHD1/PhyHealth/stVal | SPI | BCU UNHEALTHY | Y
57 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/SES_1/SESRSYN2/Rel/stVal | SPI | CONDITIONS OK FOR SYNCHRONIZATION
58 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | SPRING DISCHARGED | Y | FOR SPRING MECHANISM CBs | ANNUNCIATION FOR CIRCUIT BREAKER
59 | 220kV | STNMD1Q01BNMBCU |  | SPI | AC MOTOR SUPPLY FAIL | Y
60 | 220kV | STNMD1Q01BNMBCU |  | SPI | SF6 GAS LOW | Y
61 | 220kV | STNMD1Q01BNMBCU |  | SPI | OPERATION LOCKED OUT | Y
62 | 220kV | STNMD1Q01BNMBCU |  | SPI | CB READY FOR AUTORECLOSURE | Y
63 | 220kV | STNMD1Q01BNMBCU |  | SPI | DC SUPPLY FAIL | Y
64 | 220kV | STNMD1Q01BNMBCU |  | SPI | TRIP RELAY 86 A FAULTY (SUPERVISION) | Y |  |  | Addition
65 | 220kV | STNMD1Q01BNMBCU |  | SPI | TRIP RELAY 86 B FAULTY (SUPERVISION) | Y |  |  | Addition
66 | 220kV | STNMD1Q01BNMBCU |  | SPI | TC-1 FAULTY R-PH | Y |  |  | Addition
67 | 220kV | STNMD1Q01BNMBCU |  | SPI | TC-1 FAULTY Y-PH | Y |  |  | Addition
68 | 220kV | STNMD1Q01BNMBCU |  | SPI | TC-1 FAULTY B-PH | Y |  |  | Addition
69 | 220kV | STNMD1Q01BNMBCU |  | SPI | TC-2 FAULTY R-PH | Y |  |  | Addition
70 | 220kV | STNMD1Q01BNMBCU |  | SPI | TC-2 FAULTY Y-PH | Y |  |  | Addition
71 | 220kV | STNMD1Q01BNMBCU |  | SPI | TC-2 FAULTY B-PH | Y |  |  | Addition
72 | 220kV | STNMD1Q01BNMBCU |  | SPI | DT RECEIVE CH-1 | Y |  |  | Available in REC670 (Sig. 5) | Agreed
73 | 220kV | STNMD1Q01BNMBCU |  | SPI | DT RECEIVE CH-2 | Y |  |  | Available in REC670 (Sig. 6) | Agreed
74 | 220kV | STNMD1Q01BNMBCU |  | SPI | CB MANUAL TRIP CMD | Y |  |  | Addition
75 | 220kV | STNMD1Q01BNMBCU |  | SPI | CB MANUAL CLOSE CMD | Y |  |  | Addition
76 | 220kV | STNMD1Q01BNMBCU |  | SPI | START A/R | Y |  |  | Addition
77 | 220kV | STNMD1Q01BNMBCU |  | SPI | BLOCK A/R | Y |  |  | Addition
78 | 220kV | STNMD1Q01BNMBCU |  | SPI | PREPARE 3PH TRIP | Y |  |  | Addition, Available in REC670 (Sig. 11) | Agreed
79 | 220kV | STNMD1Q01BNMBCU |  | SPI | BUSBAR PROTN OPTD | Y |  |  | Addition
80 | 220kV | STNMD1Q01BNMBCU |  | SPI | S.A. COUNTER R-PH | Y |  |  | Addition | As per CRP scheme will be configured in BCU/Protection relay
81 | 220kV | STNMD1Q01BNMBCU |  | SPI | S.A. COUNTER Y-PH | Y |  |  | Addition | As per CRP scheme will be configured in BCU/Protection relay
82 | 220kV | STNMD1Q01BNMBCU |  | SPI | S.A. COUNTER B-PH | Y |  |  | Addition | As per CRP scheme will be configured in BCU/Protection relay
83 | 220kV | STNMD1Q01BNMBCU |  | SPI | INCOMER DC-1 FAIL | Y |  |  | Addition
84 | 220kV | STNMD1Q01BNMBCU |  | SPI | INCOMER DC-2 FAIL | Y |  |  | Addition
85 | 220kV | STNMD1Q01BNMBCU |  | SPI | POLE DISCREPANCY RELAY OPTD | Y
86 | 220kV | STNMD1Q01BNMBCU |  | SPI | COMPRESSOR SUPPLY FAIL | Y | FOR HYDRAULLIC MECHANISM CBs
87 | 220kV | STNMD1Q01BNMBCU |  | SPI | AIR PRESSURE LOW | Y
88 | 220kV | STNMD1Q01BNMBCU |  | SPI | COMPRESSOR RUN TIME SUPERVISION | Y
89 | 220kV | STNMD1Q01BNMBCU |  | SPI | CB R-PH RECLOSE ALARM | Y |  |  | Addition
90 | 220kV | STNMD1Q01BNMBCU |  | SPI | CB Y-PH RECLOSE ALARM | Y | CSD Related Eventsf (if Applicable) |  | Addition
91 | 220kV | STNMD1Q01BNMBCU |  | SPI | CB B-PH RECLOSE ALARM | Y |  |  | Addition
92 | 220kV | STNMD1Q01BNMBCU |  | SPI | CSD OPERATION LIMIT ALARM WHEN OPENING | Y |  |  | Addition
93 | 220kV | STNMD1Q01BNMBCU |  | SPI | CSD OPERATION LIMIT ALARM WHEN CLOSING | Y |  |  | Addition
94 | 220kV | STNMD1Q01BNMBCU |  | SPI | CSD GROUP ALARM | Y |  |  | Addition
95 | 220kV | STNMD1Q01BNMBCU |  | SPI | CSD RESERVED | Y |  |  | Addition
96 | 220kV | STNMD1Q01BNMBCU |  | SPI | CSD SYNCHROTEQ IN LOCAL MODE | Y |  |  | Addition
97 | 220kV | STNMD1Q01BNMBCU |  | SPI | CSD CB INTERFACE ALARM | Y |  |  | Addition
98 | 220kV | STNMD1Q01BNMBCU |  | SPI | CSD SENSOR ALARM | Y |  |  | Addition
99 | 220kV | STNMD1Q01BNMBCU |  | SPI | CSD IN | Y |  |  | Addition
100 | 220kV | STNMD1Q01BNMBCU |  | SPI | CSD BYPASS | Y
101 | 220kV | STNMD1Q01BNMBCU |  | SPI | CSD FAIL | Y
102 | 220kV | STNMD1Q01BNMBCU |  | SPI | ICT/REACTOR-n R PH OUT OF SERVICE |  | Single phase ICT/Reactor OUT of service & Spare reactor out of service information |  | Addition
103 | 220kV | STNMD1Q01BNMBCU |  | SPI | ICT/REACTOR-n Y PH OUT OF SERVICE |  |  |  | Addition
104 | 220kV | STNMD1Q01BNMBCU |  | SPI | ICT/REACTOR-n B PH OUT OF SERVICE | Y |  |  | Addition
105 | 220kV | STNMD1Q01BNMBCU |  | SPI | ICT/Reactor- SPARE PH IN SERVICE IN ICT/Reactor-n | Y |  |  | Addition
106 | 220kV | STNMD1Q01BNMBCU |  | SPI | BUS-1 VT RESET |  | VT SELECTION FOR TRANSFORMER & REACTOR
107 | 220kV | STNMD1Q01BNMBCU |  | SPI | BUS-2 VT RESET
108 | 220kV | STNMD1Q01BNMBCU |  | SPI | LINE VT RESET
109 | 220kV | STNMD1Q01BNMBCU |  | SPI | BUS-1 VT SELECTED
110 | 220kV | STNMD1Q01BNMBCU |  | SPI | BUS-2 VT SELECTED
111 | 220kV | STNMD1Q01BNMBCU |  | SPI | LINE VTSELECTED
112 | 220kV | STNMD1Q01BNMBCU |  | SPI | GAS COMPARTMENT n Alarm Stage n | Y | Stage 1 to n as per scheme | ANNUNCIATION FOR GIS BAYS
113 | 220kV | STNMD1Q01BNMBCU |  | SPI | LCC PANEL AC SUPPLY FAIL | Y
114 | 220kV | STNMD1Q01BNMBCU |  | SPI | LCC PANEL DC SUPPLY FAIL | Y
115 | 220kV | STNMD1Q01BNMBCU |  | SPI | SELECTOR SWITCH POSITION LOCAL/REMOTE | Y
116 | 220kV | STNMD1Q01BNMBCU |  | SPI | BUS VT MCB TRIP | Y |  | FOR BCUs HAVING BUS VT INPUT
117 | 220kV | STNMD1Q01BNMBCU |  | SPI | Bay IN NORMAL |  | Applicable for Double Main Transfer Busbar system |  | Addition
118 | 220kV | STNMD1Q01BNMBCU |  | SPI | Bay IN TRANSFER |  |  |  | Addition
119 | 220kV | STNMD1Q01BNMBCU |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme |  | Addition
120 | 220kV | STNMD1Q01BNMBCU |  | SPI | RELAY IN TEST MODE | Y |  |  | Addition
121 | 220kV | STNMD1Q01BNMBCU |  | SPI | SETTINGS CHANGED | Y |  |  | Addition
122 | 220kV | STNMD1Q01BNMBCU |  | SPI | DR MEMMORY 80% FULL | Y |  |  | Addition
123 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/MON/CMMXU1/A/phsA/cVal/mag | AI | CURRENT L1 |  |  |  | Addition
124 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/MON/CMMXU1/A/phsB/cVal/mag | AI | CURRENT L2 |  |  |  | Addition
125 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/MON/CMMXU1/A/phsC/cVal/mag | AI | CURRENT L3 |  |  |  | Addition
126 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/MON/VMMXU1/PPV/phsAB/cVal/mag | AI | VOLTAGE U12 |  |  |  | Addition
127 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/MON/VMMXU1/PPV/phsBC/cVal/mag | AI | VOLTAGE U23 |  |  |  | Addition
128 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/MON/VMMXU1/PPV/phsCA/cVal/mag | AI | VOLTAGE U31 |  |  |  | Addition
129 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/MON/CVMMXN1/Watt/mag | AI | ACTIVE POWER (P) |  |  |  | Addition
130 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/MON/CVMMXN1/VolAmpr/mag | AI | REACTIVE POWER (Q) |  |  |  | Available in REC670 (Sig. 95) | Agreed
131 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/MON/CVMMXN1/PwrFact/mag | AI | POWER FACTOR (PF) |  |  |  | Available in REC670 (Sig. 95) | Agreed
132 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/MON/CVMMXN1/PwrFact/mag | AI | FREQUENCY (HZ) |  |  |  | Available in REC670 (Sig. 95) | Agreed
133 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCUMON/L4UFCNTn/CntVal/actVal | AI | S.A. COUNTER R-PH |  |  |  | Addition
134 | 220kV | STNMD1Q01BNMBCU |  | AI | S.A. COUNTER Y-PH |  |  |  | Addition
135 | 220kV | STNMD1Q01BNMBCU |  | AI | S.A. COUNTER B-PH |  |  |  | Addition
136 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/MON/MVGAPC/AnIn_n/mag | AI | TAP POSITION R PH |  |  |  | Addition
137 | 220kV | STNMD1Q01BNMBCU |  | AI | TAP POSITION Y PH |  |  |  | Addition
138 | 220kV | STNMD1Q01BNMBCU |  | AI | TAP POSITION B PH |  |  |  | Addition
139 | 220kV | STNMD1Q01BNMBCU |  | AI | WTI HV R PH |  |  |  | Addition
140 | 220kV | STNMD1Q01BNMBCU |  | AI | WTI IV R PH |  |  |  | Addition
141 | 220kV | STNMD1Q01BNMBCU |  | AI | WTI LV R PH |  |  |  | Addition
142 | 220kV | STNMD1Q01BNMBCU |  | AI | OTI R PH |  |  |  | Addition
143 | 220kV | STNMD1Q01BNMBCU |  | AI | WTI HV Y PH |  |  |  | Addition
144 | 220kV | STNMD1Q01BNMBCU |  | AI | WTI IV Y PH |  |  |  | Addition
145 | 220kV | STNMD1Q01BNMBCU |  | AI | WTI LV Y PH |  |  |  | Addition
146 | 220kV | STNMD1Q01BNMBCU |  | AI | OTI Y PH |  |  |  | Addition
147 | 220kV | STNMD1Q01BNMBCU |  | AI | WTI HV B PH |  |  |  | Addition
148 | 220kV | STNMD1Q01BNMBCU |  | AI | WTI IV B PH |  |  |  | Addition
149 | 220kV | STNMD1Q01BNMBCU |  | AI | WTI LV B PH |  |  |  | Addition
150 | 220kV | STNMD1Q01BNMBCU |  | AI | OTI B PH |  |  |  | Addition
151 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCUMON/L4UFCNTn/CntVal/actVal | AI | BREAKER R-PHASE OPERATION COUNTER |  |  |  | Addition
152 | 220kV | STNMD1Q01BNMBCU |  | AI | BREAKER Y-PHASE OPERATION COUNTER |  |  |  | Addition
153 | 220kV | STNMD1Q01BNMBCU |  | AI | BREAKER B-PHASE OPERATION COUNTER |  |  |  | Addition
154 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | RPH MOG LOW OIL LEVEL ALARM | Y |  | FOR 3Phase TRANSFORMER, INPUTS CAN BE DISTRIBUTED TO ANY IED. BUTSIGNAL SHOULD BE AS PER TRANSFORMER AVIALABLE SIGNAL | Addition
155 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH MOG LOW OIL LEVEL ALARM | Y |  |  | Addition
156 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH MOG LOW OIL LEVEL ALARM | Y |  |  | Addition
157 | 220kV | STNMD1Q01BNMBCU |  | SPI | SP-PH MOG LOW OIL LEVEL ALARM | Y |  |  | Addition
158 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH MOG HIGH OIL LEVEL ALARM | Y |  |  | Addition
159 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH MOG HIGH OIL LEVEL ALARM | Y |  |  | Addition
160 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH MOG HIGH OIL LEVEL ALARM | Y |  |  | Addition
161 | 220kV | STNMD1Q01BNMBCU |  | SPI | SP-PH MOG HIGH OIL LEVEL ALARM | Y |  |  | Addition
162 | 220kV | STNMD1Q01BNMBCU |  | SPI | R-PH OIL FLOW SENSITIVE VALVE ALARM | Y |  |  | Addition
163 | 220kV | STNMD1Q01BNMBCU |  | SPI | Y-PH OIL FLOW SENSITIVE VALVE ALARM | Y |  |  | Addition
164 | 220kV | STNMD1Q01BNMBCU |  | SPI | B-PH OIL FLOW SENSITIVE VALVE ALARM | Y |  |  | Addition
165 | 220kV | STNMD1Q01BNMBCU |  | SPI | SP-PH OIL FLOW SENSITIVE VALVE ALARM | Y |  |  | Addition
166 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH PUMP FAIL - BANK A | Y |  |  | Addition
167 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH PUMP FAIL - BANK B | Y |  |  | Addition
168 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH PUMP FAIL - BANK C | Y |  |  | Addition
169 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH PUMP FAIL - BANK D | Y |  |  | Addition
170 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH PUMP FAIL - BANK A | Y |  |  | Addition
171 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH PUMP FAIL - BANK B | Y |  |  | Addition
172 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH PUMP FAIL - BANK C | Y |  |  | Addition
173 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH PUMP FAIL - BANK D | Y |  |  | Addition
174 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH PUMP FAIL - BANK A | Y |  |  | Addition
175 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH PUMP FAIL - BANK B | Y |  |  | Addition
176 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH PUMP FAIL - BANK C | Y |  |  | Addition
177 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH PUMP FAIL - BANK D | Y |  |  | Addition
178 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH PUMP FAIL - BANK A | Y |  |  | Addition
179 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH PUMP FAIL - BANK B | Y |  |  | Addition
180 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH PUMP FAIL - BANK C | Y |  |  | Addition
181 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH PUMP FAIL - BANK D | Y |  |  | Addition
182 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH THERMAL OVERLOAD TRIP - BANK A | Y |  |  | Addition
183 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH THERMAL OVERLOAD TRIP - BANK B | Y |  |  | Addition
184 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH THERMAL OVERLOAD TRIP - BANK C | Y |  |  | Addition
185 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH THERMAL OVERLOAD TRIP - BANK D | Y |  |  | Addition
186 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH THERMAL OVERLOAD TRIP - BANK A | Y |  |  | Addition
187 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH THERMAL OVERLOAD TRIP - BANK B | Y |  |  | Addition
188 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH THERMAL OVERLOAD TRIP - BANK C | Y |  |  | Addition
189 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH THERMAL OVERLOAD TRIP - BANK D | Y |  |  | Addition
190 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH THERMAL OVERLOAD TRIP - BANK A | Y |  |  | Addition
191 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH THERMAL OVERLOAD TRIP - BANK B | Y |  |  | Addition
192 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH THERMAL OVERLOAD TRIP - BANK C | Y |  |  | Addition
193 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH THERMAL OVERLOAD TRIP - BANK D | Y |  |  | Addition
194 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH THERMAL OVERLOAD TRIP - BANK A | Y |  |  | Addition
195 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH THERMAL OVERLOAD TRIP - BANK B | Y |  |  | Addition
196 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH THERMAL OVERLOAD TRIP - BANK C | Y |  |  | Addition
197 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH THERMAL OVERLOAD TRIP - BANK D | Y |  |  | Addition
198 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH LOW OIL FLOW/REVERSE FLOW - BANK A | Y |  |  | Addition
199 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH LOW OIL FLOW/REVERSE FLOW - BANK B | Y |  |  | Addition
200 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH LOW OIL FLOW/REVERSE FLOW - BANK C | Y |  |  | Addition
201 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH LOW OIL FLOW/REVERSE FLOW - BANK D | Y |  |  | Addition
202 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH LOW OIL FLOW/REVERSE FLOW - BANK A | Y |  |  | Addition
203 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH LOW OIL FLOW/REVERSE FLOW - BANK B | Y |  |  | Addition
204 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH LOW OIL FLOW/REVERSE FLOW - BANK C | Y |  |  | Addition
205 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH LOW OIL FLOW/REVERSE FLOW - BANK D | Y |  |  | Addition
206 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH LOW OIL FLOW/REVERSE FLOW - BANK A | Y |  |  | Addition
207 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH LOW OIL FLOW/REVERSE FLOW - BANK B | Y |  |  | Addition
208 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH LOW OIL FLOW/REVERSE FLOW - BANK C | Y |  |  | Addition
209 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH LOW OIL FLOW/REVERSE FLOW - BANK D | Y |  |  | Addition
210 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH LOW OIL FLOW/REVERSE FLOW - BANK A | Y |  |  | Addition
211 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH LOW OIL FLOW/REVERSE FLOW - BANK B | Y |  |  | Addition
212 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH LOW OIL FLOW/REVERSE FLOW - BANK C | Y |  |  | Addition
213 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH LOW OIL FLOW/REVERSE FLOW - BANK D | Y |  |  | Addition
214 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH COOLER CONTROL SUPPLY FAIL | Y |  |  | Addition
215 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH COOLER CONTROL SUPPLY FAIL | Y |  |  | Addition
216 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH COOLER CONTROL SUPPLY FAIL | Y |  |  | Addition
217 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH COOLER CONTROL SUPPLY FAIL | Y |  |  | Addition
218 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH SUPPLY CHANGE OVER FAIL | Y |  |  | Addition
219 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH SUPPLY CHANGE OVER FAIL | Y |  |  | Addition
220 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH SUPPLY CHANGE OVER FAIL | Y |  |  | Addition
221 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH SUPPLY CHANGE OVER FAIL | Y |  |  | Addition
222 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH SUPPLY - A FAIL | Y |  |  | Addition
223 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH SUPPLY - A FAIL | Y |  |  | Addition
224 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH SUPPLY - A FAIL | Y |  |  | Addition
225 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH SUPPLY - A FAIL | Y |  |  | Addition
226 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH SUPPLY - B FAIL | Y |  |  | Addition
227 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH SUPPLY - B FAIL | Y |  |  | Addition
228 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH SUPPLY - B FAIL | Y |  |  | Addition
229 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH SUPPLY - B FAIL | Y |  |  | Addition
230 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH OLTC MOTOR OVERLOAD | Y |  |  | Addition
231 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH TAP CHANGE IN PROGRESS | Y |  |  | Addition
232 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH TAP CHANGE IN COMPLETE | Y |  |  | Addition
233 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH OLTC IN LOCAL | Y |  |  | Addition
234 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH OLTC IN REMOTE | Y |  |  | Addition
235 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH TAP CHANGE CONTROL SUPPLY FAIL | Y |  |  | Addition
236 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH LOWEST POSITION REACHDED | Y |  |  | Addition
237 | 220kV | STNMD1Q01BNMBCU |  | SPI | RPH HIGHESHT POSITION REACHDED | Y |  |  | Addition
238 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SPC1CGGIO n/ctlOpen | CMD | RPH OLTC RAISE COMMAND | Y |  |  | Addition
239 | 220kV | STNMD1Q01BNMBCU |  | CMD | RPH OLTC LOWER COMMAND | Y |  |  | Addition
240 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | YPH OLTC MOTOR OVERLOAD | Y |  |  | Addition
241 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH TAP CHANGE IN PROGRESS | Y |  |  | Addition
242 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH TAP CHANGE IN COMPLETE | Y |  |  | Addition
243 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH OLTC IN LOCAL | Y |  |  | Addition
244 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH OLTC IN REMOTE | Y |  |  | Addition
245 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH TAP CHANGE CONTROL SUPPLY FAIL | Y |  |  | Addition
246 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH LOWEST POSITION REACHDED | Y |  |  | Addition
247 | 220kV | STNMD1Q01BNMBCU |  | SPI | YPH HIGHESHT POSITION REACHDED | Y |  |  | Addition
248 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SPC1CGGIO n/ctlOpen | CMD | YPH OLTC RAISE COMMAND | Y |  |  | Addition
249 | 220kV | STNMD1Q01BNMBCU |  | CMD | YPH OLTC LOWER COMMAND | Y |  |  | Addition
250 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | BPH OLTC MOTOR OVERLOAD | Y |  |  | Addition
251 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH TAP CHANGE IN PROGRESS | Y |  |  | Addition
252 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH TAP CHANGE IN COMPLETE | Y |  |  | Addition
253 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH OLTC IN LOCAL | Y |  |  | Addition
254 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH OLTC IN REMOTE | Y |  |  | Addition
255 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH TAP CHANGE CONTROL SUPPLY FAIL | Y |  |  | Addition
256 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH LOWEST POSITION REACHDED | Y |  |  | Addition
257 | 220kV | STNMD1Q01BNMBCU |  | SPI | BPH HIGHESHT POSITION REACHDED | Y |  |  | Addition
258 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SPC1CGGIO n/ctlOpen | CMD | BPH OLTC RAISE COMMAND | Y |  |  | Addition
259 | 220kV | STNMD1Q01BNMBCU |  | CMD | BPH OLTC LOWER COMMAND | Y |  |  | Addition
260 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | SPH OLTC MOTOR OVERLOAD | Y |  |  | Addition
261 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH TAP CHANGE IN PROGRESS | Y |  |  | Addition
262 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH TAP CHANGE IN COMPLETE | Y |  |  | Addition
263 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH OLTC IN LOCAL | Y |  |  | Addition
264 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH OLTC IN REMOTE | Y |  |  | Addition
265 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH TAP CHANGE CONTROL SUPPLY FAIL | Y |  |  | Addition
266 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH LOWEST POSITION REACHDED | Y |  |  | Addition
267 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPH HIGHESHT POSITION REACHDED | Y |  |  | Addition
268 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SPC1CGGIO n/ctlOpen | CMD | SPH OLTC RAISE COMMAND | Y |  |  | Addition
269 | 220kV | STNMD1Q01BNMBCU |  | CMD | SPH OLTC LOWER COMMAND | Y |  |  | Addition
270 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database |  | Addition
271 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPARE ALARM-2 | Y |  |  | Addition
272 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPARE ALARM-3 | Y |  |  | Addition
273 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPARE ALARM-4 | Y |  |  | Addition
274 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPARE ALARM-5 | Y |  |  | Addition
275 | 220kV | STNMD1Q01BNMBCU | SS_BAY_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-6 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database |  | Addition
276 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPARE ALARM-7 | Y |  |  | Addition
277 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPARE ALARM-8 | Y |  |  | Addition
278 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPARE ALARM-9 | Y |  |  | Addition
279 | 220kV | STNMD1Q01BNMBCU |  | SPI | SPARE ALARM-10 | Y |  |  | Addition
ADDITIONAL SIGNAL FOR CB TROUBLE ETC AS PER SCHEME
** 10 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
NOTE 1: The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified.
NOTE 2: If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.
NOTE 3: The characters "STNM" stand for Substation Name with maximum 4 characters, this code will be given by POWERGRID for each project.
NOTE 4: The characters "Q01" stand for Bay Number, this will be vary based on Bay number eg. Q01 for BAY01, Q02 for BAY02 etc…
NOTE 5: The characters "BNM" stand for Bay Name, this will be vary based on Bay name eg. L for LINE, BR for BUSREACTOR, LR for LINEREACTOR, TIE for TIE & ICT fo ICT bay.
REQUIRED SIGNALS FOR LINE DIFFERENTAIL cum DISTANCE RELAYS
| IED name: | R_REL670_21M1
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS | HE Comments | POWERGRID Reply (Meeting on 07/12/2023)
1 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/OV2_1/OV2PTOV1/Str/general | SPI | OVERVOLATGE STAGE 1 START
2 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/OV2_1/OV2PTOV1/Op/general | SPI | OVERVOLATGE STAGE 1 TRIP | Y
3 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/OV2PTOV2/Str/general | SPI | OVER VOLTAGE STAGE-2 START | Y |  | Addition
4 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/OV2_1/OV2PTOV2/Op/general | SPI | OVERVOLATGE STAGE 2 TRIP | Y
5 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/EF4_1/EF4PTOC1/Str/general | SPI | DEF START
6 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/EF4_1/EF4PTOC1/Op/general | SPI | DEF TRIP | Y
7 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/STBPTOC1/Op/general | SPI | STUB PROTECTION OPERATED | Y | Applicable for One and Half CB Busbar system
8 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCVPSOF1/Op/general | SPI | SOTF OPERATED | Y
9 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Str/general | SPI | START, Z1
10 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/general | SPI | START, Z2
11 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsA | SPI | START, Z2 R PH
12 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsB | SPI | START, Z2 Y PH
13 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Str/phsC | SPI | START, Z2 B PH
14 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS3/Str/general | SPI | START, Z3
15 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS4/Str/general | SPI | START, Z4(REVERSE) |  | ** Whichever the zone choses as Reverse | Text correction
16 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS5/Str/general | SPI | START, Z5
17 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/general | SPI | GENERAL TRIP, Z1 | Y
18 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsA | SPI | TRIP, Z1 R PH | Y
19 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsB | SPI | TRIP, Z1 Y PH | Y
20 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCPDIS1/Op/phsC | SPI | TRIP, Z1 B PH | Y
21 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/general | SPI | GENERAL TRIP, Z2 | Y
22 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsA | SPI | TRIP, Z2 R PH | Y
23 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsB | SPI | TRIP, Z2 Y PH | Y
24 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS2/Op/phsC | SPI | TRIP, Z2 B PH | Y
25 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS3/Op/general | SPI | GENERAL TRIP, Z3 | Y
26 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS4/Op/general | SPI | GENERAL TRIP, Z4(REVERSE) | Y | ** Whichever the zone choses as Reverse | Text correction
27 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS5/Op/general | SPI | GENERAL TRIP, Z5 | Y
28 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/ProTx/stVal | SPI | CARRIER SEND | Y
29 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/ProRx/stVal | SPI | CARRIER RECEIVE | Y
30 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCPSCH1/Op/general | SPI | CARRIER AIDED SCHEME OPERATED | Y
31 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMRPSB1/Str/general | SPI | POWER SWING DETECTED | Y
32 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMRPSB1/BlkZn/stVal | SPI | POWER SWING BLOCKING | Y
33 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SMPPTRC1/Op/general | SPI | DISTANCE RELAY GENERAL TRIP | Y
34 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | R PHASE FAULT | Y |  | Addition
35 | 220kV | STNMD1Q01LM1DIF |  | SPI | Y PHASE FAULT | Y |  | Addition
36 | 220kV | STNMD1Q01LM1DIF |  | SPI | B PHASE FAULT | Y |  | Addition
37 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltDiskm/mag | DINT | FAULT LOCATOR DISTANCE
38 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltZ/cVal.mag | DINT | FAULT LOCATOR IMPEDANCE
39 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SDDRFUF1/Str/general | SPI | CVT FUSE FAIL | Y
40 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/BRCPTOC1/Op/general | SPI | BROKEN CONDUCTOR ALARM | Y
41 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | TIME SYNCHRONIZATION ERROR | Y
42 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/LPHD1/PhyHealth/stVal | SPI | M1 IED UNHEALTHY | Y
43 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | START AR TO BCU |  |  | Text correction
44 | 220kV | STNMD1Q01LM1DIF |  | SPI | BLOCK AR TO BCU |  |  | Text correction
45 | 220kV | STNMD1Q01LM1DIF |  | SPI | LINE ISOLATOR OPEN FOR STUB ACTIVATION |  | Applicable for One and Half CB Busbar system
46 | 220kV | STNMD1Q01LM1DIF |  | SPI | DT SEND CH 1 | Y
47 | 220kV | STNMD1Q01LM1DIF |  | SPI | DT SEND CH 2 | Y
48 | 220kV | STNMD1Q01LM1DIF |  | SPI | DT RECEIVE CH 1 | Y |  |  | Only for DR in RED670, for SCADA to be configured from BCU
49 | 220kV | STNMD1Q01LM1DIF |  | SPI | DT RECEIVE CH 2 | Y |  |  | Only for DR in RED670, for SCADA to be configured from BCU
50 | 220kV | STNMD1Q01LM1DIF |  | SPI | TRIP RELAY 86 A HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
51 | 220kV | STNMD1Q01LM1DIF |  | SPI | TRIP RELAY 86 B HEALTHY (SUPERVISION) | Y |  | This signal can be moved to BCU, Need to discuss | Agreed
52 | 220kV | STNMD1Q01LM1DIF |  | SPI | GR A RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RED670, for SCADA to be configured from BCU
53 | 220kV | STNMD1Q01LM1DIF |  | SPI | GR B RELAY OPERATED | Y |  | This signal can be moved to BCU, Need to discuss | Only for DR in RED670, for SCADA to be configured from BCU
54 | 220kV | STNMD1Q01LM1DIF |  | SPI | CARRIER RECEIVE CH-1 | Y
55 | 220kV | STNMD1Q01LM1DIF |  | SPI | CARRIER RECEIVE CH-2 | Y
56 | 220kV | STNMD1Q01LM1DIF |  | SPI | CARRIER CHANNEL 1 OUT OF SERVICE | Y
57 | 220kV | STNMD1Q01LM1DIF |  | SPI | CARRIER CHANNEL 2 OUT OF SERVICE | Y
58 | 220kV | STNMD1Q01LM1DIF |  | SPI | CARRIER CHANNEL 1 FAIL | Y
59 | 220kV | STNMD1Q01LM1DIF |  | SPI | CARRIER CHANNEL 2 FAIL | Y
60 | 220kV | STNMD1Q01LM1DIF |  | SPI | MAIN 2/1 RELAY FAIL | Y
61 | 220kV | STNMD1Q01LM1DIF |  | SPI | CB CLOSE COMMAND FOR SOTF INITIATION |  |  | Text correction
62 | 220kV | STNMD1Q01LM1DIF |  | SPI | BCU RELAY FAIL | Y
63 | 220kV | STNMD1Q01LM1DIF |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
64 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsA | SPI | START, Z1 R PH |  |  | Addition
65 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsB | SPI | START, Z1 Y PH |  |  | Addition
66 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZMCAPDIS1/Str/phsC | SPI | START, Z1 B PH |  |  | Addition
67 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP 3PH | Y |  | Addition
68 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP R PH | Y |  | Addition
69 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP Y PH | Y |  | Addition
70 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SMPPTRC/*** | SPI | GENERAL TRIP B PH | Y |  | Addition
71 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | PREPARE 3-PH TRIP FROM TIE BCU | Y |  | Addition, Available in BCU | It is also required in RED670
72 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | PREPARE 3-PH TRIP FROM MAIN BCU | Y |  | Addition, Available in BCU | It is also required in RED670
73 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | MAIN/ TIE CB AR OPTD | Y |  | Addition, Available in BCU | Only for DR in RED670, for SCADA to be configured from BCU
74 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | MAIN/TIE LBB PROTECTION OPERATED | Y |  | Addition, Available in BBP | Only for DR in RED670, for SCADA to be configured from LBB/BBP relay
75 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | BUSBAR M1/M2 OPTD | Y |  | Addition, Available in BBP | Only for DR in RED670, for SCADA to be configured from BBP relay
76 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | GROUP RELAY 86A OPTD | Y |  | Available in REL670 (Sig. 52) | Agreed
77 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/EchoWei/stVal | SPI | WEAK INFEED ECHO SEND | Y |  | Addition
78 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/EchoWeiOp/stVal | SPI | WEAK INFEED TRIP | Y |  | Addition
79 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/ZCRWPSCH/RvABlk/stVal | SPI | CURRENT REVERSAL DETECTED | Y |  | Addition
80 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | RELAY IN TEST MODE | Y |  | Addition
81 | 220kV | STNMD1Q01LM1DIF |  | SPI | SETTINGS CHANGED | Y |  | Addition
82 | 220kV | STNMD1Q01LM1DIF |  | SPI | DR MEMMORY 80% FULL | Y |  | Addition
83 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltDiskm/mag | AI | DISTANCE MEASUREMENT IN KM | Y |  | Available in REL670 (Sig. 37) | Agreed
84 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/LMBRFLO1/FltZ/cVal/mag | AI | DISTANCE MEASUREMENT IN IMPEDANCE | Y |  | Available in REL670 (Sig. 38) | Agreed
85 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/MON/L4UFCNTn/CntVal/actVal | AI | CH-1 Code-1 Tx (MAIN-1 CARRIER RECEIVE CHANNEL-1) |  |  | CH-1 Code-1 Tx (MAIN-1 CARRIER SEND CHANNEL-1)
86 | 220kV | STNMD1Q01LM1DIF |  | AI | CH-1 Code-1 Rx (MAIN-1 CARRIER SEND CHANNEL-1) |  |  | CH-1 Code-1 Rx (MAIN-1 CARRIER RECEIVE CHANNEL-1)
87 | 220kV | STNMD1Q01LM1DIF |  | AI | CH-1 Code-2 Tx (MAIN-2 CARRIER RECEIVE CHANNEL-1) |  |  | CH-1 Code-2 Tx (MAIN-2 CARRIER SEND CHANNEL-1)
88 | 220kV | STNMD1Q01LM1DIF |  | AI | CH-1 Code-2 Rx (MAIN-2 CARRIER SEND CHANNEL-1) |  |  | CH-1 Code-2 Rx (MAIN-2 CARRIER RECEIVE CHANNEL-1)
89 | 220kV | STNMD1Q01LM1DIF |  | AI | CH-2 Code-2 Tx (MAIN-2 CARRIER RECEIVE CHANNEL-2) |  |  | CH-2 Code-2 Tx (MAIN-2 CARRIER SEND CHANNEL-2)
90 | 220kV | STNMD1Q01LM1DIF |  | AI | CH-2 Code-2 Rx (MAIN-2 CARRIER SEND CHANNEL-2) |  |  | CH-2 Code-2 Rx (MAIN-2 CARRIER RECEIVECHANNEL-2)
91 | 220kV | STNMD1Q01LM1DIF |  | AI | CH-2 Code-1 Tx (MAIN-1 CARRIER RECEIVE CHANNEL-2) |  |  | CH-2 Code-1 Tx (MAIN-1 CARRIER SEND CHANNEL-2)
92 | 220kV | STNMD1Q01LM1DIF |  | AI | CH-2 Code-1 Rx (MAIN-1 CARRIER SEND CHANNEL-2) |  |  | CH-2 Code-1 Rx (MAIN-1 CARRIER RECEIVE CHANNEL-2)
93 | 220kV | STNMD1Q01LM1DIF |  | AI | CH-1 Code-3 Tx (DT RECEIVE CHANNEL-1) |  |  | CH-1 Code-3 Tx (DT SEND CHANNEL-1)
94 | 220kV | STNMD1Q01LM1DIF |  | AI | CH-1 Code-3 Rx (DT SEND CHANNEL-1) |  |  | CH-1 Code-3 Rx (DT RECEIVE CHANNEL-1)
95 | 220kV | STNMD1Q01LM1DIF |  | AI | CH-2 Code-3 Tx (DT RECEIVE CHANNEL-2) |  |  | CH-2 Code-3 Tx (DT SEND CHANNEL-2)
96 | 220kV | STNMD1Q01LM1DIF |  | AI | CH-2 Code-3 Rx (DT SEND CHANNEL-2) |  |  | CH-2 Code-3 Rx (DT RECEIVE CHANNEL-2)
97 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-1 | Y | ** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database | Addition
98 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-2 | Y |  | Addition
99 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-3 | Y |  | Addition
100 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-4 | Y |  | Addition
101 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DISTANCE/LD0/SP16GGIO n/Ind n/stVal | SPI | SPARE ALARM-5 | Y |  | Addition
102 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Op/general | SPI | DIFFERENTIAL PROTECTION TRIP | Y | Line Differential protection, 3 CT sets, 2-3 line ends Variant
103 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Op/general | SPI |  | Y | Line Differential protection, 6 CT sets, 3-5 line ends Variant
104 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Op/phsA | SPI | DIFFERENTIAL PROTECTION RPH TRIP | Y | Line Differential protection, 3 CT sets, 2-3 line ends Variant
105 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Op/phsA | SPI |  | Y | Line Differential protection, 6 CT sets, 3-5 line ends Variant
106 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Op/phsB | SPI | DIFFERENTIAL PROTECTION YPH TRIP | Y | Line Differential protection, 3 CT sets, 2-3 line ends Variant
107 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Op/phsB | SPI |  | Y | Line Differential protection, 6 CT sets, 3-5 line ends Variant
108 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Op/phsC | SPI | DIFFERENTIAL PROTECTION BPH TRIP | Y | Line Differential protection, 3 CT sets, 2-3 line ends Variant
109 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Op/phsC | SPI |  | Y | Line Differential protection, 6 CT sets, 3-5 line ends Variant
110 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Str/general | SPI | DIFFERENTIAL PROTECTION START |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
111 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Str/general | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
112 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Str/phsA | SPI | DIFFERENTIAL PROTECTION RPH START |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
113 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Str/phsA | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
114 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Str/phsB | SPI | DIFFERENTIAL PROTECTION YPH START |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
115 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Str/phsB | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
116 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Str/phsC | SPI | DIFFERENTIAL PROTECTION BPH START |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
117 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Str/phsC | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
102 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/OpnCTAlm/stVal | SPI | DIFFERENTIAL PROTECTION OCT ALARM |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
103 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/OpnCTAlm/stVal | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
104 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/StrRst/stVal | SPI | DIFFERENTIAL PROTECTION OPTD (RESTRAINED MODE) |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
105 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/StrRst/stVal | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
106 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/StrUnRst/stVal | SPI | DIFFERENTIAL PROTECTION OPTD (UNRESTRAINED MODE) |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant
107 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/StrUnRst/stVal | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
108 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Blk2H/stVal | SPI | DIFFERENTIAL PROTECTION 2nd HARMONIC BLOCK |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant | Applicable for Line cum Transformer bay
109 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Blk2H/stVal | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
110 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L3CPDIF4/Blk5H/stVal | SPI | DIFFERENTIAL PROTECTION 5th HARMONIC BLOCK |  | Line Differential protection, 3 CT sets, 2-3 line ends Variant | Applicable for Line cum Transformer bay
111 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/L6CPDIF2/Blk5H/stVal | SPI |  |  | Line Differential protection, 6 CT sets, 3-5 line ends Variant
112 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | DIFFERENTIAL PROTECTION COMMUNICATION FAIL
113 | 220kV | STNMD1Q01LM1DIF | SS_BAY_M1_DIFFERENTIAL/LD0/SP16GGIO n/Ind n/stVal | SPI | REMOTE END INTERTRIP RECEIVE
** 5 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
ANY ADDITIONAL SIGNAL AS PER SCHEME

## AUX SYSTEM
ABB SCADA SIGNAL LIST FOR VARIOUS PROTECTION & CONTROL SIGNALS - REV03 (AUX SYSTEM)
REQUIRED SIGNALS FOR AUX SYSTEM
| IED name: | R_REC670_BCU
SL. NO. | Voltage Level | IED name in SCD | IEC 61850 ADDRESS | TYPE | EVENT/ALARM NAME | WHETHER ALARM TO BE GENERATED | REMARKS
1 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/QCBAY1/LocSwPos/stVal | INT | BCU IN LOCAL/ REMOTE
2 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaOpn/stVal | SPI | DG_CB_OPEN PERMITTED OR ENABLED
3 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaCls/stVal | SPI | DG_CB_CLOSE PERMITTED OR ENABLED
4 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/stVal | DPI | DG_CB POSITION
5 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOff for Open SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOn for Close | CMD | DG_CB COMMAND |  | CLOSE / OPEN
6 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaOpn/stVal | SPI | MSB_INCOMER_1_CB_OPEN PERMITTED OR ENABLED
7 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaCls/stVal | SPI | MSB_INCOMER_1_CB_CLOSE PERMITTED OR ENABLED
8 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/stVal | DPI | MSB_INCOMER_1_CB POSITION
9 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOff for Open SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOn for Close | CMD | MSB_INCOMER_1_CB COMMAND |  | CLOSE / OPEN
10 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaOpn/stVal | SPI | MSB_INCOMER_2_CB_OPEN PERMITTED OR ENABLED
11 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaCls/stVal | SPI | MSB_INCOMER_2_CB_CLOSE PERMITTED OR ENABLED
12 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/stVal | DPI | MSB_INCOMER_2_CB POSITION
13 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOff for Open SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOn for Close | CMD | MSB_INCOMER_2_CB COMMAND |  | CLOSE / OPEN
14 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaOpn/stVal | SPI | MSB_BUSCOUPLER_CB_OPEN PERMITTED OR ENABLED
15 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaCls/stVal | SPI | MSB_BUSCOUPLER_CB_CLOSE PERMITTED OR ENABLED
16 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/stVal | DPI | MSB_BUSCOUPLER_CB POSITION
17 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOff for Open SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOn for Close | CMD | MSB_BUSCOUPLER_CB COMMAND |  | CLOSE / OPEN
18 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaOpn/stVal | SPI | ACDB_INCOMER_1_CB_OPEN PERMITTED OR ENABLED
19 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaCls/stVal | SPI | ACDB_INCOMER_1_CB_CLOSE PERMITTED OR ENABLED
20 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/stVal | DPI | ACDB_INCOMER_1_CB POSITION
21 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOff for Open SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOn for Close | CMD | ACDB_INCOMER_1_CB COMMAND |  | CLOSE / OPEN
22 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaOpn/stVal | SPI | ACDB_INCOMER_2_CB_OPEN PERMITTED OR ENABLED
23 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaCls/stVal | SPI | ACDB_INCOMER_2_CB_CLOSE PERMITTED OR ENABLED
24 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/stVal | DPI | ACDB_INCOMER_2_CB POSITION
25 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOff for Open SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOn for Close | CMD | ACDB_INCOMER_2_CB COMMAND |  | CLOSE / OPEN
26 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaOpn/stVal | SPI | ACDB_BUSCOPULER_CB_OPEN PERMITTED OR ENABLED
27 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaCls/stVal | SPI | ACDB_BUSCOPULER_CB_CLOSE PERMITTED OR ENABLED
28 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/stVal | DPI | ACDB_BUSCOPULER_CB POSITION
29 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOff for Open SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOn for Close | CMD | ACDB_BUSCOPULER_CB COMMAND |  | CLOSE / OPEN
30 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaOpn/stVal | SPI | HVW_MOTOR_CB_OPEN PERMITTED OR ENABLED
31 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaCls/stVal | SPI | HVW_MOTOR_CB_CLOSE PERMITTED OR ENABLED
32 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/stVal | DPI | HVW_MOTOR_CB_ POSITION
33 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOff for Open SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOn for Close | CMD | HVW_MOTOR_CB_ COMMAND |  | CLOSE / OPEN
34 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaOpn/stVal | SPI | SEB_33kV_CB_OPEN PERMITTED OR ENABLED
35 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaCls/stVal | SPI | SEB_33kV_CB_CLOSE PERMITTED OR ENABLED
36 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/stVal | DPI | SEB_33kV_CB_ POSITION
37 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOff for Open SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOn for Close | CMD | SEB_33kV_CB_ COMMAND |  | CLOSE / OPEN
38 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaOpn/stVal | SPI | SEB_33kV_ISOLATOR_OPEN PERMITTED OR ENABLED
39 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaCls/stVal | SPI | SEB_33kV_ISOLATOR_CLOSE PERMITTED OR ENABLED
40 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/stVal | DPI | SEB_33kV_ISOLATOR_ POSITION
41 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOff for Open SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOn for Close | CMD | SEB_33kV_ISOLATOR_ COMMAND |  | CLOSE / OPEN
42 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaOpn/stVal | SPI | TERTIARY TRAFO_33kV_CB_OPEN PERMITTED OR ENABLED |  | If the inputs taken in Respecetive ICT Protection/BCU these signals may be omitted.
43 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaCls/stVal | SPI | TERTIARY TRAFO_33kV_CB_CLOSE PERMITTED OR ENABLED
44 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/stVal | DPI | TERTIARY TRAFO_33kV_CB_ POSITION
45 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOff for Open SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOn for Close | CMD | TERTIARY TRAFO_33kV_CB_ COMMAND
46 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaOpn/stVal | SPI | TERTIARY TRAFO_33kV_ISOLATOR_OPEN PERMITTED OR ENABLED
47 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCILOn/EnaCls/stVal | SPI | TERTIARY TRAFO_33kV_ISOLATOR_CLOSE PERMITTED OR ENABLED
48 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/stVal | DPI | TERTIARY TRAFO_33kV_ISOLATOR_ POSITION
49 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOff for Open SS_AUX_BCU/LD0/SCSWIn/Pos/ctlOperOn for Close | CMD | TERTIARY TRAFO_33kV_ISOLATOR_ COMMAND
THE LOGICAL NODE INSTANCE NUMBER (SCSWIn/SCILOn) FOR BBREAKERS MAY BE ASSIGNED AS PER AVAILABILITY
50 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CMMXUn/A/phsA/cVal/mag | AI | DG INCOMER CURRENT L1
51 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CMMXUn/A/phsB/cVal/mag | AI | DG INCOMER CURRENT L2
52 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CMMXUn/A/phsC/cVal/mag | AI | DG INCOMER CURRENT L3
53 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/VMMXUn/PPV/phsAB/cVal/mag | AI | DG INCOMER VOLTAGE U12
54 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/VMMXUn/PPV/phsBC/cVal/mag | AI | DG INCOMER VOLTAGE U23
55 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/VMMXUn/PPV/phsCA/cVal/mag | AI | DG INCOMER VOLTAGE U31
56 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CVMMXNn/Watt/mag | AI | DG INCOMER ACTIVE POWER (P)
57 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CVMMXNn/VolAmpr/mag | AI | DG INCOMER REACTIVE POWER (Q)
58 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CVMMXNn/PwrFact/mag | AI | DG INCOMER POWER FACTOR (PF)
59 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CVMMXNn/PwrFact/mag | AI | DG INCOMER FREQUENCY (HZ)
60 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CMMXUn/A/phsA/cVal/mag | AI | MSB INCOMER-1 CURRENT L1
61 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CMMXUn/A/phsB/cVal/mag | AI | MSB INCOMER-1 CURRENT L2
62 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CMMXUn/A/phsC/cVal/mag | AI | MSB INCOMER-1 CURRENT L3
63 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/VMMXUn/PPV/phsAB/cVal/mag | AI | MSB INCOMER-1 VOLTAGE U12
64 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/VMMXUn/PPV/phsBC/cVal/mag | AI | MSB INCOMER-1 VOLTAGE U23
65 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/VMMXUn/PPV/phsCA/cVal/mag | AI | MSB INCOMER-1 VOLTAGE U31
66 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CVMMXNn/Watt/mag | AI | MSB INCOMER-1 ACTIVE POWER (P)
67 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CVMMXNn/VolAmpr/mag | AI | MSB INCOMER-1 REACTIVE POWER (Q)
68 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CVMMXNn/PwrFact/mag | AI | MSB INCOMER-1 POWER FACTOR (PF)
69 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CVMMXNn/PwrFact/mag | AI | MSB INCOMER-1 FREQUENCY (HZ)
70 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CMMXUn/A/phsA/cVal/mag | AI | MSB INCOMER-2 CURRENT L1
71 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CMMXUn/A/phsB/cVal/mag | AI | MSB INCOMER-2 CURRENT L2
72 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CMMXUn/A/phsC/cVal/mag | AI | MSB INCOMER-2 CURRENT L3
73 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/VMMXUn/PPV/phsAB/cVal/mag | AI | MSB INCOMER-2 VOLTAGE U12
74 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/VMMXUn/PPV/phsBC/cVal/mag | AI | MSB INCOMER-2 VOLTAGE U23
75 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/VMMXUn/PPV/phsCA/cVal/mag | AI | MSB INCOMER-2 VOLTAGE U31
76 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CVMMXNn/Watt/mag | AI | MSB INCOMER-2 ACTIVE POWER (P)
77 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CVMMXNn/VolAmpr/mag | AI | MSB INCOMER-2 REACTIVE POWER (Q)
78 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CVMMXNn/PwrFact/mag | AI | MSB INCOMER-2 POWER FACTOR (PF)
79 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/CVMMXNn/PwrFact/mag | AI | MSB INCOMER-2 FREQUENCY (HZ)
80 | 415V | STNMN1AUXBCU | SS_AUX_BCU/MON/MVGAPC/AnIn_n/mag | AI | 220V CHARGER 1 CURRENT
81 | 415V | STNMN1AUXBCU |  | AI | 220V CHARGER 2 CURRENT
82 | 415V | STNMN1AUXBCU |  | AI | 48V CHARGER 1 CURRENT
83 | 415V | STNMN1AUXBCU |  | AI | 48V CHARGER 2 CURRENT
84 | 415V | STNMN1AUXBCU |  | AI | 220V DCDB 1 VOLTAGE
85 | 415V | STNMN1AUXBCU |  | AI | 220V DCDB 1 CURRENT
86 | 415V | STNMN1AUXBCU |  | AI | 220V DCDB 2 VOLTAGE
87 | 415V | STNMN1AUXBCU |  | AI | 220V DCDB 2 CURRENT
88 | 415V | STNMN1AUXBCU |  | AI | 48V DCDB 1 VOLTAGE
89 | 415V | STNMN1AUXBCU |  | AI | 48V DCDB 1 CURRENT
90 | 415V | STNMN1AUXBCU |  | AI | 48V DCDB 2 VOLTAGE
91 | 415V | STNMN1AUXBCU |  | AI | 48V DCDB 2 CURRENT
92 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | 220V CHARGER-1 ON FLOAT MODE
93 | 415V | STNMN1AUXBCU |  | SPI | 220V CHARGER-1 ON BOAST MODE
94 | 415V | STNMN1AUXBCU |  | SPI | 220V CHARGER 1 TROUBLE | Y | CLOSE / OPEN
95 | 415V | STNMN1AUXBCU |  | SPI | 220V DCDB-1 EARTH FAULT OPTD | Y
96 | 415V | STNMN1AUXBCU |  | SPI | 220V CHARGER-2 ON FLOAT MODE
97 | 415V | STNMN1AUXBCU |  | SPI | 220V CHARGER-2 ON BOAST MODE
98 | 415V | STNMN1AUXBCU |  | SPI | 220V CHARGER 2 TROUBLE | Y
99 | 415V | STNMN1AUXBCU |  | SPI | 220V DCDB-2 EARTH FAULT OPTD | Y
100 | 415V | STNMN1AUXBCU |  | SPI | 48V CHARGER-1 ON FLOAT MODE |  | CLOSE / OPEN
101 | 415V | STNMN1AUXBCU |  | SPI | 48V CHARGER-1 ON BOAST MODE
102 | 415V | STNMN1AUXBCU |  | SPI | 48V CHARGER 1 TROUBLE | Y
103 | 415V | STNMN1AUXBCU |  | SPI | 48V CHARGER-2 ON FLOAT MODE
104 | 415V | STNMN1AUXBCU |  | SPI | 48V CHARGER-2 ON BOAST MODE |  | CLOSE / OPEN
105 | 415V | STNMN1AUXBCU |  | SPI | 48V CHARGER 2 TROUBLE | Y
106 | 415V | STNMN1AUXBCU |  | SPI | 415V INCOMER-1 UNDERVOLTAGE | Y
107 | 415V | STNMN1AUXBCU |  | SPI | 415V INCOMER-2 UNDERVOLTAGE | Y | CLOSE / OPEN
108 | 415V | STNMN1AUXBCU |  | SPI | SEB TRAFO - BUCHHOLZ ALARM | Y
109 | 415V | STNMN1AUXBCU |  | SPI | SEB TRAFO - BUCHHOLZ TRIP | Y
110 | 415V | STNMN1AUXBCU |  | SPI | SEB TRAFO - WTI ALARM | Y
111 | 415V | STNMN1AUXBCU |  | SPI | SEB TRAFO - WTI TRIP | Y
112 | 415V | STNMN1AUXBCU |  | SPI | SEB TRAFO - OTI ALARM | Y
113 | 415V | STNMN1AUXBCU |  | SPI | SEB TRAFO - OTI TRIP | Y
114 | 415V | STNMN1AUXBCU |  | SPI | SEB TRAFO - PRD ALARM | Y
115 | 415V | STNMN1AUXBCU |  | SPI | SEB TRAFO - PRD TRIP | Y
116 | 415V | STNMN1AUXBCU |  | SPI | SEB 33KV_TC-1 FAULTY | Y
117 | 415V | STNMN1AUXBCU |  | SPI | SEB 33KV_TC-2 FAULTY | Y
118 | 415V | STNMN1AUXBCU | SS_AUX_BCU/OC4_1/OC4PTOC1/Str/general | SPI | SEB 33kV PHASE OVERCURRENT START | Y
119 | 415V | STNMN1AUXBCU | SS_AUX_BCU/OC4_1/OC4PTOC1/Op/general | SPI | SEB33kV PHASE OVERCURRENT TRIP | Y
120 | 415V | STNMN1AUXBCU | SS_AUX_BCU/EF4_1/EF4PTOC1/Str/general | SPI | SEB 33kV PHASE EARTHFAULT START | Y
121 | 415V | STNMN1AUXBCU | SS_AUX_BCU/EF4_1/EF4PTOC1/Op/general | SPI | SEB 33kV PHASE EARTHFAULT TRIP | Y
122 | 415V | STNMN1AUXBCU | SS_AUX_BCU/ROV2_1/ROV2PTOV1/Str/general | SPI | SEB 33kV PHASE RESIDUAL OVERVOLTAGE START | Y
123 | 415V | STNMN1AUXBCU | SS_AUX_BCU/ROV2_1/ROV2PTOV1/OP/general | SPI | SEB 33kV PHASE RESIDUAL OVERVOLTAGE TRIP | Y
124 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | SEB 33kV 86 OPTD | Y
125 | 415V | STNMN1AUXBCU |  | SPI | SEB 33kV CB ASSOCIATED ALARMS | Y
126 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO - BUCHHOLZ ALARM | Y | If the inputs taken in Respecetive ICT Protection/BCU these signals may be omitted.
127 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO - BUCHHOLZ TRIP | Y
128 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO - WTI ALARM | Y
129 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO - WTI TRIP | Y
130 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO - OTI ALARM | Y
131 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO - OTI TRIP | Y
132 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO - PRD ALARM | Y
133 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY TRAFO - PRD TRIP | Y
134 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY 33KV_TC-1 FAULTY | Y
135 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY 33KV_TC-2 FAULTY | Y
136 | 415V | STNMN1AUXBCU | SS_AUX_BCU/OC4_1/OC4PTOC2/Str/general | SPI | TERTIARY 33kV PHASE OVERCURRENT START | Y
137 | 415V | STNMN1AUXBCU | SS_AUX_BCU/OC4_1/OC4PTOC2/Op/general | SPI | TERTIARY33kV PHASE OVERCURRENT TRIP | Y
138 | 415V | STNMN1AUXBCU | SS_AUX_BCU/EF4_1/EF4PTOC2/Str/general | SPI | TERTIARY 33kV PHASE EARTHFAULT START | Y
139 | 415V | STNMN1AUXBCU | SS_AUX_BCU/EF4_1/EF4PTOC2/Op/general | SPI | TERTIARY 33kV PHASE EARTHFAULT TRIP | Y
140 | 415V | STNMN1AUXBCU | SS_AUX_BCU/ROV2_1/ROV2PTOV2/Str/general | SPI | TERTIARY 33kV PHASE RESIDUAL OVERVOLTAGE START | Y
141 | 415V | STNMN1AUXBCU | SS_AUX_BCU/ROV2_1/ROV2PTOV2/OP/general | SPI | TERTIARY 33kV PHASE RESIDUAL OVERVOLTAGE TRIP | Y
142 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | TERTIARY 33kV 86 OPTD | Y
143 | 415V | STNMN1AUXBCU |  | SPI | TERTIARY 33kV CB ASSOCIATED ALARMS | Y
144 | 415V | STNMN1AUXBCU |  | SPI | AUX INCOMER DC-1 FAULTY | Y
145 | 415V | STNMN1AUXBCU |  | SPI | AUX INCOMER DC-2 FAULTY | Y
146 | 415V | STNMN1AUXBCU |  | SPI | WATER STORAGE TANK-1 LEVEL LOW | Y
147 | 415V | STNMN1AUXBCU |  | SPI | WATER STORAGE TANK-2 LEVEL LOW | Y
148 | 415V | STNMN1AUXBCU |  | SPI | HVW MOTOR DRIVEN PUMP RUNNING
149 | 415V | STNMN1AUXBCU |  | SPI | HVW MOTOR DRIVEN PUMP FAILS TO START | Y
150 | 415V | STNMN1AUXBCU |  | SPI | HVW MOTOR PUMP TRIP FEEDBACK | Y
151 | 415V | STNMN1AUXBCU |  | SPI | DIESEL ENGINE RUNNING
152 | 415V | STNMN1AUXBCU |  | SPI | DIESEL ENGINE FAILS TO START | Y
153 | 415V | STNMN1AUXBCU |  | SPI | DIESEL ENGINE TANK LEVEL LOW | Y
154 | 415V | STNMN1AUXBCU |  | SPI | JOCKEY PUMP -1 RUNNING
155 | 415V | STNMN1AUXBCU |  | SPI | JOCKEY PUMP -2 RUNNING
156 | 415V | STNMN1AUXBCU |  | SPI | JOCKEY PUMP -1 FAILS TO START | Y
157 | 415V | STNMN1AUXBCU |  | SPI | JOCKEY PUMP -2 FAILS TO START | Y
158 | 415V | STNMN1AUXBCU |  | SPI | JOCKEY PUMP O/L TRIP | Y
159 | 415V | STNMN1AUXBCU |  | SPI | JOCKEY PUMP PANEL DC HEALTHY | Y
160 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SPC8GAPCn/SPCSOn/ctlOper | CMD | HVW MOTORT START
161 | 415V | STNMN1AUXBCU |  | CMD | HVW MOTORT STOP
162 | 415V | STNMN1AUXBCU |  | CMD | DIESEL ENGINE START
163 | 415V | STNMN1AUXBCU |  | CMD | DIESEL ENGINE STOP
164 | 415V | STNMN1AUXBCU |  | CMD | JOCKEY PUMP-1 START
165 | 415V | STNMN1AUXBCU |  | CMD | JOCKEY PUMP-1 STOP
166 | 415V | STNMN1AUXBCU |  | CMD | JOCKEY PUMP-2 START
167 | 415V | STNMN1AUXBCU |  | CMD | JOCKEY PUMP-2 STOP
168 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | FIRE IN ZONE -1 | Y
169 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN ZONE -2 | Y
170 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN ZONE -3 | Y
171 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN ZONE -4 | Y
172 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN ZONE -5 | Y
173 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN ZONE -N | Y
174 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN TRANSFORMER-1 | Y | If the inputs taken in Respecetive ICT Protection/BCU these signals may be omitted.
175 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN TRANSFORMER-2 | Y
176 | 415V | STNMN1AUXBCU |  | SPI | FIRE IN TRANSFORMER-N | Y
177 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SPC8GAPCn/SPCSOn/ctlOper | CMD | DELUGE COMMAND TO TRANSFORMER-1
178 | 415V | STNMN1AUXBCU |  | CMD | DELUGE COMMAND TO TRANSFORMER-2
179 | 415V | STNMN1AUXBCU |  | CMD | DELUGE COMMAND TO TRANSFORMER-N
180 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | DG DIFFERENTIAL PROT TRIP | Y
181 | 415V | STNMN1AUXBCU |  | SPI | DG OC/EF PROT TRIP | Y
182 | 415V | STNMN1AUXBCU |  | SPI | DG FAIL TO START | Y
183 | 415V | STNMN1AUXBCU |  | SPI | ALTERNATOR ON
184 | 415V | STNMN1AUXBCU |  | SPI | DG LUBE OIL LOW PRESSURE ALARM | Y
185 | 415V | STNMN1AUXBCU |  | SPI | HIGH WATER TEMP TRIP | Y | CLOSE / OPEN
186 | 415V | STNMN1AUXBCU |  | SPI | ENGG. COM FAULT | Y
187 | 415V | STNMN1AUXBCU |  | SPI | LACK OF FUEL ALARM | Y
188 | 415V | STNMN1AUXBCU |  | SPI | DG CHARGER-1 ON
189 | 415V | STNMN1AUXBCU |  | SPI | DG CHARGER-1 OFF | Y | CLOSE / OPEN
190 | 415V | STNMN1AUXBCU |  | SPI | DG CHARGER-2 ON
191 | 415V | STNMN1AUXBCU |  | SPI | DG CHARGER-2 OFF | Y
192 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SPC8GAPCn/SPCSO1/ctlOper | CMD | DG START/STOP COMMAND |  | CLOSE / OPEN
193 | 415V | STNMN1AUXBCU | SS_AUX_BCU/LD0/SP16GGIO n/Ind n/stVal | SPI | AUX INCOMER DC-1 FAULTY | Y
194 | 415V | STNMN1AUXBCU |  | SPI | AUX INCOMER DC-2 FAULTY | Y
195 | 415V | STNMN1AUXBCU |  | SPI | TIME SYNCHRONIZATION ERROR | Y
196 | 415V | STNMN1AUXBCU |  | SPI | BCU UNHEALTHY | Y
197 | 415V | STNMN1AUXBCU |  | SPI | GOOSE RECEIPT FAIL/TROUBLE | Y | Only if the IED subscriber to GOOSE messgaes as per the scheme
198 | 415V | STNMN1AUXBCU |  | SPI | RELAY IN TEST MODE | Y
199 | 415V | STNMN1AUXBCU |  | SPI | SETTINGS CHANGED | Y
200 | 415V | STNMN1AUXBCU |  | SPI | DR MEMMORY 80% FULL | Y
201 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-1 |  | ** 20 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database
202 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-2
203 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-3
204 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-4
205 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-5
206 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-6
207 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-7
208 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-8
209 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-9
210 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-10
211 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-11
212 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-12
213 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-13
214 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-14
215 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-15
216 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-16
217 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-17
218 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-18
219 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-19
220 | 415V | STNMN1AUXBCU |  | SPI | SPARE ALARM-20
ADDITIONAL SIGNAL FOR CB TROUBLE ETC AS PER SCHEME
** 20 Nos of SP16GGIO signal need to be configured as SPARE till the SCADA Database