## LEGEND
SIEMENS SCADA GENERAL SIGNAL LIST FOR VARIOUS PROTECTION & CONTROL SIGNALS - REV03 (INDEX)
Sheet Ref. | IED MODEL | IED SYMBOLIC NAME(TYPICAL) | APPLICATION | IED NAME IN SCD | Additional Remarks
1 | 6MD66 | BCU | LINE BCU | STNM7XXLBCU | BCU is for each bay so 7XX refers to Bay
2 | 7SA522 | 7SA522_21M1 | LINE DISTANCE MAIN-1 | STNM7XXL21M1 | Bay No. 7XX will be always the main bay number for the ICT feeder
3 | 7SD522 | 7SD522_87M1 | LINE DIFFERENTIAL/DISTANCE MAIN-2 | STNM7XXL87M1 | Bay No. 7XX will be always the main bay number for the ICT feeder
NOTE 1: The characters "STNM" stand for Substation Name with maximum 4 characters, this code will be given by POWERGRID for each project.
NOTE 2: The characters "7XX" stand for Bay name, example if the bay no 701 then same has to be implemented like STNM701BCU

## BCU
765kV LINE
Sr. No. | Voltage Level | Feeder Name
|  |  | SIGNAL DESCRIPTION | INFORMATION TYPE | Telegram Address | POSITION | EVENT | ALARM
BINARY INPUT (Double Point)
1 | 765kV | 765kV LINE | CB B-PH POSITION | DP | B706_BCUCBB$XCBR1$ST$Pos:2 | stVal | √
2 |  |  | CB R-PH POSITION | DP | B706_BCUCBR$XCBR1$ST$Pos:2 | stVal | √
3 |  |  | CB Y-PH POSITION | DP | B706_BCUCBY$XCBR1$ST$Pos:2 | stVal | √
4 |  |  | CB POSITION | DP | B706_BCUCB$CSWI1$ST$Pos:2 | stVal | √
5 |  |  | 89AE1 POSITION | DP | B706_BCU89AE1$CSWI3$ST$Pos:2 | stVal | √
6 |  |  | 89AE2 POSITION | DP | B706_BCU89AE2$CSWI8$ST$Pos:2 | stVal | √
7 |  |  | 89BE POSITION | DP | B706_BCU89BE$CSWI5$ST$Pos:2 | stVal | √
8 |  |  | 89A POSITION | DP | B706_BCU89A$CSWI2$ST$Pos:2 | stVal | √
9 |  |  | 89B POSITION | DP | B706_BCU89B$CSWI4$ST$Pos:2 | stVal | √
10 |  |  | 89L POSITION | DP | B706_BCU89L$CSWI6$ST$Pos:2 | stVal | √
11 |  |  | 89LE POSITION | DP | B706_BCU89LE$CSWI7$ST$Pos:2 | stVal | √
12 |  |  | 89 BE1 POSITION
13 |  |  | 89 BE2 POSITION
14 |  |  | THE LOGICAL NODE FOR BUS EARTH SWITCHES, ISOLATOR & EARTHSWITCHES FOR 3 PH/1PH REACTORS & ITCs, e.g 89 BR, BRE, LR, LRE, RS1, RS2, RS1E, 89T,TE, 89AE2, 89BE2 MAY BE ASSIGNED AS PER AVAILABILITY/SCHEME
15 |  |  | BINARY INPUT (Single Point)
16
17 |  |  | AUX POWER FAIL | SP | B706_BCUApplication$LPHD0$ST$AuxPwrFail | stVal | √ | √
18 |  |  | TIME SYNCHRONISATION ERROR | SP | B706_BCUApplication$LMTS0$ST$TmSynErr | stVal | √ | √
19 |  |  | BCU MODE | SP | B706_BCUApplication$LLN0$ST$LocKey | stVal | √
20 |  |  | BCU LOCAL
21 |  |  | BCU REMOTE
22 |  |  | CT SF6 GAS PRESSURE REFILL LOW ALARM | SP | B706_BCUApplication$USER1$ST$SPS | stVal | √ | √
23 |  |  | CT SF6 GAS PRESSURE LOCKOUT | SP | B706_BCUApplication$USER1$ST$SPS1 | stVal | √ | √
24 |  |  | TRIP RELAY SUPERVISION | SP | B706_BCUApplication$USER5$ST$SPS | stVal | √ | √
25 |  |  | CARRIER CHANNEL-2 OUT | SP | B706_BCUApplication$USER5$ST$SPS1 | stVal | √ | √
26 |  |  | MAIN-2 RELAY FAULTY | SP | B706_BCUApplication$USER5$ST$SPS2 | stVal | √ | √
27 |  |  | EMERGENCY/MANUAL TRIP | SP | B706_BCUApplication$USER5$ST$SPS4 | stVal | √ | √
28 |  |  | SPEECH CHANNEL FAIL | SP | B706_BCUApplication$USER5$ST$SPS3 | stVal | √ | √
29 |  |  | SURGE ARRESTER B-PH | SP | B706_BCUApplication$USER5$ST$SPS7 | stVal | √ | √
30 |  |  | SURGE ARRESTER R-PH | SP | B706_BCUApplication$USER5$ST$SPS5 | stVal | √ | √
31 |  |  | SURGE ARRESTER Y-PH | SP | B706_BCUApplication$USER5$ST$SPS6 | stVal | √ | √
32 |  |  | 89A POLE DESCREPENCY | SP | B706_BCUApplication$USER3$ST$SPS5 | stVal | √ | √
33 |  |  | 89B POLE DESCREPENCY | SP | B706_BCUApplication$USER3$ST$SPS6 | stVal | √ | √
34 |  |  | CB DC SUPPLY-1/2 FAIL | SP | B706_BCUApplication$USER3$ST$SPS1 | stVal | √ | √
35 |  |  | CB SPRING NOT CHARGED B-PH | SP | B706_BCUApplication$USER3$ST$SPS4 | stVal | √ | √
36 |  |  | CB SPRING NOT CHARGED R-PH | SP | B706_BCUApplication$USER3$ST$SPS2 | stVal | √ | √
37 |  |  | CB SPRING NOT CHARGED Y-PH | SP | B706_BCUApplication$USER3$ST$SPS3 | stVal | √ | √
38 |  |  | CB SF6 GAS PRESSURE LOCKOUT | SP | B706_BCUApplication$USER3$ST$SPS | stVal | √ | √
39 |  |  | 86B TRIP RELAY FAULTY | SP | B706_BCUApplication$USER4$ST$SPS3 | stVal | √ | √
40 |  |  | 86A TRIP RELAY FAULTY | SP | B706_BCUApplication$USER4$ST$SPS3 | stVal | √ | √
41 |  |  | 86A TRIP RELAY OPERATED | SP | B706_BCUApplication$USER4$ST$SPS2 | stVal | √ | √
42 |  |  | 86B TRIP RELAY OPERATED | SP | B706_BCUApplication$USER4$ST$SPS6 | stVal | √ | √
43 |  |  | 89L POLE DESCREPENCY | SP | B706_BCUApplication$USER4$ST$SPS | stVal | √ | √
44 |  |  | CARRIER CHANNEL-1 OUT | SP | B706_BCUApplication$USER4$ST$SPS4 | stVal | √ | √
45 |  |  | CB TC-1 FAULTY | SP | B706_BCUApplication$USER4$ST$SPS1 | stVal | √ | √
46 |  |  | CB TC-2 FAULTY | SP | B706_BCUApplication$USER4$ST$SPS5 | stVal | √ | √
47 |  |  | CB POLE DESCREPENCY OPTD-1
48 |  |  | CB POLE DESCREPENCY OPTD-2 | SP | B706_BCUApplication$USER2$ST$SPS1 | stVal | √ | √
49 |  |  | CB SF6 GAS PRESSURE REFILL LOW ALARM | SP | B706_BCUApplication$USER2$ST$SPS | stVal | √ | √
50 |  |  | BUS-1 VT SELECTED | SP | B706_BCUApplication$USER6$ST$SPS1 | stVal | √
51 |  |  | ICT LV VT SELECTED | SP | B706_BCUApplication$USER6$ST$SPS2 | stVal | √
52 |  |  | LINE VT SELECTED | SP | B706_BCUApplication$USER6$ST$SPS | stVal | √
53 |  |  | CB READY | SP | B706_BCUCB$XCBR1$ST$Rdy | stVal | √
54 |  |  | EMERGENCY/MANUAL CB CLOSE | SP | B706_BCUCB$GAPC2$ST$Detected | stVal | √
55 |  |  | DEVICE HEALTHY | SP | B706_BCUApplication$LPHD0$ST$PhyHealth:0 | stVal:1 | √
56 |  |  | CB POSITION NO SYNC | SP | B706_BCUCB$CSWI1$ST$Pos | noSync | √ | √
57 |  |  | CB CLOSE INTERLOCK | SP | B706_BCUCB$CILO1$ST$EnaCls | stVal | √ | √
58 | 765kV | 765kV LINE | 89AE1 OPEN INTERLOCK | SP | B706_BCU89AE1$CILO3$ST$EnaOpn | stVal | √ | √
59 |  |  | 89AE2 OPEN INTERLOCK | SP | B706_BCU89AE2$CILO8$ST$EnaOpn | stVal | √ | √
60 |  |  | 89BE OPEN INTERLOCK | SP | B706_BCU89BE$CILO5$ST$EnaOpn | stVal | √ | √
61 |  |  | 89A OPEN INTERLOCK | SP | B706_BCU89A$CILO2$ST$EnaOpn | stVal | √ | √
62 |  |  | 89B OPEN INTERLOCK | SP | B706_BCU89B$CILO4$ST$EnaOpn | stVal | √ | √
63 |  |  | 89L OPEN INTERLOCK | SP | B706_BCU89L$CILO6$ST$EnaOpn | stVal | √ | √
64 |  |  | 89LE OPEN INTERLOCK | SP | B706_BCU89LE$CILO7$ST$EnaOpn | stVal | √ | √
65 |  |  | DC-1 FAIL
66 |  |  | DC-2 FAIL
67 |  |  | BUSBAR 7ES-B1 OPEN(BUS EARTH SWITCH)
68 |  |  | BUSBAR 7ES-B2 OPEN(BUS EARTH SWITCH)
69 |  |  | BUSBAR 7ES-B1 CLOSE INTERLOCK
70 |  |  | BUSBAR 7ES-B2 CLOSE INTERLOCK
71 |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B706_BCUApplication$USER6$ST$SPS3 | stVal | √ | √
72 |  |  | DFR/DR FAIL ALARM
73 |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B706_BCUApplication$LLN0$ST$SPS | stVal | √
74 |  |  | A/R BLOCK | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$BlkFct | stVal | √
75 |  |  | A/R FUNCTION OFF | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$Off | stVal | √
76 |  |  | A/R FUNCTION ON | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$On | stVal | √
77 |  |  | A/R READY | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$AutoRecSt:0 | stVal:1 | √
78 |  |  | A/R UNSUCCESSFUL | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$AutoRecSt:0 | stVal:10 | √ | √
79 |  |  | A/R START
80 |  |  | A/R SUCCESSFUL | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$Successful | stVal | √
81 |  |  | RECLAIM IN PROGRESS
82 |  |  | MAIN A/R LOCKOUT
83 |  |  | TIE A/R LOCKOUT
84 |  |  | Tie CB A/R PRIORITY CLOSE
85 |  |  | MAIN/TIE BCU HEALTHY
86 |  |  | AR SINGLE PHASE TRIP PERMITTED
87 |  |  | CB NOT READY | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$CBnotRdy | stVal | √
88 |  |  | A/R CLOSE COMMAND INDICATION | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$OpCls | general | √
89 |  |  | A/R IN PROGRESS | SP | B706_BCUCB1_79AutoReclosing$GEN_RREC1$ST$RecInit | stVal | √
90 |  |  | MEASUREMENT
91
92 |  |  | POWER FACTOR | ME_FL | B706_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotPF:1 | mag$f
93 |  |  | FREQUENCY | ME_FL | B706_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$Hz:1 | mag$f
94 |  |  | ACTIVE POWER | ME_FL | B706_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotW:1 | mag$f
95 |  |  | REACTIVE POWER | ME_FL | B706_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVAr:1 | mag$f
96 |  |  | APPARENT POWER | ME_FL | B706_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVA:1 | mag$f
97 |  |  | I-R-PH CURRENT | ME_FL | B706_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsA$cVal$mag$f
98 |  |  | I-Y-PH CURRENT | ME_FL | B706_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsB$cVal$mag$f
99 |  |  | I-B-PH CURRENT | ME_FL | B706_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsC$cVal$mag$f
100 |  |  | R-Y VOLTAGE | ME_FL | B706_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsAB$cVal$mag$f
101 |  |  | Y-B VOLTAGE | ME_FL | B706_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsBC$cVal$mag$f
102 |  |  | B-R VOLYAGE | ME_FL | B706_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsCA$cVal$mag$f
103 |  |  | CB-B-PH COUNTER | ME_I | B706_BCUCBB$XCBR1$ST$OpCnt | stVal
104 |  |  | CB-R-PH COUNTER | ME_I | B706_BCUCBR$XCBR1$ST$OpCnt | stVal
105 |  |  | CB-Y-PH COUNTER | ME_I | B706_BCUCBY$XCBR1$ST$OpCnt | stVal
106 |  |  | SURGE ARRESTER B-PH | ME_I
107 |  |  | SURGE ARRESTER R-PH | ME_I
108 |  |  | SURGE ARRESTER Y-PH | ME_I
109 |  |  | CB R-PHASE OPERATION COUNTER | ME_I
110 |  |  | CB Y-PHASE OPERATION COUNTER | ME_I
111 |  |  | CB B-PHASE OPERATION COUNTER | ME_I
112
113 |  |  | COMMANDS
114
115 |  |  | CB CONTROL | DC | B706_BCUCB$CSWI1$CO$Pos:8 | Oper$ctlVal | √
116 |  |  | 89AE1 CONTROL | DC | B706_BCU89AE1$CSWI3$CO$Pos:8 | Oper$ctlVal | √
117 |  |  | 89AE2 CONTROL | DC | B706_BCU89AE2$CSWI8$CO$Pos:8 | Oper$ctlVal | √
118 |  |  | 89BE CONTROL | DC | B706_BCU89BE$CSWI5$CO$Pos:8 | Oper$ctlVal | √
119 |  |  | 89A CONTROL | DC | B706_BCU89A$CSWI2$CO$Pos:8 | Oper$ctlVal | √
120 |  |  | 89B CONTROL | DC | B706_BCU89B$CSWI4$CO$Pos:8 | Oper$ctlVal | √
121 |  |  | 89L CONTROL | DC | B706_BCU89L$CSWI6$CO$Pos:8 | Oper$ctlVal | √
122 |  |  | 89LE CONTROL | DC | B706_BCU89LE$CSWI7$CO$Pos:8 | Oper$ctlVal | √
123 |  |  | CB CONTROL NO SYNC | SC | B706_BCUCB$CSWI1$CO$Pos | Oper$noSync | √
124 |  |  | 86A TRIP RELAY RESET COMMAND | SC | B706_BCUApplication$USER2$CO$SPC:8 | Oper$ctlVal | √
125 |  |  | 86B TRIP RELAY RESET COMMAND | SC | B706_BCUApplication$USER2$CO$SPC1:8 | Oper$ctlVal | √
126 |  |  | A/R ON CONTROL | SC | B706_BCUApplication$USER8$CO$SPC:8 | Oper$ctlVal | √
127 |  |  | A/R OFF CONTROL | SC | B706_BCUApplication$USER8$CO$SPC1:8 | Oper$ctlVal | √
128 |  |  | MAIN-1 LED RESET | SC
129 |  |  | MAIN-2 LED RESET | SC
130 |  |  | SETTINGS CHANGED
131 |  |  | RELAY IN TEST MODE
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 7SA52_21.1
765kV LINE
Sr. No. | Voltage Level | Feeder Name |  | Assumed as Main-1 relay
|  |  | SIGNAL DESCRIPTION | INFORMATION TYPE | Telegram Address | POSITION | EVENT | ALARM
MEASUREMENT
1 | 765kV | 765kV LINE | FAULT DISTANCE | ME_FL | B706_21_1PROT$RFLO1$MX$FltDiskm:0 | mag$f
2 |  |  | FAULT CURRENT | ME_FL
3 |  |  | FAULT LOCATION DISTANCE | ME_FL
4 |  |  | MAIN-1 CARRIER RECEIVE CHANNEL-1 | ME_I
5 |  |  | MAIN-1 CARRIER SEND CHANNEL-1 | ME_I
6 |  |  | MAIN-2 CARRIER RECEIVE CHANNEL-1 | ME_I
7 |  |  | MAIN-2 CARRIER SEND CHANNEL-1 | ME_I
8 |  |  | MAIN-2 CARRIER RECEIVE CHANNEL-2 | ME_I
9 |  |  | MAIN-2 CARRIER SEND CHANNEL-2 | ME_I
10 |  |  | MAIN-1 CARRIER RECEIVE CHANNEL-2 | ME_I
11 |  |  | MAIN-1 CARRIER SEND CHANNEL-2 | ME_I
12 |  |  | DT RECEIVE CHANNEL-1 | ME_I
13 |  |  | DT SEND CHANNEL-1 | ME_I
14 |  |  | DT RECEIVE CHANNEL-2 | ME_I
15 |  |  | DT SEND CHANNEL-2 | ME_I
16 |  |  | CARRIER FAIL CHANNEL-1 | ME_I
17 |  |  | CARRIER FAIL CHANNEL-2 | ME_I
18 |  |  | CARRIER RECEIVED CHANNEL-1 | ME_I | B706_21_1CTRL$GGIO1$ST$ISCSO3:0 | stVal
19 |  |  | CARRIER RECEIVED CHANNEL-2 | ME_I | B706_21_1CTRL$GGIO1$ST$ISCSO4:0 | stVal
20 |  |  | CARRIER SEND CHANNEL-2 | ME_I | B706_21_1CTRL$GGIO1$ST$ISCSO1:0 | stVal
21 |  |  | CARRIER SEND CHANNEL-1 | ME_I | B706_21_1CTRL$GGIO1$ST$ISCSO2:0 | stVal
22 |  |  | DIRECT TRIP RECEIVED CHANNEL-1 | ME_I | B706_21_1CTRL$GGIO1$ST$ISCSO6:0 | stVal
23 |  |  | DIRECT TRIP SEND CHANNEL-1 | ME_I | B706_21_1CTRL$GGIO1$ST$ISCSO5:0 | stVal
24 |  |  | CARRIER FAIL CHANNEL-1 | ME_I | B706_21_1CTRL$GGIO2$ST$ISCSO7:0 | stVal
25 |  |  | CARRIER FAIL CHANNEL-2 | ME_I | B706_21_1CTRL$GGIO2$ST$ISCSO8:0 | stVal
26
27 |  |  | BINARY INPUT (Single Point)
28 |  |  | DIRECT TRIP SEND CHANNEL-2 | [5 empty] | GOOSE
29 |  |  | CARRIER FAIL CHANNEL-1 | SP | B706_21_1CTRL$GGIO1$ST$SPCSO25:0 | stVal | √ | √
30 |  |  | NO VOLTAGE IN LINE | SP | B706_21_1CTRL$GGIO1$ST$SPCSO21:0 | stVal | √ | √
31 |  |  | A/R BLOCK | SP | B706_21_1CTRL$GGIO1$ST$SPCSO14:0 | stVal | √
32 |  |  | MAIN A/R LOCKOUT
33 |  |  | TIE A/R LOCKOUT
34 |  |  | DIRECT TRIP SEND CHANNEL-1 | SP | B706_21_1CTRL$GGIO1$ST$SPCSO18:0 | stVal | √ | √
35 |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B706_21_1CTRL$GGIO1$ST$SPCSO24:0 | stVal | √ | √
36 |  |  | MAIN-2 RELAY FAIL | SP | B706_21_1CTRL$GGIO1$ST$SPCSO20:0 | stVal | √
37 |  |  | 89L OPEN FOR STUB | SP | B706_21_1CTRL$GGIO1$ST$SPCSO17:0 | stVal | √ | √
38 |  |  | DIRECT TRIP RECEIVED CHANNEL-1 | SP | B706_21_1CTRL$GGIO1$ST$SPCSO16:0 | stVal | √ | √
39 |  |  | LBB OPERATED | SP | B706_21_1CTRL$GGIO1$ST$SPCSO10:0 | stVal | √ | √
40 |  |  | TIME SYNCHRONISATION ERROR | SP | B706_21_1EXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
41 |  |  | VT FUSE FAILURE | SP | B706_21_1EXT$pdGGIO3$ST$SPCSO42:0 | stVal | √ | √
42 |  |  | BROKEN CONDUCTOR | SP | B706_21_1EXT$pdGGIO4$ST$SPCSO3:0 | stVal | √ | √
43 |  |  | EMERGENCY/MANUAL CLOSE | SP | B706_21_1EXT$pdGGIO6$ST$SPCSO36:0 | stVal | √
44 |  |  | CARRIER RECEIVED CHANNEL-1 | SP | B706_21_1EXT$pdGGIO63$ST$SPCSO38:0 | stVal | √ | √
45 |  |  | CARRIER RECEIVED CHANNEL-2 | SP | B706_21_1EXT$pdGGIO63$ST$SPCSO42:0 | stVal | √ | √
46 |  |  | CARRIER FAULTY | SP | B706_21_1EXT$pdGGIO63$ST$SPCSO37:0 | stVal | √ | √ | NOT REQUIRED
47 |  |  | SOTF PICKUP | SP | B706_21_1EXT$pdGGIO67$ST$SPCSO57:0 | stVal | √
48 |  |  | SOTF TRIP( OC)
49 |  |  | SOTF TRIP( IMPEDANCE Z1B) | SP | B706_21_1EXT$pdGGIO68$ST$SPCSO7:0 | stVal | √ | √
50 |  |  | CARRIER SEND CHANNEL-1 | SP | B706_21_1PROT$PSCH1$ST$ProTx | stVal | √ | √
51 |  |  | CARRIER SEND CHANNEL-2 | [5 empty] | GOOSE
52 |  |  | DIRECT TRIP RECEIVED CHANNEL-2 | [5 empty] | GOOSE
53 |  |  | CARRIER RECEIVED | SP | B706_21_1PROT$PSCH1$ST$ProRx | stVal | √ | √ | NOT REQUIRED
54 |  |  | CARRIER ADDIED TRIP/Z COM. TRIP | SP | B706_21_1PROT$PSCH1$ST$Op | general | √ | √
55 |  |  | MAIN A/R OPTD
56 |  |  | TIE A/R OPTD
57 |  |  | CB MANUAL CLOSE
58 |  |  | CB MANUAL TRIP
59 |  |  | 86 GROUP-A OPTD
60 |  |  | 86 GROUP-B OPTD
61 |  |  | MAIN A/R START
62 |  |  | TIE A/R START
63 |  |  | DISTANCE ZONE-1 PICKUP | SP | B706_21_1PROT$PDIS1$ST$Str | general | √
64 |  |  | DISTANCE PROTN ZONE-1 TRIP | SP | B706_21_1PROT$PDIS1$ST$Op | general | √ | √
65 |  |  | DISTANCE PROTN ZONE-1 R-PH TRIP | SP | B706_21_1PROT$PDIS1$ST$Op | phsA | √ | √
66 |  |  | DISTANCE PROTN ZONE-1 Y-PH TRIP | SP | B706_21_1PROT$PDIS1$ST$Op | phsB | √ | √
67 |  |  | DISTANCE PROTN ZONE-1 B-PH TRIP | SP | B706_21_1PROT$PDIS1$ST$Op | phsC | √ | √
68 |  |  | DISTANCE ZONE-2 PICKUP | SP | B706_21_1PROT$PDIS2$ST$Str | general | √
69 |  |  | DISTANCE PROTN ZONE-2 TRIP | SP | B706_21_1PROT$PDIS2$ST$Op | general | √ | √
70 |  |  | DISTANCE PROTN ZONE-2 R-PH TRIP | SP | B706_21_1PROT$PDIS2$ST$Op | phsA | √ | √
71 |  |  | DISTANCE PROTN ZONE-2 Y-PH TRIP | SP | B706_21_1PROT$PDIS2$ST$Op | phsB | √ | √
72 |  |  | DISTANCE PROTN ZONE-2 B-PH TRIP | SP | B706_21_1PROT$PDIS2$ST$Op | phsC | √ | √
73 |  |  | DISTANCE ZONE-3 PICKUP | SP | B706_21_1PROT$PDIS3$ST$Str | general | √
74 |  |  | DISTANCE PROTN ZONE-3 TRIP | SP | B706_21_1PROT$PDIS3$ST$Op | general | √ | √
75 |  |  | DISTANCE ZONE-4 PICKUP | SP | B706_21_1PROT$PDIS4$ST$Str | general | √
76 |  |  | DISTANCE PROTN ZONE-4 TRIP | SP | B706_21_1PROT$PDIS4$ST$Op | general | √ | √
77 |  |  | DISTANCE PROTN ZONE-4 R-PH TRIP
78 |  |  | DISTANCE PROTN ZONE-4 Y-PH TRIP
79 |  |  | DISTANCE PROTN ZONE-4 B-PH TRIP
80 |  |  | DISTANCE PROTN ZONE-1B PICKUP | SP | B706_21_1PROT$PDIS10$ST$Str | general | √
81 |  |  | DISTANCE PROTN ZONE-1B TRIP | SP | B706_21_1PROT$PDIS10$ST$Op | general | √ | √
82 |  |  | DISTANCE PROTN ZONE-1B B-PH TRIP | SP | B706_21_1PROT$PDIS10$ST$Op | phsC | √ | √
83 |  |  | DISTANCE PROTN ZONE-1B R-PH TRIP | SP | B706_21_1PROT$PDIS10$ST$Op | phsA | √ | √
84 |  |  | DISTANCE PROTN ZONE-1B Y-PH TRIP | SP | B706_21_1PROT$PDIS10$ST$Op | phsB | √ | √
85 |  |  | DISTANCE PROTN ZONE-5 PICKUP
86 |  |  | STUB PICKUP | SP | B706_21_1PROT$PTOC4$ST$Str | general | √
87 |  |  | STUB OPERATED | SP | B706_21_1PROT$PTOC4$ST$Op | general | √ | √
88 |  |  | DEF FAULT PICKUP | SP | B706_21_1PROT$PTOC8$ST$Str | general | √
89 |  |  | DEF FAULT TRIP | SP | B706_21_1PROT$PTOC8$ST$Op | general | √ | √
90 |  |  | OVERVOLTAGE STAGE-1-PH-N PICKUP | SP | B706_21_1PROT$PTOV1$ST$Str | general | √
91 |  |  | OVERVOLTAGE STAGE-1 -PH-N TRIP | SP | B706_21_1PROT$PTOV1$ST$Op | general | √ | √
92 |  |  | OVERVOLTAGE STAGE-2-PH-N PICKUP | SP | B706_21_1PROT$PTOV2$ST$Str | general | √
93 |  |  | OVERVOLTAGE STAGE-2-PH-N TRIP | SP | B706_21_1PROT$PTOV2$ST$Op | general | √ | √
94 |  |  | OVERVOLTAGE STAGE-1-PH-PH PICKUP | SP | B706_21_1PROT$PTOV3$ST$Str | general | √
95 |  |  | OVERVOLTAGE STAGE-1-PH-PH TRIP | SP | B706_21_1PROT$PTOV3$ST$Op | general | √ | √
96 |  |  | OVERVOLTAGE STAGE-2-PH-PH PICKUP | SP | B706_21_1PROT$PTOV4$ST$Str | general | √
97 |  |  | OVERVOLTAGE STAGE-2-PH-PH TRIP | SP | B706_21_1PROT$PTOV4$ST$Op | general | √ | √
98 |  |  | POWER SWING ZONE-1 DETECTED | SP | B706_21_1PROT$RPSB1$ST$Str | general | √ | √
99 |  |  | POWER SWING ZONE-1 BLOCK | SP | B706_21_1PROT$RPSB1$ST$BlkZn | stVal | √
100 |  |  | POWER SWING ZONE-1B DETECTED | SP | B706_21_1PROT$RPSB10$ST$Str | general | √ | √
101 |  |  | POWER SWING ZONE-1B BLOCK | SP | B706_21_1PROT$RPSB10$ST$BlkZn | stVal | √
102 |  |  | POWER SWING ZONE-2 DETECTED | SP | B706_21_1PROT$RPSB2$ST$Str | general | √ | √
103 |  |  | POWER SWING ZONE-2 BLOCK | SP | B706_21_1PROT$RPSB2$ST$BlkZn | stVal | √
104 |  |  | POWER SWING ZONE-3 DETECTED | SP | B706_21_1PROT$RPSB3$ST$Str | general | √ | √
105 |  |  | POWER SWING ZONE-3 BLOCK | SP | B706_21_1PROT$RPSB3$ST$BlkZn | stVal | √
106 |  |  | POWER SWING ZONE-4 DETECTED | SP | B706_21_1PROT$RPSB4$ST$Str | general | √ | √
107 |  |  | POWER SWING ZONE-4 BLOCK | SP | B706_21_1PROT$RPSB4$ST$BlkZn | stVal | √
108 |  |  | BUSBAR PROTN OPTD
109 |  |  | RELAY LED RESET | SC
110 |  |  | MAIN BCU FAIL
111 |  |  | TIE BCU FAIL
112 |  |  | MANUAL DR TRIGGER | SC
113 |  |  | GENERAL TRIP | SP | B706_21_1PROT$PTRC1$ST$Tr | general | √ | √
114 |  |  | DEVICE HEALTHY | SP | B707_21_1PROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
115 |  |  | MAIN-2 PROTN OPTD
116 |  |  | STUB BLOCKED | SP | B706_21_1PROT$PTOC4$ST$Blk | stVal | √ | √
117 |  |  | SETTINGS CHANGED
118 |  |  | RELAY IN TEST MODE
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 7SD52_87.1
765kV LINE
Sr. No. | Voltage Level | Feeder Name |  | Assumed as Main-1 relay
|  |  | SIGNAL DESCRIPTION | INFORMATION TYPE | Telegram Address | POSITION | EVENT | ALARM
MEASUREMENT
1 | 765kV | 765kV LINE | FAULT DISTANCE | ME_FL | B706_21_1PROT$RFLO1$MX$FltDiskm:0 | mag$f
2 |  |  | FAULT CURRENT | ME_FL
3 |  |  | FAULT LOCATION DISTANCE | ME_FL
4 |  |  | MAIN-1 CARRIER RECEIVE CHANNEL-1 | ME_I
5 |  |  | MAIN-1 CARRIER SEND CHANNEL-1 | ME_I
6 |  |  | MAIN-2 CARRIER RECEIVE CHANNEL-1 | ME_I
7 |  |  | MAIN-2 CARRIER SEND CHANNEL-1 | ME_I
8 |  |  | MAIN-2 CARRIER RECEIVE CHANNEL-2 | ME_I
9 |  |  | MAIN-2 CARRIER SEND CHANNEL-2 | ME_I
10 |  |  | MAIN-1 CARRIER RECEIVE CHANNEL-2 | ME_I
11 |  |  | MAIN-1 CARRIER SEND CHANNEL-2 | ME_I
12 |  |  | DT RECEIVE CHANNEL-1 | ME_I
13 |  |  | DT SEND CHANNEL-1 | ME_I
14 |  |  | DT RECEIVE CHANNEL-2 | ME_I
15 |  |  | DT SEND CHANNEL-2 | ME_I
16 |  |  | CARRIER FAIL CHANNEL-1 | ME_I
17 |  |  | CARRIER FAIL CHANNEL-2 | ME_I
18 |  |  | CARRIER RECEIVED CHANNEL-1 | ME_I | B706_21_1CTRL$GGIO1$ST$ISCSO3:0 | stVal
19 |  |  | CARRIER RECEIVED CHANNEL-2 | ME_I | B706_21_1CTRL$GGIO1$ST$ISCSO4:0 | stVal
20 |  |  | CARRIER SEND CHANNEL-2 | ME_I | B706_21_1CTRL$GGIO1$ST$ISCSO1:0 | stVal
21 |  |  | CARRIER SEND CHANNEL-1 | ME_I | B706_21_1CTRL$GGIO1$ST$ISCSO2:0 | stVal
22 |  |  | DIRECT TRIP RECEIVED CHANNEL-1 | ME_I | B706_21_1CTRL$GGIO1$ST$ISCSO6:0 | stVal
23 |  |  | DIRECT TRIP SEND CHANNEL-1 | ME_I | B706_21_1CTRL$GGIO1$ST$ISCSO5:0 | stVal
24 |  |  | CARRIER FAIL CHANNEL-1 | ME_I | B706_21_1CTRL$GGIO2$ST$ISCSO7:0 | stVal
25 |  |  | CARRIER FAIL CHANNEL-2 | ME_I | B706_21_1CTRL$GGIO2$ST$ISCSO8:0 | stVal
26
27 |  |  | BINARY INPUT (Single Point)
28 |  |  | LINE DIFFERENTIAL GENERAL TIP
29 |  |  | LINE DIFFERENTIAL REMOTE TRIP
30 |  |  | LINE DIFFERENTIAL R-PH TRIP
31 |  |  | LINE DIFFERENTIAL Y-PH TRIP
32 |  |  | LINE DIFFERENTIAL -PH TRIP
33 |  |  | LINE COMMUNICATION CHANNEL-1 FAULTY
34 |  |  | LINE COMMUNICATION CHANNEL-2 FAULTY
35 |  |  | DIRECT TRIP SEND CHANNEL-2 | [5 empty] | GOOSE
36 |  |  | CARRIER FAIL CHANNEL-1 | SP | B706_21_1CTRL$GGIO1$ST$SPCSO25:0 | stVal | √ | √
37 |  |  | NO VOLTAGE IN LINE | SP | B706_21_1CTRL$GGIO1$ST$SPCSO21:0 | stVal | √ | √
38 |  |  | A/R BLOCK | SP | B706_21_1CTRL$GGIO1$ST$SPCSO14:0 | stVal | √
39 |  |  | MAIN A/R LOCKOUT
40 |  |  | TIE A/R LOCKOUT
41 |  |  | DIRECT TRIP SEND CHANNEL-1 | SP | B706_21_1CTRL$GGIO1$ST$SPCSO18:0 | stVal | √ | √
42 |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B706_21_1CTRL$GGIO1$ST$SPCSO24:0 | stVal | √ | √
43 |  |  | MAIN-2 RELAY FAIL | SP | B706_21_1CTRL$GGIO1$ST$SPCSO20:0 | stVal | √
44 |  |  | 89L OPEN FOR STUB | SP | B706_21_1CTRL$GGIO1$ST$SPCSO17:0 | stVal | √ | √
45 |  |  | DIRECT TRIP RECEIVED CHANNEL-1 | SP | B706_21_1CTRL$GGIO1$ST$SPCSO16:0 | stVal | √ | √
46 |  |  | LBB OPERATED | SP | B706_21_1CTRL$GGIO1$ST$SPCSO10:0 | stVal | √ | √
47 |  |  | TIME SYNCHRONISATION ERROR | SP | B706_21_1EXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
48 |  |  | VT FUSE FAILURE | SP | B706_21_1EXT$pdGGIO3$ST$SPCSO41:0 | stVal | √ | √
49 |  |  | BROKEN CONDUCTOR | SP | B706_21_1EXT$pdGGIO4$ST$SPCSO3:0 | stVal | √ | √
50 |  |  | EMERGENCY/MANUAL CLOSE | SP | B706_21_1EXT$pdGGIO6$ST$SPCSO36:0 | stVal | √
51 |  |  | CARRIER RECEIVED CHANNEL-1 | SP | B706_21_1EXT$pdGGIO63$ST$SPCSO38:0 | stVal | √ | √
52 |  |  | CARRIER RECEIVED CHANNEL-2 | SP | B706_21_1EXT$pdGGIO63$ST$SPCSO42:0 | stVal | √ | √
53 |  |  | CARRIER FAULTY | SP | B706_21_1EXT$pdGGIO63$ST$SPCSO37:0 | stVal | √ | √ | NOT REQUIRED
54 |  |  | SOTF PICKUP | SP | B706_21_1EXT$pdGGIO67$ST$SPCSO57:0 | stVal | √
55 |  |  | SOTF TRIP( OC)
56 |  |  | SOTF TRIP( IMPEDANCE Z1B) | SP | B706_21_1EXT$pdGGIO68$ST$SPCSO7:0 | stVal | √ | √
57 |  |  | CARRIER SEND CHANNEL-1 | SP | B706_21_1PROT$PSCH1$ST$ProTx | stVal | √ | √
58 |  |  | CARRIER SEND CHANNEL-2 | [5 empty] | GOOSE
59 |  |  | DIRECT TRIP RECEIVED CHANNEL-2 | [5 empty] | GOOSE
60 |  |  | CARRIER RECEIVED | SP | B706_21_1PROT$PSCH1$ST$ProRx | stVal | √ | √ | NOT REQUIRED
61 |  |  | CARRIER ADDIED TRIP/Z COM. TRIP | SP | B706_21_1PROT$PSCH1$ST$Op | general | √ | √
62 |  |  | MAIN A/R OPTD
63 |  |  | TIE A/R OPTD
64 |  |  | CB MANUAL CLOSE
65 |  |  | CB MANUAL TRIP
66 |  |  | 86 GROUP-A OPTD
67 |  |  | 86 GROUP-B OPTD
68 |  |  | MAIN A/R START
69 |  |  | TIE A/R START
70 |  |  | DISTANCE ZONE-1 PICKUP | SP | B706_21_1PROT$PDIS1$ST$Str | general | √
71 |  |  | DISTANCE PROTN ZONE-1 TRIP | SP | B706_21_1PROT$PDIS1$ST$Op | general | √ | √
72 |  |  | DISTANCE PROTN ZONE-1 R-PH TRIP | SP | B706_21_1PROT$PDIS1$ST$Op | phsA | √ | √
73 |  |  | DISTANCE PROTN ZONE-1 Y-PH TRIP | SP | B706_21_1PROT$PDIS1$ST$Op | phsB | √ | √
74 |  |  | DISTANCE PROTN ZONE-1 B-PH TRIP | SP | B706_21_1PROT$PDIS1$ST$Op | phsC | √ | √
75 |  |  | DISTANCE ZONE-2 PICKUP | SP | B706_21_1PROT$PDIS2$ST$Str | general | √
76 |  |  | DISTANCE PROTN ZONE-2 TRIP | SP | B706_21_1PROT$PDIS2$ST$Op | general | √ | √
77 |  |  | DISTANCE PROTN ZONE-2 R-PH TRIP | SP | B706_21_1PROT$PDIS2$ST$Op | phsA | √ | √
78 |  |  | DISTANCE PROTN ZONE-2 Y-PH TRIP | SP | B706_21_1PROT$PDIS2$ST$Op | phsB | √ | √
79 |  |  | DISTANCE PROTN ZONE-2 B-PH TRIP | SP | B706_21_1PROT$PDIS2$ST$Op | phsC | √ | √
80 |  |  | DISTANCE ZONE-3 PICKUP | SP | B706_21_1PROT$PDIS3$ST$Str | general | √
81 |  |  | DISTANCE PROTN ZONE-3 TRIP | SP | B706_21_1PROT$PDIS3$ST$Op | general | √ | √
82 |  |  | DISTANCE ZONE-4 PICKUP | SP | B706_21_1PROT$PDIS4$ST$Str | general | √
83 |  |  | DISTANCE PROTN ZONE-4 TRIP | SP | B706_21_1PROT$PDIS4$ST$Op | general | √ | √
84 |  |  | DISTANCE PROTN ZONE-4 R-PH TRIP
85 |  |  | DISTANCE PROTN ZONE-4 Y-PH TRIP
86 |  |  | DISTANCE PROTN ZONE-4 B-PH TRIP
87 |  |  | DISTANCE PROTN ZONE-1B PICKUP | SP | B706_21_1PROT$PDIS10$ST$Str | general | √
88 |  |  | DISTANCE PROTN ZONE-1B TRIP | SP | B706_21_1PROT$PDIS10$ST$Op | general | √ | √
89 |  |  | DISTANCE PROTN ZONE-1B B-PH TRIP | SP | B706_21_1PROT$PDIS10$ST$Op | phsC | √ | √
90 |  |  | DISTANCE PROTN ZONE-1B R-PH TRIP | SP | B706_21_1PROT$PDIS10$ST$Op | phsA | √ | √
91 |  |  | DISTANCE PROTN ZONE-1B Y-PH TRIP | SP | B706_21_1PROT$PDIS10$ST$Op | phsB | √ | √
92 |  |  | DISTANCE PROTN ZONE-5 PICKUP
93 |  |  | STUB PICKUP | SP | B706_21_1PROT$PTOC4$ST$Str | general | √
94 |  |  | STUB OPERATED | SP | B706_21_1PROT$PTOC4$ST$Op | general | √ | √
95 |  |  | DEF FAULT PICKUP | SP | B706_21_1PROT$PTOC8$ST$Str | general | √
96 |  |  | DEF FAULT TRIP | SP | B706_21_1PROT$PTOC8$ST$Op | general | √ | √
97 |  |  | OVERVOLTAGE STAGE-1-PH-N PICKUP | SP | B706_21_1PROT$PTOV1$ST$Str | general | √
98 |  |  | OVERVOLTAGE STAGE-1 -PH-N TRIP | SP | B706_21_1PROT$PTOV1$ST$Op | general | √ | √
99 |  |  | OVERVOLTAGE STAGE-2-PH-N PICKUP | SP | B706_21_1PROT$PTOV2$ST$Str | general | √
100 |  |  | OVERVOLTAGE STAGE-2-PH-N TRIP | SP | B706_21_1PROT$PTOV2$ST$Op | general | √ | √
101 |  |  | OVERVOLTAGE STAGE-1-PH-PH PICKUP | SP | B706_21_1PROT$PTOV3$ST$Str | general | √
102 |  |  | OVERVOLTAGE STAGE-1-PH-PH TRIP | SP | B706_21_1PROT$PTOV3$ST$Op | general | √ | √
103 |  |  | OVERVOLTAGE STAGE-2-PH-PH PICKUP | SP | B706_21_1PROT$PTOV4$ST$Str | general | √
104 |  |  | OVERVOLTAGE STAGE-2-PH-PH TRIP | SP | B706_21_1PROT$PTOV4$ST$Op | general | √ | √
105 |  |  | POWER SWING ZONE-1 DETECTED | SP | B706_21_1PROT$RPSB1$ST$Str | general | √ | √
106 |  |  | POWER SWING ZONE-1 BLOCK | SP | B706_21_1PROT$RPSB1$ST$BlkZn | stVal | √
107 |  |  | POWER SWING ZONE-1B DETECTED | SP | B706_21_1PROT$RPSB10$ST$Str | general | √ | √
108 |  |  | POWER SWING ZONE-1B BLOCK | SP | B706_21_1PROT$RPSB10$ST$BlkZn | stVal | √
109 |  |  | POWER SWING ZONE-2 DETECTED | SP | B706_21_1PROT$RPSB2$ST$Str | general | √ | √
110 |  |  | POWER SWING ZONE-2 BLOCK | SP | B706_21_1PROT$RPSB2$ST$BlkZn | stVal | √
111 |  |  | POWER SWING ZONE-3 DETECTED | SP | B706_21_1PROT$RPSB3$ST$Str | general | √ | √
112 |  |  | POWER SWING ZONE-3 BLOCK | SP | B706_21_1PROT$RPSB3$ST$BlkZn | stVal | √
113 |  |  | POWER SWING ZONE-4 DETECTED | SP | B706_21_1PROT$RPSB4$ST$Str | general | √ | √
114 |  |  | POWER SWING ZONE-4 BLOCK | SP | B706_21_1PROT$RPSB4$ST$BlkZn | stVal | √
115 |  |  | BUSBAR PROTN OPTD
116 |  |  | RELAY LED RESET | SC
117 |  |  | MAIN BCU FAIL
118 |  |  | TIE BCU FAIL
119 |  |  | MANUAL DR TRIGGER | SC
120 |  |  | GENERAL TRIP | SP | B706_21_1PROT$PTRC1$ST$Tr | general | √ | √
121 |  |  | DEVICE HEALTHY | SP | B707_21_1PROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
122 |  |  | MAIN-2 PROTN OPTD
123 |  |  | STUB BLOCKED | SP | B706_21_1PROT$PTOC4$ST$Blk | stVal | √ | √
124 |  |  | SETTINGS CHANGED
125 |  |  | RELAY IN TEST MODE
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.