## LEGEND
SIEMENS SCADA GENERAL SIGNAL LIST FOR VARIOUS PROTECTION & CONTROL SIGNALS - REV03 (INDEX)
Sheet Ref. | IED MODEL | IED SYMBOLIC NAME(TYPICAL) | APPLICATION | IED NAME IN SCD | Additional Remarks
1 | 7SS52 | MCU-1 | BUSBAR MAIN-1 | STNM7XXBB1M1 | BCU is for each bay so 7XX refers to Bay
4 | 7SS52 | MCU-2 | BUSBAR MAIN-1 | STNM7XXBB1M2 | Bay No. 7XX will be always the main bay number for the ICT feeder
NOTE 1: The characters "STNM" stand for Substation Name with maximum 4 characters, this code will be given by POWERGRID for each project.
NOTE 2: The characters "7XX" stand for Bay name, example if the bay no 701 then same has to be implemented like STNM701BCU

## MCU-1
765kV MCU-2
Sr. No. | Voltage Level | Source | NAME ( 765KV MCU-1)
|  |  | SIGNAL DESCRIPTION | INFORMATION TYPE | Telegram Address | POSITION | Event | Alarm | Remarks
BINARY INPUT (Double Point)
1 | 765kV | MCU-1 | DC SOURCE-2 FAIL | SP | MCU_II_765kVCTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
2 |  |  | MCU-2 UNHEALTHY | SP | MCU_II_765kVCTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
3 |  |  | BREAKER FAILURE TRANSFER TRIP | SP | MCU_II_765kVEXT$pdGGIO164$ST$SPCSO1:0 | stVal | √ | √
4 |  |  | TIME SYNCHRONISATION ERROR | SP | MCU_II_765kVEXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
5 |  |  | BUSBAR TRIP | SP | MCU_II_765kVPROT$PDIF1$ST$Op | general | √ | √
6 |  |  | BAY UNIT-01 FAILURE | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO1:0 | stVal | √ | √
7 |  |  | BAY UNIT-02 FAILURE | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO8:0 | stVal | √ | √
8 |  |  | BAY UNIT-03 FAILURE | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO16:0 | stVal | √ | √
9 |  |  | BAY UNIT-03 FAILURE | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO24:0 | stVal | √ | √
10 |  |  | BAY UNIT-05 FAILURE | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO33:0 | stVal | √ | √
11 |  |  | BAY UNIT-06 FAILURE | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO41:0 | stVal | √ | √
12 |  |  | BAY UNIT-07 FAILURE | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO49:0 | stVal | √ | √
13 |  |  | BAY UNIT-08 FAILURE | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO57:0 | stVal | √ | √
14 |  |  | BUS-1 PROTECTION BLOCKED BY HANDLE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO9:0 | stVal | √ | √
15 |  |  | BUS-2 PROTECTION BLOCKED BY HANDLE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO26:0 | stVal | √ | √
16 |  |  | BUS-1 PROTECTION BLOCKED BY INTERM STATE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO17:0 | stVal | √ | √
17 |  |  | BUS-2 PROTECTION BLOCKED BY INTERM STATE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO33:0 | stVal | √ | √
18 |  |  | CURRENT SUPERVISION BUS-1 | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO10:0 | stVal | √ | √
19 |  |  | CURRENT SUPERVISION BUS-2 | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO27:0 | stVal | √ | √
20 |  |  | Trip command BF for BUS-1 R-PH | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO5:0 | stVal | √ | √
21 |  |  | Trip command BF for BUS-1 Y-PH | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO6:0 | stVal | √ | √
22 |  |  | Trip command BF for BUS-1 B-PH | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO7:0 | stVal | √ | √
23 |  |  | Trip command BF for BUS-2 R-PH | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO22:0 | stVal | √ | √
24 |  |  | Trip command BF for BUS-2 Y-PH | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO23:0 | stVal | √ | √
25 |  |  | Trip command BF for BUS-2 B-PH | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO24:0 | stVal | √ | √
26 |  |  | 3-PH Trip command BF for BUS-1 | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO1:0 | stVal | √ | √
27 |  |  | 3-PH Trip command BF for BUS-2 | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO18:0 | stVal | √ | √
28 |  |  | LBB RETRIP | SP | MCU_II_765kVPROT$RBRF1$ST$OpIn | general | √ | √
29 |  |  | LBB TRIP | SP | MCU_II_765kVPROT$RBRF1$ST$OpEx | general | √ | √
30 |  |  | GENERAL TRIP | SP | MCU_II_765kVPROT$PTRC1$ST$Tr | general | √ | √
31 |  |  | GENERAL TRIP R-PH | SP | MCU_II_765kVPROT$PTRC1$ST$Tr | phsA | √ | √
32 |  |  | GENERAL TRIP Y-PH | SP | MCU_II_765kVPROT$PTRC1$ST$Tr | phsB | √ | √
33 |  |  | GENERAL TRIP B-PH | SP | MCU_II_765kVPROT$PTRC1$ST$Tr | phsC | √ | √
34 |  |  | DEVICE OK | SP | MCU_II_765kVPROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √ | √
35 |  |  | BAY UNIT-01 OUT OF SERVICE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO34:0 | stVal | √ | √
36 |  |  | BAY UNIT-02 OUT OF SERVICE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO35:0 | stVal | √ | √
37 |  |  | BAY UNIT-03 OUT OF SERVICE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO36:0 | stVal | √ | √
38 |  |  | BAY UNIT-04 OUT OF SERVICE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO37:0 | stVal | √ | √
39 |  |  | BAY UNIT-05 OUT OF SERVICE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO38:0 | stVal | √ | √
40 |  |  | BAY UNIT-06 OUT OF SERVICE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO39:0 | stVal | √ | √
41 |  |  | BAY UNIT-07 OUT OF SERVICE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO40:0 | stVal | √ | √
42 |  |  | BAY UNIT-08 OUT OF SERVICE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO41:0 | stVal | √ | √
43 |  |  | Trip repeat Bay Unit-01 R-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO2:0 | stVal | √ | √
44 |  |  | Trip repeat Bay Unit-01 Y-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO3:0 | stVal | √ | √
45 |  |  | Trip repeat Bay Unit-01 B-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO4:0 | stVal | √ | √
46 |  |  | Trip repeat Bay Unit-02 R-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO9:0 | stVal | √ | √
47 |  |  | Trip repeat Bay Unit-02 Y-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO10:0 | stVal | √ | √
48 |  |  | Trip repeat Bay Unit-02 B-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO11:0 | stVal | √ | √
49 |  |  | Trip repeat Bay Unit-03 R-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO17:0 | stVal | √ | √
50 |  |  | Trip repeat Bay Unit-03 Y-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO18:0 | stVal | √ | √
51 |  |  | Trip repeat Bay Unit-03 B-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO19:0 | stVal | √ | √
52 |  |  | Trip repeat Bay Unit-04 R-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO25:0 | stVal | √ | √
53 |  |  | Trip repeat Bay Unit-04 Y-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO26:0 | stVal | √ | √
54 |  |  | Trip repeat Bay Unit-04 B-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO27:0 | stVal | √ | √
55 |  |  | Trip repeat Bay Unit-05 R-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO34:0 | stVal | √ | √
56 |  |  | Trip repeat Bay Unit-05 Y-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO35:0 | stVal | √ | √
57 |  |  | Trip repeat Bay Unit-05 B-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO36:0 | stVal | √ | √
58 |  |  | Trip repeat Bay Unit-06 R-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO42:0 | stVal | √ | √
59 |  |  | Trip repeat Bay Unit-06 Y-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO43:0 | stVal | √ | √
60 |  |  | Trip repeat Bay Unit-06 B-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO44:0 | stVal | √ | √
61 |  |  | Trip repeat Bay Unit-07 R-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO50:0 | stVal | √ | √
62 |  |  | Trip repeat Bay Unit-07 Y-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO51:0 | stVal | √ | √
63 |  |  | Trip repeat Bay Unit-07 B-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO52:0 | stVal | √ | √
64 |  |  | Trip repeat Bay Unit-08 R-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO58:0 | stVal | √ | √
65 |  |  | Trip repeat Bay Unit-08 Y-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO59:0 | stVal | √ | √
66 |  |  | Trip repeat Bay Unit-08 B-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO60:0 | stVal | √ | √
67 |  |  | Transfer Trip BUS-1 | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO8:0 | stVal | √ | √
68 |  |  | Transfer Trip BUS-2 | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO25:0 | stVal | √ | √
69 |  |  | BUS ZONE 1 TRIP | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO28:0 | stVal | √ | √
70 |  |  | BUS ZONE 2 TRIP | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO24:0 | stVal | √ | √
71 |  |  | BUSBAR CHECKZONE ALARM
72 |  |  | BUSBAR CHECKZONE TRIP
73 |  |  | BREAKER FAILURE - BUSBAR 1 BLOCKED
74 |  |  | BREAKER FAILURE - BUSBAR 2 BLOCKED
75 |  |  | ISOLATOR IN INTERMEDIATE STATUS
76 |  |  | BAY N TRIP
77 |  |  | BUSBAR BLOCKED DUE TO COMMUNICATION ERROR_Bay_n
78 |  |  | BAY_N_BREAKER FAILURE R-PH INITIATION
79 |  |  | BAY_N_BREAKER FAILURE Y-PH INITIATION
80 |  |  | BAY_N_BREAKER FAILURE B-PH INITIATION
81 |  |  | BAY_N_BREAKER FAILURE 3PH INITIATION
82 |  |  | BAY_N_EXTERNAL BUSBAR ZONE n
83 |  |  | BAY_N_BREAKER FAILURE RETRIP
84 |  |  | BAY_N_BREAKER FAILURE BACKTRIP
85 |  |  | BAY_N_BREAKER FAILURE RPH- RETRIP
86 |  |  | BAY_N_BREAKER FAILURE YPH- RETRIP
87 |  |  | BAY_N_BREAKER FAILURE BPH- RETRIP
88 |  |  | BBP CENTRAL UNIT IED UNHEALTHY
89 |  |  | SETTING CHANGE
90 |  |  | RELAY IN TEST MODE
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## MCU-2
765kV MCU-2
Sr. No. | Voltage Level | Source | NAME ( 765KV MCU-2)
|  |  | SIGNAL DESCRIPTION | INFORMATION TYPE | Telegram Address | POSITION | Event | Alarm | Remarks
BINARY INPUT (Double Point)
1 | 765kV | MCU-1 | DC SOURCE-1 FAIL | SP | MCU_II_765kVCTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
2 |  |  | MCU-1 UNHEALTHY | SP | MCU_II_765kVCTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
3 |  |  | BREAKER FAILURE TRANSFER TRIP | SP | MCU_II_765kVEXT$pdGGIO164$ST$SPCSO1:0 | stVal | √ | √
4 |  |  | TIME SYNCHRONISATION ERROR | SP | MCU_II_765kVEXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
5 |  |  | BUSBAR TRIP | SP | MCU_II_765kVPROT$PDIF1$ST$Op | general | √ | √
6 |  |  | BAY UNIT-01 FAILURE | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO1:0 | stVal | √ | √
7 |  |  | BAY UNIT-02 FAILURE | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO8:0 | stVal | √ | √
8 |  |  | BAY UNIT-03 FAILURE | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO16:0 | stVal | √ | √
9 |  |  | BAY UNIT-04 FAILURE | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO24:0 | stVal | √ | √
10 |  |  | BAY UNIT-05 FAILURE | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO33:0 | stVal | √ | √
11 |  |  | BAY UNIT-06 FAILURE | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO41:0 | stVal | √ | √
12 |  |  | BAY UNIT-07 FAILURE | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO49:0 | stVal | √ | √
13 |  |  | BAY UNIT-08 FAILURE | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO57:0 | stVal | √ | √
14 |  |  | BUS-1 PROTECTION BLOCKED BY HANDLE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO9:0 | stVal | √ | √
15 |  |  | BUS-2 PROTECTION BLOCKED BY HANDLE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO26:0 | stVal | √ | √
16 |  |  | BUS-1 PROTECTION BLOCKED BY INTERM STATE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO17:0 | stVal | √ | √
17 |  |  | BUS-2 PROTECTION BLOCKED BY INTERM STATE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO33:0 | stVal | √ | √
18 |  |  | CURRENT SUPERVISION BUS-1 | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO10:0 | stVal | √ | √
19 |  |  | CURRENT SUPERVISION BUS-2 | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO27:0 | stVal | √ | √
20 |  |  | Trip command BF for BUS-1 R-PH | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO5:0 | stVal | √ | √
21 |  |  | Trip command BF for BUS-1 Y-PH | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO6:0 | stVal | √ | √
22 |  |  | Trip command BF for BUS-1 B-PH | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO7:0 | stVal | √ | √
23 |  |  | Trip command BF for BUS-2 R-PH | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO22:0 | stVal | √ | √
24 |  |  | Trip command BF for BUS-2 Y-PH | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO23:0 | stVal | √ | √
25 |  |  | Trip command BF for BUS-2 B-PH | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO24:0 | stVal | √ | √
26 |  |  | 3-PH Trip command BF for BUS-1 | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO1:0 | stVal | √ | √
27 |  |  | 3-PH Trip command BF for BUS-2 | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO18:0 | stVal | √ | √
28 |  |  | LBB RETRIP | SP | MCU_II_765kVPROT$RBRF1$ST$OpIn | general | √ | √
29 |  |  | LBB TRIP | SP | MCU_II_765kVPROT$RBRF1$ST$OpEx | general | √ | √
30 |  |  | GENERAL TRIP | SP | MCU_II_765kVPROT$PTRC1$ST$Tr | general | √ | √
31 |  |  | GENERAL TRIP R-PH | SP | MCU_II_765kVPROT$PTRC1$ST$Tr | phsA | √ | √
32 |  |  | GENERAL TRIP Y-PH | SP | MCU_II_765kVPROT$PTRC1$ST$Tr | phsB | √ | √
33 |  |  | GENERAL TRIP B-PH | SP | MCU_II_765kVPROT$PTRC1$ST$Tr | phsC | √ | √
34 |  |  | DEVICE OK | SP | MCU_II_765kVPROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √ | √
35 |  |  | BAY UNIT-01 OUT OF SERVICE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO34:0 | stVal | √ | √
36 |  |  | BAY UNIT-02 OUT OF SERVICE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO35:0 | stVal | √ | √
37 |  |  | BAY UNIT-03 OUT OF SERVICE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO36:0 | stVal | √ | √
38 |  |  | BAY UNIT-04 OUT OF SERVICE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO37:0 | stVal | √ | √
39 |  |  | BAY UNIT-05 OUT OF SERVICE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO38:0 | stVal | √ | √
40 |  |  | BAY UNIT-06 OUT OF SERVICE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO39:0 | stVal | √ | √
41 |  |  | BAY UNIT-07 OUT OF SERVICE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO40:0 | stVal | √ | √
42 |  |  | BAY UNIT-08 OUT OF SERVICE | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO41:0 | stVal | √ | √
43 |  |  | Trip repeat Bay Unit-01 R-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO2:0 | stVal | √ | √
44 |  |  | Trip repeat Bay Unit-01 Y-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO3:0 | stVal | √ | √
45 |  |  | Trip repeat Bay Unit-01 B-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO4:0 | stVal | √ | √
46 |  |  | Trip repeat Bay Unit-02 R-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO9:0 | stVal | √ | √
47 |  |  | Trip repeat Bay Unit-02 Y-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO10:0 | stVal | √ | √
48 |  |  | Trip repeat Bay Unit-02 B-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO11:0 | stVal | √ | √
49 |  |  | Trip repeat Bay Unit-03 R-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO17:0 | stVal | √ | √
50 |  |  | Trip repeat Bay Unit-03 Y-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO18:0 | stVal | √ | √
51 |  |  | Trip repeat Bay Unit-03 B-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO19:0 | stVal | √ | √
52 |  |  | Trip repeat Bay Unit-04 R-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO25:0 | stVal | √ | √
53 |  |  | Trip repeat Bay Unit-04 Y-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO26:0 | stVal | √ | √
54 |  |  | Trip repeat Bay Unit-04 B-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO27:0 | stVal | √ | √
55 |  |  | Trip repeat Bay Unit-05 R-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO34:0 | stVal | √ | √
56 |  |  | Trip repeat Bay Unit-05 Y-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO35:0 | stVal | √ | √
57 |  |  | Trip repeat Bay Unit-05 B-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO36:0 | stVal | √ | √
58 |  |  | Trip repeat Bay Unit-06 R-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO42:0 | stVal | √ | √
59 |  |  | Trip repeat Bay Unit-06 Y-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO43:0 | stVal | √ | √
60 |  |  | Trip repeat Bay Unit-06 B-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO44:0 | stVal | √ | √
61 |  |  | Trip repeat Bay Unit-07 R-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO50:0 | stVal | √ | √
62 |  |  | Trip repeat Bay Unit-07 Y-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO51:0 | stVal | √ | √
63 |  |  | Trip repeat Bay Unit-07 B-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO52:0 | stVal | √ | √
64 |  |  | Trip repeat Bay Unit-08 R-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO58:0 | stVal | √ | √
65 |  |  | Trip repeat Bay Unit-08 Y-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO59:0 | stVal | √ | √
66 |  |  | Trip repeat Bay Unit-08 B-PH | SP | MCU_II_765kVPROT$GGIO1$ST$SPCSO60:0 | stVal | √ | √
67 |  |  | Transfer Trip BUS-1 | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO8:0 | stVal | √ | √
68 |  |  | Transfer Trip BUS-2 | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO25:0 | stVal | √ | √
69 |  |  | BUS ZONE 1 TRIP | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO28:0 | stVal | √ | √
70 |  |  | BUS ZONE 2 TRIP | SP | MCU_II_765kVPROT$GGIO2$ST$SPCSO24:0 | stVal | √ | √
71 |  |  | BUSBAR CHECKZONE ALARM
72 |  |  | BUSBAR CHECKZONE TRIP
73 |  |  | BREAKER FAILURE - BUSBAR 1 BLOCKED
74 |  |  | BREAKER FAILURE - BUSBAR 2 BLOCKED
75 |  |  | ISOLATOR IN INTERMEDIATE STATUS
76 |  |  | BAY N TRIP
77 |  |  | BUSBAR BLOCKED DUE TO COMMUNICATION ERROR_Bay_n
78 |  |  | BAY_N_BREAKER FAILURE R-PH INITIATION
79 |  |  | BAY_N_BREAKER FAILURE Y-PH INITIATION
80 |  |  | BAY_N_BREAKER FAILURE B-PH INITIATION
81 |  |  | BAY_N_BREAKER FAILURE 3PH INITIATION
82 |  |  | BAY_N_EXTERNAL BUSBAR ZONE n
83 |  |  | BAY_N_BREAKER FAILURE RETRIP
84 |  |  | BAY_N_BREAKER FAILURE BACKTRIP
85 |  |  | BAY_N_BREAKER FAILURE RPH- RETRIP
86 |  |  | BAY_N_BREAKER FAILURE YPH- RETRIP
87 |  |  | BAY_N_BREAKER FAILURE BPH- RETRIP
88 |  |  | BBP CENTRAL UNIT IED UNHEALTHY
89 |  |  | SETTING CHANGE
90 |  |  | RELAY IN TEST MODE
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.