## Rev History
GE Standard Signals for 400kV Level
Revision History
Rev.No | Description of Remarks | Date | Remarks
02 | Old Signal list | --
03 | 1. Distance relay - Missing internal signals related to functions such as AR, Weak-infeed, SOTF. 2. Addition of Differential Protection signals 3. Addition of Transformer phase wise Mechanical tripping signals 4. Addition of Centralized Busbar protection related signals. 5. Addition of tertiary transformer related protection signals. 6. Addition of Backup impedance protection signals for ICT & Reactor. 7. Addition of Directional OC & EF protection signals for ICT. 8. Addition of Mechanical trippings & alarms associated with REF. 9. Addition of NGR associated protection & CB Alarms 10. Addition of De-centralised - Busbar protection signals 11. Addition of Breaker failure protection initiation & Re-trip signals in standalone & centralized busbar protection 12. Addition of BCU – AR associated internal signals, TC phase wise, CSD related alarms, Bay wise measurements | 16.01.2024

## INDEX
REVISION 3- STANDARD SIGNAL LIST FOR GE
BAY NUMBERS ARE SYMBOLIC. FOLLOWING IEDS REPRESENT THE APPLICATIONS AS MENTIONED BELOW.
Sheet Ref. | IED MODEL | IED SYMBOLIC NAME(TYPICAL) | APPLICATION | IED NAME IN SCD | Additional Remarks
1 | P741 | IEC BB4_P741_87CUA | BUSBAR PROTECTION(DISTRIBUTED) MAIN 1 RELAY FOR 400KV | BHWD400BBM1 | Where same IED protects both Bus 1 & 2
2 | P741 | IEC BB4_P741_87CUB | BUSBAR PROTECTION(DISTRIBUTED) MAIN 2 RELAY FOR 400KV | BHWD400BBM2 | Where same IED protects both Bus 1 & 2
3 | B90 | IEC BB4_B90_87 | BUSBAR PROTECTION(CENTRALIZIED) MAIN RELAY FOR 400KV | BHWD400BB1M1 | Where same IED protects both Bus 1 & 2
4 | P444 | IEC R401_P444_21M1 | LINE DISTANCE RELAY MAIN-1 | BHWD4XXM1DIS | Bay No. 4XX will be always the main bay number for the Line feeder
5 | D60 | IEC R401_D60_21M1 | LINE DISTANCE RELAY MAIN-1 | BHWD4XXM1DIS | Bay No. 4XX will be always the main bay number for the Line feeder
6 | L90 | IEC R401_L90_21M2 | LINE DIFFERENTIAL RELAY MAIN-2 | BHWD4XXM2DIS | Bay No. 4XX will be always the main bay number for the Line feeder
7 | P546 | IEC R401_P546_21M2 | LINE DISTANCE RELAY MAIN-2 | BHWD4XXM2DIS | Bay No. 4XX will be always the main bay number for the Line feeder
8 | P743 | IEC R401_P743_PU_A | LINE PU-1 | BHWD4XXM1PU | Only if standalone reporting directly to HMI. Includes BFR related signals also
9 | P743 | IEC R401_P743_PU_B | LINE PU-2 | BHWD4XXM2PU | Only if standalone reporting directly to HMI. Includes BFR related signals also
10 | P743 | IEC R402_P743_50BF | STANDALONE BREAKER FAILURE RELAY FOR TIE BREAKER | BHWD4XXBFR | Only if standalone reporting directly to HMI
11 | P643 | IEC R407_P643_87T | ICT DIFFERENTIAL RELAY | BHWD4XXTDIF | Bay No. 4XX will be always the main bay number for the ICT feeder
12 | P643 | IEC R407_P643_64T | ICT REF RELAY | BHWD4XXTREF | Bay No. 4XX will be always the main bay number for the ICT feeder
13 | P442 | IEC R407_P442_21R | ICT BACKUP IMPEDNACE | BHWD4XXTBU | Bay No. 4XX will be always the main bay number for the ICT feeder
14 | P743 | IEC R407_P743_PU_A | ICT PU-1 | BHWD4XXM1PU | Only if standalone reporting directly to HMI. Includes BFR related signals also
15 | P743 | IEC R407_P743_PU_B | ICT PU-2 | BHWD4XXM2PU | Only if standalone reporting directly to HMI. Includes BFR related signals also
16 | P643 | IEC R412_P643_87R | REACTOR DIFFERENTIAL RELAY | BHWD4XXBRDIF | Bay No. 4XX will be always the main bay number for the Bus Reactor feeder. BR for Bus Reactor & LR for Line reactor
17 | P141 | IEC R412_P141_64R | REACTOR REF RELAY | BHWD4XXBRREF | Bay No. 4XX will be always the main bay number for the Bus Reactor feeder. BR for Bus Reactor & LR for Line reactor
18 | P442 | IEC R412_P442_21R | REACTOR BACKUP IMPEDANCE RELAY | BHWD4XXBRBU | Bay No. 4XX will be always the main bay number for the Bus Reactor feeder. BR for Bus Reactor & LR for Line reactor
19 | P743 | IEC R412_P743_PU_A | REACTOR PU-1 | BHWD4XXM1PU | Only if standalone reporting directly to HMI. Includes BFR related signals also
20 | P743 | IEC R412_P743_PU_B | REACTOR PU-2 | BHWD4XXM2PU | Only if standalone reporting directly to HMI. Includes BFR related signals also
21 | BCU | BCU B401_LINE | LINE BCU | BHWD4XXBCU | BCU is for each bay so 4XX refers to Bay
22 | BCU | BCU B402_TIE | TIE BCU | BHWD4XXBCU | BCU is for each bay so 4XX refers to Bay
23 | BCU | BCU B409_ICT1 | ICT BCU | BHWD2XXBCU | BCU is for each bay so 2XX refers to Bay
24 | BCU | BCU B412_BR | BUS REACTOR BCU | BHWD4XXBCU | BCU is for each bay so 4XX refers to Bay
25 | P442 | IEC R407_P442_67 HV | ICT LV OVERCURRENT RELAY | BHWD4XXTLVBU | Bay No. 4XX will be always the main bay number for the ICT feeder
26 | P442 | IEC R407_P442_67 LV | ICT HV OVERCURRENT RELAY | BHWD4XXTHVBU | Bay No. 4XX will be always the main bay number for the ICT feeder
27 |  | Time Synch | TIME SYNC ADDRESS FOR ALL BCUs IS GIVEN IN THIS SHEET
28 |  | Goose | GOOSE FAIL ALARM ADDRESS FOR ALL BCUs IS GIVEN IN THIS SHEET

## IEC BB4_P741_87CUA
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | BB4_P741_87CUA |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | BB4_P741_87CUA
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | BB4_P741_87CUA
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | BB4_P741_87CUA | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | BB4_P741_87CUA | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  | System;GosGGIO2 | ST;Ind5;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | BB4_P741_87CUA | PROTECTION | ZONE-1 BUSBAR BLOCKED EXTERNAL | Set | Reset | RS_ST_BB BLOCK 1 | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind5;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | 0
A |  |  | System;GosGGIO2 | ST;Ind5;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | BB4_P741_87CUA | PROTECTION | ZONE-2 BUSBAR BLOCKED EXTERNAL | Set | Reset | RS_ST_BB BLOCK 2 | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind6;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | 0
A |  |  | System;GosGGIO2 | ST;Ind5;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | BB4_P741_87CUA | PROTECTION | ZONE-1 BUSBAR BLOCKED | Set | Reset | RS_ST_BB BLOCK 1 | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Indxx;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind5;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | BB4_P741_87CUA | PROTECTION | ZONE-2 BUSBAR BLOCKED | Set | Reset | RS_ST_BB BLOCK 2 | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Indxx;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind6;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | BB4_P741_87CUA | PROTECTION | Z1 BUSBAR BLOCKED DUE TO COMM. ERR | Set | Reset | RS_ST_BB BLOCKC1 | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind7;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind6;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | BB4_P741_87CUA | PROTECTION | Z2 BUSBAR BLOCKED DUE TO COMM. ERR | Set | Reset | RS_ST_BB BLOCKC2 | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind8;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind7;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | BB4_P741_87CUA | PROTECTION | ZONE-1 BB BLOCKED DUE TO INTERMED. | Set | Reset | RS_ST_BB BLOCKI1 | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind9;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind7;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | BB4_P741_87CUA | PROTECTION | ZONE-2 BB BLOCKED DUE TO INTERMED. | Set | Reset | RS_ST_BB BLOCKI2 | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind10;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind1;stVal;SPS | SPE_HLa_Reset_In | SPS | 400kV | BB4_P741_87CUA | SYSTEM | MAIN-1 B/B ZONE-1 | In | Reset | RS_IN_M1 BB Z1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind1;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind3;stVal;SPS | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | BB4_P741_87CUA | SYSTEM | 87CUB RELAY | Healthy | Unhealthy | UH_HL_87CUB | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind3;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind4;stVal;SPS | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | BB4_P741_87CUA | SYSTEM | BBMT2 RELAY | Healthy | Unhealthy | UH_HL_BBMT2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind4;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind7;stVal;SPS | SPE_HLa_Reset_In | SPS | 400kV | BB4_P741_87CUA | SYSTEM | MAIN-1 B/B ZONE-2 | In | Reset | RS_IN_M1 BB Z2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind7;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CftPhsPDIF1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | BB4_P741_87CUA | PROTECTION | ZONE-1 CIRCUITRY FAULT | Operated | Reset | RS_OP_ZONE1 CFT | Transmitted to IEC | [7 empty] | Protection;CftPhsPDIF1 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CftPhsPDIF2 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | BB4_P741_87CUA | PROTECTION | ZONE-2 CIRCUITRY FAULT | Operated | Reset | RS_OP_ZONE2 CFT | Transmitted to IEC | [7 empty] | Protection;CftPhsPDIF2 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;TrpPhsPDIF1 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | BB4_P741_87CUA | PROTECTION | B/B ZONE-1 | Operated | Reset | RS_OP_ZONE1 | Transmitted to IEC | [7 empty] | Protection;TrpPhsPDIF1 | ST;Op;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;TrpPhsPDIF2 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | BB4_P741_87CUA | PROTECTION | B/B ZONE-2 | Operated | Reset | RS_OP_ZONE2 | Transmitted to IEC | [7 empty] | Protection;TrpPhsPDIF2 | ST;Op;general;ACT |  |  | None | [11 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | BB4_P741_87CUA | PROTECTION | ZONE MERGE (IF APPLICABLE ) | Set | Reset | RS_ST_ZONE_MRG
[6 empty] | SPS | 400kV | BB4_P741_87CUA | PROTECTION | BUSBAR ZONE 1 R- PHASE TRIP | Operated | Reset | RS_OP_ZONE1_R | [8 empty] | Protection;TrpPhsPDIF1 | ST;Op;phs1
[6 empty] | SPS | 400kV | BB4_P741_87CUA | PROTECTION | BUSBAR ZONE 1 Y- PHASE TRIP | Operated | Reset | RS_OP_ZONE1_Y | [8 empty] | Protection;TrpPhsPDIF1 | ST;Op;phs2
[6 empty] | SPS | 400kV | BB4_P741_87CUA | PROTECTION | BUSBAR ZONE 1 B- PHASE TRIP | Operated | Reset | RS_OP_ZONE1_B | [8 empty] | Protection;TrpPhsPDIF1 | ST;Op;phs3
[6 empty] | SPS | 400kV | BB4_P741_87CUA | PROTECTION | BUSBAR ZONE 2 R- PHASE TRIP | Operated | Reset | RS_OP_ZONE2_R | [8 empty] | Protection;TrpPhsPDIF2 | ST;Op;phs1
[6 empty] | SPS | 400kV | BB4_P741_87CUA | PROTECTION | BUSBAR ZONE 2 Y- PHASE TRIP | Operated | Reset | RS_OP_ZONE2_Y | [8 empty] | Protection;TrpPhsPDIF2 | ST;Op;phs2
[6 empty] | SPS | 400kV | BB4_P741_87CUA | PROTECTION | BUSBAR ZONE 2 B- PHASE TRIP | Operated | Reset | RS_OP_ZONE2_B | [8 empty] | Protection;TrpPhsPDIF2 | ST;Op;phs3
A |  |  |  |  | SPARE | SPS | 400kv | BB4_P741_87CUA | PROTECTION | CHECK ZONE | Operated | Reset | RS_OP_CHECKZONE | [12 empty] | None |  | No | [9 empty] | 1 | #REF!
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | BB4_P741_87CUA
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUA
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUA
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUA
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUA
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUA
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUA
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUA
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUA
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUA
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUA
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | BB4_P741_87CUA
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name BB4_P741_87CUA
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name BB4_P741_87CUA
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name BB4_P741_87CUA
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name BB4_P741_87CUA
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | BB4_P741_87CUA
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name BB4_P741_87CUA
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name BB4_P741_87CUA
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | BB4_P741_87CUA
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name BB4_P741_87CUA
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name BB4_P741_87CUA
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name BB4_P741_87CUA
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name BB4_P741_87CUA
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D49: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E49: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D63: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E63: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC63: HMI Display : Specify if the data appears in HMI.
Note on AD63: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE63: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D71: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E71: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D77: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E77: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB77: LCD Display : Specify if the data appears in computer LCD.
Note on AC77: HMI Display : Specify if the data appears in HMI.
Note on AD77: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE77: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC140: HMI Display : Specify if the data appears in HMI.
Note on AD140: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE140: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB160: LCD Display : Specify if the data appears in computer LCD.
Note on AC160: HMI Display : Specify if the data appears in HMI.
Note on AD160: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE160: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC BB4_P741_87CUB
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | BB4_P741_87CUB |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | BB4_P741_87CUB
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | BB4_P741_87CUB
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | BB4_P741_87CUB | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name BB4_P741_87CUB
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | BB4_P741_87CUB | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind5;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | BB4_P741_87CUB | PROTECTION | ZONE-1 BUSBAR BLOCKED EXTERNAL | Set | Reset | RS_ST_BB BLOCK 1 | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind5;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind6;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | BB4_P741_87CUB | PROTECTION | ZONE-2 BUSBAR BLOCKED EXTERNAL | Set | Reset | RS_ST_BB BLOCK 2 | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind6;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind5;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | BB4_P741_87CUB | PROTECTION | ZONE-1 BUSBAR BLOCKED | Set | Reset | RS_ST_BB BLOCK 1 | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Indxx;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind6;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | BB4_P741_87CUB | PROTECTION | ZONE-2 BUSBAR BLOCKED | Set | Reset | RS_ST_BB BLOCK 2 | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Indxx;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind7;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | BB4_P741_87CUB | PROTECTION | Z1 BUSBAR BLOCKED DUE TO COMM. ERR | Set | Reset | RS_ST_BB BLOCKC1 | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind7;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | BB4_P741_87CUB | PROTECTION | Z2 BUSBAR BLOCKED DUE TO COMM. ERR | Set | Reset | RS_ST_BB BLOCKC2 | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind8;stVal;SPS
[6 empty] | SPS | 400kV | BB4_P741_87CUB | PROTECTION | ZONE-1 BB BLOCKED DUE TO INTERMED. | Set | Reset | RS_ST_BB BLOCKI1 | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind9;stVal;SPS
[6 empty] | SPS | 400kV | BB4_P741_87CUB | PROTECTION | ZONE-2 BB BLOCKED DUE TO INTERMED. | Set | Reset | RS_ST_BB BLOCKI2 | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind10;stVal;SPS
A |  |  | System;OptGGIO1 | ST;Ind1;stVal;SPS | SPE_HLa_Reset_In | SPS | 400kV | BB4_P741_87CUB | SYSTEM | MAIN-1 B/B ZONE-1 | In | Reset | RS_IN_M2 BB Z1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind1;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind3;stVal;SPS | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | BB4_P741_87CUB | SYSTEM | 87CUA RELAY | Healthy | Unhealthy | UH_HL_87CUA | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind3;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind4;stVal;SPS | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | BB4_P741_87CUB | SYSTEM | BBMT2 RELAY | Healthy | Unhealthy | UH_HL_BBMT1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind4;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind7;stVal;SPS | SPE_HLa_Reset_In | SPS | 400kV | BB4_P741_87CUB | SYSTEM | MAIN-1 B/B ZONE-2 | In | Reset | RS_IN_M2 BB Z2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind7;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CftPhsPDIF1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | BB4_P741_87CUB | PROTECTION | ZONE-1 CIRCUITRY FAULT | Operated | Reset | RS_OP_ZONE1 CFT | Transmitted to IEC | [7 empty] | Protection;CftPhsPDIF1 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CftPhsPDIF2 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | BB4_P741_87CUB | PROTECTION | ZONE-2 CIRCUITRY FAULT | Operated | Reset | RS_OP_ZONE2 CFT | Transmitted to IEC | [7 empty] | Protection;CftPhsPDIF2 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;TrpPhsPDIF1 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | BB4_P741_87CUB | PROTECTION | B/B ZONE-1 | Operated | Reset | RS_OP_ZONE1 | Transmitted to IEC | [7 empty] | Protection;TrpPhsPDIF1 | ST;Op;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;TrpPhsPDIF2 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | BB4_P741_87CUB | PROTECTION | B/B ZONE-2 | Operated | Reset | RS_OP_ZONE2 | Transmitted to IEC | [7 empty] | Protection;TrpPhsPDIF2 | ST;Op;general;ACT |  |  | None | [11 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | BB4_P741_87CUB | PROTECTION | ZONE MERGE (IF APPLICABLE ) | Set | Reset | RS_ST_ZONE_MRG
[6 empty] | SPS | 400kV | BB4_P741_87CUB | PROTECTION | BUSBAR ZONE 1 R- PHASE TRIP | Operated | Reset | RS_OP_ZONE1_R | [8 empty] | Protection;TrpPhsPDIF1 | ST;Op;phs1
[6 empty] | SPS | 400kV | BB4_P741_87CUB | PROTECTION | BUSBAR ZONE 1 Y- PHASE TRIP | Operated | Reset | RS_OP_ZONE1_Y | [8 empty] | Protection;TrpPhsPDIF1 | ST;Op;phs2
[6 empty] | SPS | 400kV | BB4_P741_87CUB | PROTECTION | BUSBAR ZONE 1 B- PHASE TRIP | Operated | Reset | RS_OP_ZONE1_B | [8 empty] | Protection;TrpPhsPDIF1 | ST;Op;phs3
[6 empty] | SPS | 400kV | BB4_P741_87CUB | PROTECTION | BUSBAR ZONE 2 R- PHASE TRIP | Operated | Reset | RS_OP_ZONE2_R | [8 empty] | Protection;TrpPhsPDIF2 | ST;Op;phs1
[6 empty] | SPS | 400kV | BB4_P741_87CUB | PROTECTION | BUSBAR ZONE 2 Y- PHASE TRIP | Operated | Reset | RS_OP_ZONE2_Y | [8 empty] | Protection;TrpPhsPDIF2 | ST;Op;phs2
[6 empty] | SPS | 400kV | BB4_P741_87CUB | PROTECTION | BUSBAR ZONE 2 B- PHASE TRIP | Operated | Reset | RS_OP_ZONE2_B | [8 empty] | Protection;TrpPhsPDIF2 | ST;Op;phs3
[6 empty] | SPS | 400kV | BB4_P741_87CUB | PROTECTION | CHECK ZONE | Operated | Reset | RS_OP_CHECKZONE
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | BB4_P741_87CUB
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUB
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUB
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUB
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUB
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUB
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUB
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUB
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUB
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUB
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name BB4_P741_87CUB
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | BB4_P741_87CUB
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name BB4_P741_87CUB
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name BB4_P741_87CUB
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name BB4_P741_87CUB
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name BB4_P741_87CUB
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | BB4_P741_87CUB
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name BB4_P741_87CUB
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name BB4_P741_87CUB
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | BB4_P741_87CUB
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name BB4_P741_87CUB
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name BB4_P741_87CUB
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name BB4_P741_87CUB
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name BB4_P741_87CUB
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D49: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E49: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D63: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E63: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC63: HMI Display : Specify if the data appears in HMI.
Note on AD63: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE63: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D71: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E71: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D77: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E77: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB77: LCD Display : Specify if the data appears in computer LCD.
Note on AC77: HMI Display : Specify if the data appears in HMI.
Note on AD77: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE77: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC140: HMI Display : Specify if the data appears in HMI.
Note on AD140: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE140: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB160: LCD Display : Specify if the data appears in computer LCD.
Note on AC160: HMI Display : Specify if the data appears in HMI.
Note on AD160: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE160: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC BB4_B90_87
Designation : |  |  | Project Name | [30 empty] | Symbol : |  | SAM-DTL-DS Agile-4.3.3.0 |  |  |  | CCCC
Issue : |  |  | A | [30 empty] | Ref : |  | PROJECTNAME-Xnn-DTL
Date : |  |  | 0 | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | Site Name
IEC Description
Keys :
|  |  | Computer Name |  | 7BB1_P747_87_R |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
SCADA 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | 7BB1_P747_87_R
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | 7BB1_P747_87_R
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400KV | BB4_B90_87 | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | [8 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name 7BB1_P747_87_R
[6 empty] | SPS | 400KV | BB4_B90_87 | PROTECTION | ZONE-1 BUSBAR BLOCKED EXTERNAL | Set | Reset | RS_ST_BB BLOCK E | [8 empty] | System;GosGGIO2 | ST;Ind3;stVal;SPS
A |  |  | System;GosGGIO2 | ST;Ind3;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400KV | BB4_B90_87 | PROTECTION | ZONE-2 BUSBAR BLOCKED EXTERNAL | Set | Reset | RS_ST_BB BLOCK E | [8 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | DIGITAL INFORMATION FROM IED IED name 7BB1_P747_87_R
A |  |  | System;GosGGIO2 | ST;Ind6;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400KV | BB4_B90_87 | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | [8 empty] | System;GosGGIO2 | ST;Ind6;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
[6 empty] | SPS | 400KV | BB4_B90_87 | PROTECTION | ZONE-1 CIRCUITRY FAULT | Operated | Reset | RS_ST_CT_CKT_Err | [8 empty] | System;GosGGIO2 | ST;Ind7;stVal;SPS
A |  |  | System;GosGGIO2 | ST;Ind7;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400KV | BB4_B90_87 | PROTECTION | ZONE-2 CIRCUITRY FAULT | Operated | Reset | RS_ST_CT_CKT_Err | [8 empty] | System;GosGGIO2 | ST;Ind8;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind2;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400KV | BB4_B90_87 | SYSTEM | BAY 425 LBB | Operated | Reset | RS_OP 425 LBB | [8 empty] | System;OptGGIO1 | ST;Ind2;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind4;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400KV | BB4_B90_87 | SYSTEM | BAY 428 LBB | Operated | Reset | RS_OP 428 LBB | [8 empty] | System;OptGGIO1 | ST;Ind4;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind6;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400KV | BB4_B90_87 | SYSTEM | BAY 426 LBB | Operated | Reset | RS_OP 426 LBB | [8 empty] | System;OptGGIO1 | ST;Ind6;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind25;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400KV | BB4_B90_87 | SYSTEM | ZONE-1 MAIN-1 SWITCH IN | Set | Reset | RS_ST Z-1 IN | [8 empty] | System;OptGGIO1 | ST;Ind25;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind27;stVal;SPS | SPE_HLA_Unhlthy_Hlthy | SPS | 400KV | BB4_B90_87 | SYSTEM | BB M2 RELAY R-PH | Healthy | Unhealthy | UH_HL BB M2 RLY | [8 empty] | System;OptGGIO1 | ST;Ind27;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind29;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400KV | W | SYSTEM | ZONE-2 MAIN-1 SWITCH IN | Set | Reset | RS_ST Z-2 IN | [8 empty] | System;OptGGIO1 | ST;Ind29;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CznPDIF1 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400KV | BB4_B90_87 | PROTECTION | CHECK ZONE DIFF PROT | Operated | Reset | RS_OP_CHK ZONE | [8 empty] | Protection;CznPDIF1 | ST;Op;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;BbpT01PDIF1 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400KV | BB4_B90_87 | PROTECTION | BUSBAR ZONE1 TRIP | Operated | Reset | RS_OP_BB ZONE1 | [8 empty] | Protection;BbpT01PDIF1 | ST;Op;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;BbpT02PDIF1 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400KV | BB4_B90_87 | PROTECTION | BUSBAR ZONE2 TRIP | Operated | Reset | RS_OP_BB ZONE2 | [8 empty] | Protection;BbpT02PDIF1 | ST;Op;general;ACT |  |  | None | [11 empty] | 1 | #REF!
[6 empty] | SPS | 400KV | BB4_B90_87 | PROTECTION | BUSBAR ZONE 1 PROTECTION BLOCKED | Set | Reset
[6 empty] | SPS | 400KV | BB4_B90_87 | PROTECTION | BUSBAR ZONE 2 PROTECTION BLOCKED | Set | Reset
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | 7BB1_P747_87_R
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name 7BB1_P747_87_R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name 7BB1_P747_87_R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name 7BB1_P747_87_R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name 7BB1_P747_87_R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name 7BB1_P747_87_R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name 7BB1_P747_87_R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name 7BB1_P747_87_R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name 7BB1_P747_87_R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name 7BB1_P747_87_R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name 7BB1_P747_87_R
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | 7BB1_P747_87_R
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name 7BB1_P747_87_R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name 7BB1_P747_87_R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name 7BB1_P747_87_R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name 7BB1_P747_87_R
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | 7BB1_P747_87_R
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name 7BB1_P747_87_R
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name 7BB1_P747_87_R
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | 7BB1_P747_87_R
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name 7BB1_P747_87_R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name 7BB1_P747_87_R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name 7BB1_P747_87_R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name 7BB1_P747_87_R
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA

## IEC R401_P444_21M1
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R401_P444_21M1 |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R401_P444_21M1
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R401_P444_21M1
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R401_P444_21M1 | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P444_21M1
A |  |  | System;AlmGGIO1 | ST;Alm6;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | CVT FUSE | Alarm | Normal | RS_OP_VT-FUSE | Transmitted to IEC | [7 empty] | System;AlmGGIO1 | ST;Alm6;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P444_21M1
A |  |  | System;AlmGGIO1 | ST;Alm31;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | BROKEN CONDUCTOR | Alarm | Normal | RS_OP_BRKN CND | Transmitted to IEC | [7 empty] | System;AlmGGIO1 | ST;Alm31;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P444_21M1
A |  |  | System;GosGGIO2 | ST;Ind15;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R401_P444_21M1 | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind15;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind4;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | SYSTEM | GROUP A TRIP RELAY | Operated | Reset | RS_OP_GRP-A | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind4;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind5;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | SYSTEM | CARRIER CHANNEL-1 | Healthy | Unhealthy | RS_set_CARr1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind5;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind6;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_P444_21M1 | SYSTEM | LINE ISO OPEN FOR STUB PROTN | Set | Reset | RS_ST_ISO_OE_STU | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind6;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind7;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_P444_21M1 | SYSTEM | CB CLOSE CMD SOTF INITIATION | Set | Reset | RS_ST_SOTF | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind7;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind8;stVal;SPS | SPE_HLA_NotRec_Recvd | SPS | 400kV | R401_P444_21M1 | SYSTEM | CARRIER CHANNEL-2 | Received | Not Received | NR_RV_CAR_R_CH2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind8;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind9;stVal;SPS | SPE_HLA_Flty_Healthy | SPS | 400kV | R401_P444_21M1 | SYSTEM | MAIN-2 RELAY | Healthy | Faulty | FL_HL_M2_RLY | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind9;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind10;stVal;SPS | SPE_HLA_NotRec_Recvd | SPS | 400kV | R401_P444_21M1 | SYSTEM | CARRIER CHANNEL-1 | Received | Not Received | NR_RV_CARR CH1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind11;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | SYSTEM | CARRIER CHANNEL-2 | Healthy | Unhealthy | RS_set_CARr2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind11;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind12;stVal;SPS | SPE_HLA_NotRec_Recvd | SPS | 400kV | R401_P444_21M1 | SYSTEM | DIRECT TRIP RECEIVED CH-1 | Received | Not Received | NR_RV_DT_REV_CH1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind12;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind13;stVal;SPS | SPE_HLA_NotRec_Recvd | SPS | 400kV | R401_P444_21M1 | SYSTEM | DIRECT TRIP RECEIVED CH-2 | Received | Not Received | NR_RV_DT_REV_CH2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind13;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind17;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | SYSTEM | GROUP B TRIP RELAY | Operated | Reset | RS_OP_GRP-B | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind17;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind24;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_P444_21M1 | SYSTEM | TRIP RELAY 86A SUPERVISION | Healthy | Unhealthy | RS_ST_86A SUPV | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind24;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Control;PsbRPSB3 | ST;Str;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | POWER SWING DETECTED | Set | Reset | RS_AL_PSB_STR | Transmitted to IEC | [7 empty] | Control;PsbRPSB3 | ST;Str;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Control;PsbRPSB3 | ST;BlkZn;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | POWER SWING BLOCKING | Set | Reset | RS_OP_PWR SW BLK | Transmitted to IEC | [7 empty] | Control;PsbRPSB3 | ST;BlkZn;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;PTRC1 | ST;Tr;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | GENERAL TRIP | Operated | Reset | RS_OP_GEN TRIP | Transmitted to IEC | [7 empty] | Protection;PTRC1 | ST;Tr;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsA;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE ZONE-1 R-PH | Operated | Reset | RS_OP_Z1R-PH | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phsA;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsB;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE ZONE-1 Y-PH | Operated | Reset | RS_OP_Z1Y-PH | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phsB;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsC;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE ZONE-1 B-PH | Operated | Reset | RS_OP_Z1B-PH | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phsC;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE PROTN ZONE-1 | Operated | Reset | RS_OP_ZONE-1 | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE ZONE-1 START | Set | Reset | RS_OP_DIS S Z1 | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE PROTN ZONE-2 | Operated | Reset | RS_OP_ZONE-2 | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Str;phsA;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE ZONE-2 START R-PH | Set | Reset | RS_OP_DIS S Z2_R | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Str;phsA;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Str;phsB;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE ZONE-2 START Y-PH | Set | Reset | RS_OP_DIS S Z2_Y | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Str;phsB;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Str;phsC;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE ZONE-2 START B-PH | Set | Reset | RS_OP_DIS S Z2_B | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Str;phsC;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE ZONE-2 START | Set | Reset | RS_OP_DIS S Z2 | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS3 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE PROTN ZONE-3 | Operated | Reset | RS_OP_ZONE-3 | Transmitted to IEC | [7 empty] | Protection;DisPDIS3 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS3 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE ZONE-3 START | Set | Reset | RS_OP_DIS S Z3 | Transmitted to IEC | [7 empty] | Protection;DisPDIS3 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS4 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE PROTN ZONE-4 | Operated | Reset | RS_OP_ZONE-4 | Transmitted to IEC | [7 empty] | Protection;DisPDIS4 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS4 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE ZONE-4 START | Set | Reset | RS_OP_DIS S Z4 | Transmitted to IEC | [7 empty] | Protection;DisPDIS4 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS5 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE PROTN ZONE-5 | Operated | Reset | RS_OP_ZONE-5 | Transmitted to IEC | [7 empty] | Protection;DisPDIS5 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS5 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE ZONE-5 START | Set | Reset | RS_OP_DIS S Z5 | Transmitted to IEC | [7 empty] | Protection;DisPDIS5 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPSCH1 | ST;CarRx;general;ACT | SPE_HLa_Reset_Set | SPS | 400kV | R401_P444_21M1 | PROTECTION | CARRIER AIDED SCHEME | Operated | Reset | RS_ST_CARR_AIDED | Transmitted to IEC | [7 empty] | Protection;DisPSCH1 | ST;CarRx;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPSCH1 | ST;ProRx;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_P444_21M1 | PROTECTION | CARRIER RECEIVE | Set | Reset | RS_ST_CARR REC | Transmitted to IEC | [7 empty] | Protection;DisPSCH1 | ST;ProRx;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPSCH1 | ST;ProTx;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_P444_21M1 | PROTECTION | CARRIER SEND | Set | Reset | RS_ST_CARR SEND | Transmitted to IEC | [7 empty] | Protection;DisPSCH1 | ST;ProTx;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;EfdPTOC1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DIRECTIONAL E/F START | Set | Reset | RS_OP_DIR E/F S | Transmitted to IEC | [7 empty] | Protection;EfdPTOC1 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;EfdPTOC1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DIRECTIONAL E/F | Operated | Reset | RS_OP_DEF | Transmitted to IEC | [7 empty] | Protection;EfdPTOC1 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;SofPSOF1 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | SOTF | Operated | Reset | RS_OP_SOTF | Transmitted to IEC | [7 empty] | Protection;SofPSOF1 | ST;Op;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;VtpPhsPTOV1 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | OVERVOLTAGE STAGE-1 | Operated | Reset | RS_OP_O/V-I | Transmitted to IEC | [7 empty] | Protection;VtpPhsPTOV1 | ST;Op;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;VtpPhsPTOV1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | OVERVOLTAGE STAGE-1 START | Set | Reset | RS_OP_O/V STG1 S | Transmitted to IEC | [7 empty] | Protection;VtpPhsPTOV1 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;VtpPhsPTOV2 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | OVERVOLTAGE STAGE-2 | Operated | Reset | RS_OP_O/V-II | Transmitted to IEC | [7 empty] | Protection;VtpPhsPTOV2 | ST;Op;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;GosGGIO1 | ST;Ind19;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | STUB PROTECTION | Operated | Reset | RS_OP_STUB | [8 empty] | System;GosGGIO2 | ST;Ind19;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | #REF!
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | R401_P444_21M1
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | Protection;DisPDIS2 | ST;Op;phsA;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE ZONE-2 R-PH TRIP | Operated | Reset | RS_OP_DIS Z1 R | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Op;phsA;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Op;phsB;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE ZONE-2 Y-PH | Operated | Reset | RS_OP_DIS Z1 Y | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Op;phsB;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Op;phsC;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE ZONE-2 B-PH | Operated | Reset | RS_OP_DIS Z1 B | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Op;phsC;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R401_P444_21M1 | PROTECTION | DISTANCE BLOCKED | Set | Reset | RS_ST_DIS BLK | [8 empty] | Protection;DisPDIS | ST;BLK | [14 empty] | 2 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R401_P444_21M1 | PROTECTION | DT SEND CH 1 | Set | Reset | RS_ST_DT_CH-1_S | [24 empty] | 2 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R401_P444_21M1 | PROTECTION | DT SEND CH 2 | Set | Reset | RS_ST_DT_CH-2_S | [24 empty] | 2 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R401_P444_21M1 | SYSTEM | BCU RELAY | Healthy | Unhealthy | RS_ST_BCU | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS | [14 empty] | 2 | #REF!
[6 empty] | SPS | 400kV | R401_P444_21M1 | SYSTEM | PREPARE 3-PH TRIP FROM TIE BCU | Set | Reset | RS_ST_MAIN_3 PH | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS
[6 empty] | SPS | 400kV | R401_P444_21M1 | SYSTEM | PREPARE 3-PH TRIP FROM MAIN BCU | Set | Reset | RS_ST_TIE_3 PH | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS
[6 empty] | SPS | 400kV | R401_P444_21M1 | SYSTEM | MAIN/ TIE CB AR OPTD | Operated | Reset | RS_OP_A/R | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS
[6 empty] | SPS | 400kV | R401_P444_21M1 | SYSTEM | MAIN/ TIE LBB PROTECTION OPERATED | Operated | Reset | RS_OP_LBB | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS
A |  |  |  |  | SPARE | [32 empty] | 2 | #REF!
A |  |  |  |  | SPARE | [32 empty] | 2 | #REF!
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | R401_P444_21M1
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | Records;PriRFLO1 | MX;FltZ;cVal;CMV | MV_hla_Fault_Impd | Z | 400kV | R401_P444_21M1 | PROTECTION | FAULT IMPEDANCE | -100.0 | 100.0 | Fltz | Transmitted to IEC | [7 empty] | Records;PriRFLO1 | MX;FltZ;cVal;CMV | [14 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P444_21M1
A |  |  | Records;PriRFLO1 | MX;FltDiskm;mag;MV | MV_Hla_Fault_Dist | Km | 400kV | R401_P444_21M1 | PROTECTION | FAULT DISTANCE | 0.0 | 1000.0 | FltDiskm | Transmitted to IEC | [7 empty] | Records;PriRFLO1 | MX;FltDiskm;mag;MV | [14 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P444_21M1
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | R401_P444_21M1
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R401_P444_21M1
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | R401_P444_21M1
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P444_21M1
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D73: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E73: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D93: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E93: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC93: HMI Display : Specify if the data appears in HMI.
Note on AD93: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE93: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D101: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E101: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D107: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E107: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB107: LCD Display : Specify if the data appears in computer LCD.
Note on AC107: HMI Display : Specify if the data appears in HMI.
Note on AD107: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE107: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC170: HMI Display : Specify if the data appears in HMI.
Note on AD170: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE170: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB190: LCD Display : Specify if the data appears in computer LCD.
Note on AC190: HMI Display : Specify if the data appears in HMI.
Note on AD190: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE190: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R401_D60_M1
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R401_P444_21M1 |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R401_P444_21M1
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R401_P444_21M1
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R401_D60_21M1 | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P444_21M1
A |  |  | System;AlmGGIO1 | ST;Alm6;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | CVT FUSE | Alarm | Normal | RS_OP_VT-FUSE | Transmitted to IEC | [7 empty] | System;AlmGGIO1 | ST;Alm6;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P444_21M1
A |  |  | System;AlmGGIO1 | ST;Alm31;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | BROKEN CONDUCTOR | Alarm | Normal | RS_OP_BRKN CND | Transmitted to IEC | [7 empty] | System;AlmGGIO1 | ST;Alm31;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P444_21M1
A |  |  | System;GosGGIO2 | ST;Ind15;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R401_D60_21M1 | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind15;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind4;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | SYSTEM | GROUP A TRIP RELAY | Operated | Reset | RS_OP_GRP-A | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind4;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind5;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | SYSTEM | CARRIER CHANNEL-1 | Healthy | Unhealthy | RS_set_CARr1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind5;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind6;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_D60_21M1 | SYSTEM | LINE ISO OPEN FOR STUB PROTN | Set | Reset | RS_ST_ISO_OE_STU | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind6;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind7;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_D60_21M1 | SYSTEM | CB CLOSE CMD SOTF INITIATION | Set | Reset | RS_ST_SOTF | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind7;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind8;stVal;SPS | SPE_HLA_NotRec_Recvd | SPS | 400kV | R401_D60_21M1 | SYSTEM | CARRIER CHANNEL-2 | Received | Not Received | NR_RV_CAR_R_CH2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind8;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind9;stVal;SPS | SPE_HLA_Flty_Healthy | SPS | 400kV | R401_D60_21M1 | SYSTEM | MAIN-2 RELAY | Healthy | Faulty | FL_HL_M2_RLY | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind9;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind10;stVal;SPS | SPE_HLA_NotRec_Recvd | SPS | 400kV | R401_D60_21M1 | SYSTEM | CARRIER CHANNEL-1 | Received | Not Received | NR_RV_CARR CH1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind11;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | SYSTEM | CARRIER CHANNEL-2 | Healthy | Unhealthy | RS_set_CARr2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind11;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind12;stVal;SPS | SPE_HLA_NotRec_Recvd | SPS | 400kV | R401_D60_21M1 | SYSTEM | DIRECT TRIP RECEIVED CH-1 | Received | Not Received | NR_RV_DT_REV_CH1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind12;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind13;stVal;SPS | SPE_HLA_NotRec_Recvd | SPS | 400kV | R401_D60_21M1 | SYSTEM | DIRECT TRIP RECEIVED CH-2 | Received | Not Received | NR_RV_DT_REV_CH2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind13;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind17;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | SYSTEM | GROUP B TRIP RELAY | Operated | Reset | RS_OP_GRP-B | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind17;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind24;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_D60_21M1 | SYSTEM | TRIP RELAY 86A SUPERVISION | Healthy | Unhealthy | RS_ST_86A SUPV | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind24;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Control;PsbRPSB3 | ST;Str;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | POWER SWING DETECTED | Set | Reset | RS_AL_PSB_STR | Transmitted to IEC | [7 empty] | Protection;PwrSwgRPSB1 | ST;Str |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Control;PsbRPSB3 | ST;BlkZn;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | POWER SWING BLOCKING | Set | Reset | RS_OP_PWR SW BLK | Transmitted to IEC | [7 empty] | Protection;PwrSwgRPSB1 | ST;BlkZn |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;PTRC1 | ST;Tr;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | GENERAL TRIP | Operated | Reset | RS_OP_GEN TRIP | Transmitted to IEC | [7 empty] | Prot.TrOutPTRC1 | ST;Tr |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsA;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE ZONE-1 R-PH TRIP | Operated | Reset | RS_OP_Z1R-PH | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phs1 |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsB;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE ZONE-1 Y-PH TRIP | Operated | Reset | RS_OP_Z1Y-PH | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phs2 |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsC;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE ZONE-1 B-PH TRIP | Operated | Reset | RS_OP_Z1B-PH | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phs3 |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE PROTN ZONE-1 | Operated | Reset | RS_OP_ZONE-1 | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE ZONE-1 START | Set | Reset | RS_OP_DIS S Z1 | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Str |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE PROTN ZONE-2 | Operated | Reset | RS_OP_ZONE-2 | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Str;phsA;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE ZONE-2 START R-PH | Set | Reset | RS_OP_DIS S Z2_R | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;str;phs1 |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Str;phsB;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE ZONE-2 START Y-PH | Set | Reset | RS_OP_DIS S Z2_Y | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;str;phs2 |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Str;phsC;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE ZONE-2 START B-PH | Set | Reset | RS_OP_DIS S Z2_B | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;str;phs3 |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE ZONE-2 START | Set | Reset | RS_OP_DIS S Z2 | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Str |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS3 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE PROTN ZONE-3 | Operated | Reset | RS_OP_ZONE-3 | Transmitted to IEC | [7 empty] | Protection;DisPDIS3 | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS3 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE ZONE-3 START | Set | Reset | RS_OP_DIS S Z3 | Transmitted to IEC | [7 empty] | Protection;DisPDIS3 | ST;Str |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS4 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE PROTN ZONE-4 | Operated | Reset | RS_OP_ZONE-4 | Transmitted to IEC | [7 empty] | Protection;DisPDIS4 | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS4 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE ZONE-4 START | Set | Reset | RS_OP_DIS S Z4 | Transmitted to IEC | [7 empty] | Protection;DisPDIS4 | ST;Str |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS5 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE PROTN ZONE-5 | Operated | Reset | RS_OP_ZONE-5 | Transmitted to IEC | [7 empty] | Protection;DisPDIS5 | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS5 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE ZONE-5 START | Set | Reset | RS_OP_DIS S Z5 | Transmitted to IEC | [7 empty] | Protection;DisPDIS5 | ST;Str |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPSCH1 | ST;CarRx;general;ACT | SPE_HLa_Reset_Set | SPS | 400kV | R401_D60_21M1 | PROTECTION | CARRIER AIDED SCHEME | Operated | Reset | RS_ST_CARR_AIDED | Transmitted to IEC | [7 empty] | Protection;DisPSCH1 | ST;CarRx |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPSCH1 | ST;ProRx;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_D60_21M1 | PROTECTION | CARRIER RECEIVE | Set | Reset | RS_ST_CARR REC | Transmitted to IEC | [7 empty] | Protection;DisPSCH1 | ST;ProRx |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPSCH1 | ST;ProTx;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_D60_21M1 | PROTECTION | CARRIER SEND | Set | Reset | RS_ST_CARR SEND | Transmitted to IEC | [7 empty] | Protection;DisPSCH1 | ST;ProTx |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;EfdPTOC1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DIRECTIONAL E/F START | Set | Reset | RS_OP_DIR E/F S | Transmitted to IEC | [7 empty] | Prot.NeuTocPTOC1 | ST;Str |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;EfdPTOC1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DIRECTIONAL E/F | Operated | Reset | RS_OP_DEF | Transmitted to IEC | [7 empty] | Prot.NeuTocPTOC1 | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;SofPSOF1 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | SOTF | Operated | Reset | RS_OP_SOTF | Transmitted to IEC | [7 empty] | Protection;SofPSOF | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;VtpPhsPTOV1 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | OVERVOLTAGE STAGE-1 | Operated | Reset | RS_OP_O/V-I | Transmitted to IEC | [7 empty] | Prot.PhsOvPTOV1 | ST;Str |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;VtpPhsPTOV1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | OVERVOLTAGE STAGE-1 START | Set | Reset | RS_OP_O/V STG1 S | Transmitted to IEC | [7 empty] | Prot.PhsOvPTOV1 | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;VtpPhsPTOV2 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | OVERVOLTAGE STAGE-2 | Operated | Reset | RS_OP_O/V-II | Transmitted to IEC | [7 empty] | Prot.PhsOvPTOV2 | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;GosGGIO1 | ST;Ind19;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | STUB PROTECTION | Operated | Reset | RS_OP_STUB | [8 empty] | System;GosGGIO2 | ST;Ind19;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | #REF!
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | R401_P444_21M1
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | Protection;DisPDIS2 | ST;Op;phsA;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE ZONE-2 R-PH | Operated | Reset | RS_OP_DIS Z1 R | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Op;phs1 |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Op;phsB;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE ZONE-2 Y-PH | Operated | Reset | RS_OP_DIS Z1 Y | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Op;phs2 |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Op;phsC;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE ZONE-2 B-PH | Operated | Reset | RS_OP_DIS Z1 B | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Op;phs3 |  |  | None | [11 empty] | 1 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R401_D60_21M1 | PROTECTION | DISTANCE BLOCKED | Set | Reset | RS_ST_DIS BLK | [8 empty] | Protection;DisPDIS | ST;BLK | [14 empty] | 2 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R401_D60_21M1 | PROTECTION | DT SEND CH 1 | Set | Reset | RS_ST_DT_CH-1_S | [24 empty] | 2 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R401_D60_21M1 | PROTECTION | DT SEND CH 2 | Set | Reset | RS_ST_DT_CH-2_S | [24 empty] | 2 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R401_D60_21M1 | SYSTEM | BCU RELAY | Healthy | Unhealthy | RS_ST_BCU | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS | [14 empty] | 2 | #REF!
[6 empty] | SPS | 400kV | R401_D60_21M1 | SYSTEM | PREPARE 3-PH TRIP FROM TIE BCU | Set | Reset | RS_ST_MAIN_3 PH | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS
[6 empty] | SPS | 400kV | R401_D60_21M1 | SYSTEM | PREPARE 3-PH TRIP FROM MAIN BCU | Set | Reset | RS_ST_TIE_3 PH | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS
[6 empty] | SPS | 400kV | R401_D60_21M1 | SYSTEM | MAIN/ TIE CB AR OPTD | Operated | Reset | RS_OP_A/R | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS
[6 empty] | SPS | 400kV | R401_D60_21M1 | SYSTEM | MAIN/ TIE LBB PROTECTION OPERATED | Operated | Reset | RS_OP_LBB | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | #REF!
SPC
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | #REF!
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | R401_P444_21M1
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | Records;PriRFLO1 | MX;FltZ;cVal;CMV | MV_hla_Fault_Impd | Z | 400kV | R401_P444_21M1 | PROTECTION | FAULT IMPEDANCE | -100.0 | 100.0 | Fltz | Transmitted to IEC | [7 empty] | Records;PriRFLO1 | MX;FltZ;cVal;CMV | [14 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P444_21M1
A |  |  | Records;PriRFLO1 | MX;FltDiskm;mag;MV | MV_Hla_Fault_Dist | Km | 400kV | R401_P444_21M1 | PROTECTION | FAULT DISTANCE | 0.0 | 1000.0 | FltDiskm | Transmitted to IEC | [7 empty] | Records;PriRFLO1 | MX;FltDiskm;mag;MV | [14 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P444_21M1
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | R401_P444_21M1
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R401_P444_21M1
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | R401_P444_21M1
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P444_21M1
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D73: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E73: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D93: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E93: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC93: HMI Display : Specify if the data appears in HMI.
Note on AD93: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE93: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D101: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E101: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D107: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E107: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB107: LCD Display : Specify if the data appears in computer LCD.
Note on AC107: HMI Display : Specify if the data appears in HMI.
Note on AD107: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE107: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC170: HMI Display : Specify if the data appears in HMI.
Note on AD170: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE170: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB190: LCD Display : Specify if the data appears in computer LCD.
Note on AC190: HMI Display : Specify if the data appears in HMI.
Note on AD190: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE190: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R401_L90_M2
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R401_P444_21M1 |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R401_P444_21M1
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R401_P444_21M1
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R401_L90_21M1 | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P444_21M1
A |  |  | System;AlmGGIO1 | ST;Alm6;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | CVT FUSE | Alarm | Normal | RS_OP_VT-FUSE | Transmitted to IEC | [7 empty] | System;AlmGGIO1 | ST;Alm6;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P444_21M1
A |  |  | System;AlmGGIO1 | ST;Alm31;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | BROKEN CONDUCTOR | Alarm | Normal | RS_OP_BRKN CND | Transmitted to IEC | [7 empty] | System;AlmGGIO1 | ST;Alm31;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P444_21M1
A |  |  | System;GosGGIO2 | ST;Ind15;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R401_L90_21M1 | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind15;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind4;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | SYSTEM | GROUP A TRIP RELAY | Operated | Reset | RS_OP_GRP-A | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind4;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind5;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | SYSTEM | CARRIER CHANNEL-1 | Healthy | Unhealthy | RS_set_CARr1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind5;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind6;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_L90_21M1 | SYSTEM | LINE ISO OPEN FOR STUB PROTN | Set | Reset | RS_ST_ISO_OE_STU | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind6;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind7;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_L90_21M1 | SYSTEM | CB CLOSE CMD SOTF INITIATION | Set | Reset | RS_ST_SOTF | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind7;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind8;stVal;SPS | SPE_HLA_NotRec_Recvd | SPS | 400kV | R401_L90_21M1 | SYSTEM | CARRIER CHANNEL-2 | Received | Not Received | NR_RV_CAR_R_CH2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind8;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind9;stVal;SPS | SPE_HLA_Flty_Healthy | SPS | 400kV | R401_L90_21M1 | SYSTEM | MAIN-2 RELAY | Healthy | Faulty | FL_HL_M2_RLY | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind9;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind10;stVal;SPS | SPE_HLA_NotRec_Recvd | SPS | 400kV | R401_L90_21M1 | SYSTEM | CARRIER CHANNEL-1 | Received | Not Received | NR_RV_CARR CH1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind11;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | SYSTEM | CARRIER CHANNEL-2 | Healthy | Unhealthy | RS_set_CARr2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind11;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind12;stVal;SPS | SPE_HLA_NotRec_Recvd | SPS | 400kV | R401_L90_21M1 | SYSTEM | DIRECT TRIP RECEIVED CH-1 | Received | Not Received | NR_RV_DT_REV_CH1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind12;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind13;stVal;SPS | SPE_HLA_NotRec_Recvd | SPS | 400kV | R401_L90_21M1 | SYSTEM | DIRECT TRIP RECEIVED CH-2 | Received | Not Received | NR_RV_DT_REV_CH2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind13;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind17;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | SYSTEM | GROUP B TRIP RELAY | Operated | Reset | RS_OP_GRP-B | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind17;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind24;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_L90_21M1 | SYSTEM | TRIP RELAY 86B SUPERVISION | Healthy | Unhealthy | RS_ST_86A SUPV | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind24;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Control;PsbRPSB3 | ST;Str;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | POWER SWING DETECTED | Set | Reset | RS_AL_PSB_STR | Transmitted to IEC | [7 empty] | Protection;PwrSwgRPSB1 | ST;Str |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Control;PsbRPSB3 | ST;BlkZn;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | POWER SWING BLOCKING | Set | Reset | RS_OP_PWR SW BLK | Transmitted to IEC | [7 empty] | Protection;PwrSwgRPSB1 | ST;BlkZn |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;PTRC1 | ST;Tr;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | GENERAL TRIP | Operated | Reset | RS_OP_GEN TRIP | Transmitted to IEC | [7 empty] | Prot.TrOutPTRC1 | ST;Tr |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsA;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE ZONE-1 R-PH | Operated | Reset | RS_OP_Z1R-PH | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phs1 |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsB;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE ZONE-1 Y-PH | Operated | Reset | RS_OP_Z1Y-PH | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phs2 |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsC;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE ZONE-1 B-PH | Operated | Reset | RS_OP_Z1B-PH | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phs3 |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE PROTN ZONE-1 | Operated | Reset | RS_OP_ZONE-1 | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE ZONE-1 START | Set | Reset | RS_OP_DIS S Z1 | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Str |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE PROTN ZONE-2 | Operated | Reset | RS_OP_ZONE-2 | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Str;phsA;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE ZONE-2 START R-PH | Set | Reset | RS_OP_DIS S Z2_R | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;str;phs1 |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Str;phsB;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE ZONE-2 START Y-PH | Set | Reset | RS_OP_DIS S Z2_Y | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;str;phs2 |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Str;phsC;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE ZONE-2 START B-PH | Set | Reset | RS_OP_DIS S Z2_B | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;str;phs3 |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE ZONE-2 START | Set | Reset | RS_OP_DIS S Z2 | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Str |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS3 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE PROTN ZONE-3 | Operated | Reset | RS_OP_ZONE-3 | Transmitted to IEC | [7 empty] | Protection;DisPDIS3 | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS3 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE ZONE-3 START | Set | Reset | RS_OP_DIS S Z3 | Transmitted to IEC | [7 empty] | Protection;DisPDIS3 | ST;Str |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS4 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE PROTN ZONE-4 | Operated | Reset | RS_OP_ZONE-4 | Transmitted to IEC | [7 empty] | Protection;DisPDIS4 | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS4 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE ZONE-4 START | Set | Reset | RS_OP_DIS S Z4 | Transmitted to IEC | [7 empty] | Protection;DisPDIS4 | ST;Str |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS5 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE PROTN ZONE-5 | Operated | Reset | RS_OP_ZONE-5 | Transmitted to IEC | [7 empty] | Protection;DisPDIS5 | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS5 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE ZONE-5 START | Set | Reset | RS_OP_DIS S Z5 | Transmitted to IEC | [7 empty] | Protection;DisPDIS5 | ST;Str |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPSCH1 | ST;CarRx;general;ACT | SPE_HLa_Reset_Set | SPS | 400kV | R401_L90_21M1 | PROTECTION | CARRIER AIDED SCHEME | Operated | Reset | RS_ST_CARR_AIDED | Transmitted to IEC | [7 empty] | Protection;DisPSCH1 | ST;CarRx |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPSCH1 | ST;ProRx;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_L90_21M1 | PROTECTION | CARRIER RECEIVE | Set | Reset | RS_ST_CARR REC | Transmitted to IEC | [7 empty] | Protection;DisPSCH1 | ST;ProRx |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPSCH1 | ST;ProTx;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_L90_21M1 | PROTECTION | CARRIER SEND | Set | Reset | RS_ST_CARR SEND | Transmitted to IEC | [7 empty] | Protection;DisPSCH1 | ST;ProTx |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;EfdPTOC1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DIRECTIONAL E/F START | Set | Reset | RS_OP_DIR E/F S | Transmitted to IEC | [7 empty] | Prot.NeuTocPTOC1 | ST;Str |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;EfdPTOC1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DIRECTIONAL E/F | Operated | Reset | RS_OP_DEF | Transmitted to IEC | [7 empty] | Prot.NeuTocPTOC1 | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;SofPSOF1 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | SOTF | Operated | Reset | RS_OP_SOTF | Transmitted to IEC | [7 empty] | Protection;SofPSOF | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;VtpPhsPTOV1 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | OVERVOLTAGE STAGE-1 | Operated | Reset | RS_OP_O/V-I | Transmitted to IEC | [7 empty] | Prot.PhsOvPTOV1 | ST;Str |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;VtpPhsPTOV1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | OVERVOLTAGE STAGE-1 START | Set | Reset | RS_OP_O/V STG1 S | Transmitted to IEC | [7 empty] | Prot.PhsOvPTOV1 | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;VtpPhsPTOV2 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | OVERVOLTAGE STAGE-2 | Operated | Reset | RS_OP_O/V-II | Transmitted to IEC | [7 empty] | Prot.PhsOvPTOV2 | ST;Op |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;GosGGIO1 | ST;Ind19;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | STUB PROTECTION | Operated | Reset | RS_OP_STUB | [8 empty] | System;GosGGIO2 | ST;Ind19;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | R401_L90_21M1 | PROTECTION | LINE DIFFERENTIAL R PH | Operated | Reset | RS_OP_DIF R | Transmitted to IEC
[6 empty] | SPS | 400kV | R401_L90_21M1 | PROTECTION | LINE DIFFERENTIAL Y PH | Operated | Reset | RS_OP_DIF Y | Transmitted to IEC
[6 empty] | SPS | 400kV | R401_L90_21M1 | PROTECTION | LINE DIFFERENTIAL B PH | Operated | Reset | RS_OP_DIF B | Transmitted to IEC
[6 empty] | SPS | 400kV | R401_L90_21M1 | PROTECTION | LINE DIFFERENTIAL | Start | Reset | RS_ST_DIF | Transmitted to IEC
[6 empty] | SPS | 400kV | R401_L90_21M1 | PROTECTION | DIFFERENTIAL COMMUNICATION FAIL | Set | Reset | RS_ST_DIFF_COM
[6 empty] | SPS | 400kV | R401_L90_21M1 | PROTECTION | DIFFERENTIAL BLOCKED | Set | Reset | RS_ST_DIFF_BLK
[6 empty] | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE ENABLED | Set | Reset | RS_ST_DIS_EN
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | R401_P444_21M1
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | Protection;DisPDIS2 | ST;Op;phsA;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE ZONE-2 R-PH TRIP | Operated | Reset | RS_OP_DIS Z1 R | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Op;phs1 |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Op;phsB;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE ZONE-2 Y-PH TRIP | Operated | Reset | RS_OP_DIS Z1 Y | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Op;phs2 |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Op;phsC;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE ZONE-2 B-PH TRIP | Operated | Reset | RS_OP_DIS Z1 B | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Op;phs3 |  |  | None | [11 empty] | 1 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R401_L90_21M1 | PROTECTION | DISTANCE BLOCKED | Set | Reset | RS_ST_DIS BLK | [8 empty] | Protection;DisPDIS | ST;BLK | [14 empty] | 2 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R401_L90_21M1 | PROTECTION | DT SEND CH 1 | Set | Reset | RS_ST_DT_CH-1_S | [24 empty] | 2 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R401_L90_21M1 | PROTECTION | DT SEND CH 2 | Set | Reset | RS_ST_DT_CH-2_S | [24 empty] | 2 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R401_L90_21M1 | SYSTEM | BCU RELAY | Healthy | Unhealthy | RS_ST_BCU | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS | [14 empty] | 2 | #REF!
[6 empty] | SPS | 400kV | R401_L90_21M1 | SYSTEM | PREPARE 3-PH TRIP FROM TIE BCU | Set | Reset | RS_ST_MAIN_3 PH | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS
[6 empty] | SPS | 400kV | R401_L90_21M1 | SYSTEM | PREPARE 3-PH TRIP FROM MAIN BCU | Set | Reset | RS_ST_TIE_3 PH | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS
[6 empty] | SPS | 400kV | R401_L90_21M1 | SYSTEM | MAIN/ TIE CB AR OPTD | Operated | Reset | RS_OP_A/R | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS
[6 empty] | SPS | 400kV | R401_L90_21M1 | SYSTEM | MAIN/ TIE LBB PROTECTION OPERATED | Operated | Reset | RS_OP_LBB | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS
RS_ST_DIS_EN
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | #REF!
SPC
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | #REF!
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | R401_P444_21M1
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | Records;PriRFLO1 | MX;FltZ;cVal;CMV | MV_hla_Fault_Impd | Z | 400kV | R401_P444_21M1 | PROTECTION | FAULT IMPEDANCE | -100.0 | 100.0 | Fltz | Transmitted to IEC | [7 empty] | Records;PriRFLO1 | MX;FltZ;cVal;CMV | [14 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P444_21M1
A |  |  | Records;PriRFLO1 | MX;FltDiskm;mag;MV | MV_Hla_Fault_Dist | Km | 400kV | R401_P444_21M1 | PROTECTION | FAULT DISTANCE | 0.0 | 1000.0 | FltDiskm | Transmitted to IEC | [7 empty] | Records;PriRFLO1 | MX;FltDiskm;mag;MV | [14 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P444_21M1
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | R401_P444_21M1
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R401_P444_21M1
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | R401_P444_21M1
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P444_21M1
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P444_21M1
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D75: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E75: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D95: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E95: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC95: HMI Display : Specify if the data appears in HMI.
Note on AD95: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE95: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D103: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E103: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D109: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E109: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB109: LCD Display : Specify if the data appears in computer LCD.
Note on AC109: HMI Display : Specify if the data appears in HMI.
Note on AD109: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE109: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC172: HMI Display : Specify if the data appears in HMI.
Note on AD172: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE172: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB192: LCD Display : Specify if the data appears in computer LCD.
Note on AC192: HMI Display : Specify if the data appears in HMI.
Note on AD192: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE192: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R401_P546_21M2
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R401_P546_21M2 |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R401_P546_21M2
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R401_P546_21M2
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R401_P546_21M2 | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P546_21M2
A |  |  | System;AlmGGIO1 | ST;Alm6;stVal;SPS | SPE_HLA_Normal_Fail | SPS | 400kV | R401_P546_21M2 | PROTECTION | CVT FUSE FAIL | Alarm | Normal | NL_FL_CVT FUSE | Transmitted to IEC | [7 empty] | System;AlmGGIO1 | ST;Alm6;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P546_21M2
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R401_P546_21M2 | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind13;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R401_P546_21M2 | PROTECTION | BROKEN CONDUCTOR | Alarm | Normal | NL_AL_BROKEN CON | Transmitted to IEC | [7 empty] | System;AlmGGIO1 | ST;Ind31;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind1;stVal;SPS | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | R401_P546_21M2 | SYSTEM | CARRIER CHANNEL-2 | Healthy | Unhealthy | UN_HL_CARR CH-2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind1;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind2;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | SYSTEM | 86B TRIP RLY | Operated | Reset | RS_OP_86B RLY | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind2;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind4;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | SYSTEM | MAIN -1 PROTECTION | Operated | Reset | RS_OP_M1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind4;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind8;stVal;SPS | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | R401_P546_21M2 | SYSTEM | TRIP RELAY 86B SUPERVISION | Healthy | Unhealthy | UN_HL_86B SUPV | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind8;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind19;stVal;SPS | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | R401_P546_21M2 | SYSTEM | BCU HEALTHY | Healthy | Unhealthy | UN_HL_BCU | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind19;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind20;stVal;SPS | SPE_HLA_NotRec_Recvd | SPS | 400kV | R401_P546_21M2 | SYSTEM | CARRIER CHANNEL-2 | Received | Not Received | NR_RV_CARR CH-2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind20;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind21;stVal;SPS | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | R401_P546_21M2 | SYSTEM | MAIN-1 RELAY | Healthy | Unhealthy | UN_HL_M1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind21;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind22;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R401_P546_21M2 | SYSTEM | LINE ISOL OPEN FOR STUB PROTN | Set | Reset | NL_AL_ISO | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind22;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind23;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R401_P546_21M2 | SYSTEM | SOTF INITIATION | Set | Reset | NL_AL_SOTF | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind23;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind24;stVal;SPS | SPE_HLA_NotRec_Recvd | SPS | 400kV | R401_P546_21M2 | SYSTEM | CARRIER CHANNEL-1 | Received | Not Received | NR_RV_CARR CH-1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind24;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Control;PsbRPSB3 | ST;Str1;general;ACD | SPE_HLA_Normal_Alarm | SPS | 400kV | R401_P546_21M2 | PROTECTION | POWER SWING DETECTED | Set | Reset | NL_AL_PWR SW DET | Transmitted to IEC | [7 empty] | Control;PsbRPSB3 | ST;Str;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Control;PsbRPSB3 | ST;BlkZn;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | POWER SWING BLOCKING | Set | Reset | RS_OP_PWR SW BLK | Transmitted to IEC | [7 empty] | Control;PsbRPSB3 | ST;BlkZn;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;PTRC1 | ST;Tr;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | GENERAL TRIP | Operated | Reset | RS_OP_GEN TRIP | Transmitted to IEC | [7 empty] | Protection;PTRC1 | ST;Tr;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DifPDIF1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | LINE DIFFERENTIAL | Operated | Reset | RS_OP_DIF | Transmitted to IEC | [7 empty] | Protection;DifPDIF1 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsA;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-1 R-PH | Operated | Reset | RS_OP_DIS Z1 R | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phsA;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsB;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-1 Y-PH | Operated | Reset | RS_OP_DIS Z1 Y | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phsB;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsC;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-1 B-PH | Operated | Reset | RS_OP_DIS Z1 B | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phsC;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-1 | Operated | Reset | RS_OP_DIS Z1 | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-1 START | Set | Reset | RS_OP_DIS S Z1 | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-2 | Operated | Reset | RS_OP_DIS Z2 | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-2 START | Set | Reset | RS_OP_DIS S Z2 | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS3 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-3 | Operated | Reset | RS_OP_DIS Z3 | Transmitted to IEC | [7 empty] | Protection;DisPDIS3 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS3 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-3 START | Set | Reset | RS_OP_DIS S Z3 | Transmitted to IEC | [7 empty] | Protection;DisPDIS3 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS4 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-4 | Operated | Reset | RS_OP_DIS Z4 | Transmitted to IEC | [7 empty] | Protection;DisPDIS4 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS4 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-4 START | Set | Reset | RS_OP_DIS S Z4 | Transmitted to IEC | [7 empty] | Protection;DisPDIS4 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;EfdPTOC1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DIRECTIONAL E/F | Operated | Reset | RS_OP_DIR E/F | Transmitted to IEC | [7 empty] | Protection;EfdPTOC1 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;EfdPTOC1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DIRECTIONAL E/F START | Set | Reset | RS_OP_DIR E/F S | Transmitted to IEC | [7 empty] | Protection;EfdPTOC1 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;SofPSOF1 | ST;Op1;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | SOTF | Operated | Reset | RS_OP_SOTF | Transmitted to IEC | [7 empty] | Protection;SofPSOF1 | ST;Op1;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;VtpPhsPTOV1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | OVERVOLTAGE STAGE-1 | Operated | Reset | RS_OP_O/V STG1 | Transmitted to IEC | [7 empty] | Protection;VtpPhsPTOV1 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;VtpPhsPTOV1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | OVERVOLTAGE STAGE-1 START | Set | Reset | RS_OP_O/V STG1 S | Transmitted to IEC | [7 empty] | Protection;VtpPhsPTOV1 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;VtpPhsPTOV2 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | OVERVOLTAGE STAGE-2 | Operated | Reset | RS_OP_O/V STG2 | Transmitted to IEC | [7 empty] | Protection;VtpPhsPTOV2 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;GosGGIO1 | ST;Ind19;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | STUB PROTECTION | Operated | Reset | RS_OP_STUB | [8 empty] | System;GosGGIO2 | ST;Ind7;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | 0
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | R401_P546_21M2
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | Protection;DisPDIS5 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-5 START | Set | Reset | RS_OP_DIS S Z5 | Transmitted to IEC | [7 empty] | Protection;DisPDIS5 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPSCH1 | ST;ProRx;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_P546_21M2 | PROTECTION | CARRIER RECEIVE | Set | Reset | RS_ST_CARR REC | Transmitted to IEC | [7 empty] | Protection;DisPSCH1 | ST;ProRx;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPSCH1 | ST;ProTx;stVal;SPS | SPE_HLa_Reset_Set | SPS | 400kV | R401_P546_21M2 | PROTECTION | CARRIER SEND | Set | Reset | RS_ST_CARR SEND | Transmitted to IEC | [7 empty] | Protection;DisPSCH1 | ST;ProTx;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Op;phsA;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-2 R-PH | Operated | Reset | RS_OP_DIS Z2 R | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Op;phsA;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Op;phsB;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-2 Y-PH | Operated | Reset | RS_OP_DIS Z2 Y | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Op;phsB;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Op;phsC;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-2 B-PH | Operated | Reset | RS_OP_DIS Z2 B | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Op;phsC;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Str;phsA;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-2 START R-PH | Set | Reset | RS_OP_DIS S Z2 R | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Str;phsA;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Str;phsB;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-2 START Y-PH | Set | Reset | RS_OP_DIS S Z2 Y | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Str;phsB;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS2 | ST;Str;phsC;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-2 START B-PH | Set | Reset | RS_OP_DIS S Z2 B | Transmitted to IEC | [7 empty] | Protection;DisPDIS2 | ST;Str;phsC;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS4 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | DISTANCE ZONE-5 | Operated | Reset | RS_OP_DIS Z5 | Transmitted to IEC | [7 empty] | Protection;DisPDIS5 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  |  |  | SPARE | SPC | 400kV | R401_P546_21M2 | PROTECTION | CARRIER AIDED SCHEME | Operated | Reset | RS_ST_CARR_AIDED | Transmitted to IEC | [7 empty] | Protection;DisPSCH1 | ST;CarRx;general;ACT | [14 empty] | 2 | #REF!
A |  |  | Protection;DifPDIF1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P546_21M2 | PROTECTION | LINE DIFFERENTIAL R PH | Operated | Reset | RS_OP_DIF R | Transmitted to IEC | [7 empty] | Protection;DifPDIF1 | ST;Op;phsA;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  |  |  | SPARE | SPC | 400kV | R401_P546_21M2 | PROTECTION | LINE DIFFERENTIAL Y PH | Operated | Reset | RS_OP_DIF Y | Transmitted to IEC | [7 empty] | Protection;DifPDIF1 | ST;Op;phsB;general;ACT | [14 empty] | 2 | #REF!
A |  |  |  |  | SPARE | SPC | 400kV | R401_P546_21M2 | PROTECTION | LINE DIFFERENTIAL B PH | Operated | Reset | RS_OP_DIF B | Transmitted to IEC | [7 empty] | Protection;DifPDIF1 | ST;Op;phsC;general;ACT | [14 empty] | 2 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R401_P546_21M2 | PROTECTION | LINE DIFFERENTIAL | START | Reset | RS_ST_DIF | Transmitted to IEC | [7 empty] | Protection;DifPDIF1 | ST;Str;general;general;ACT | [14 empty] | 2 | #REF!
[6 empty] | SPS | 400kV | R401_P546_21M2 | SYSTEM | CARRIER CHANNEL-1 | Healthy | Unhealthy | UN_HL_CARR CH-1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind9;stVal;SPS
[6 empty] | SPS | 400kV | R401_P546_21M2 | SYSTEM | DIRECT TRIP CHANNEL-1 | RECEIVED | NOT RECEIVED | NR_RC_DT-1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
A |  |  |  |  | SPARE | SPS | 400kV | R401_P546_21M2 | SYSTEM | DIRECT TRIP CHANNEL-2 | RECEIVED | NOT RECEIVED | NR_RC_DT-2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind11;stVal;SPS | [14 empty] | 2 | #REF!
[6 empty] | SPS | 400kV | R401_P546_21M3 | PROTECTION | DISTANCE ENABLED | Set | Reset | RS_ST_DIS_EN
[6 empty] | SPS | 400kV | R401_P546_21M4 | PROTECTION | DT SEND CH 1 | Set | Reset | RS_ST_DT_CH-1_S
[6 empty] | SPS | 400kV | R401_P546_21M5 | PROTECTION | DT SEND CH 2 | Set | Reset | RS_ST_DT_CH-2_S
[6 empty] | SPS | 400kV | R401_P546_21M6 | SYSTEM | MAIN/ TIE CB AR OPTD | Operated | Reset | RS_OP_A/R | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS
[6 empty] | SPS | 400kV | R401_P546_21M7 | SYSTEM | MAIN/ TIE LBB PROTECTION OPERATED | Operated | Reset | RS_OP_LBB | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS
[6 empty] | SPS | 400kV | R401_P546_21M9 | SYSTEM | BCU RELAY | Healthy | Unhealthy | RS_ST_BCU | [8 empty] | System;OptGGIO1 | ST;Indx;stVal;SPS
[6 empty] | SPS | 400kV | R401_P546_21M9 | PROTECTION | DIFFERENTIAL COMMUNICATION FAIL | Set | Reset | RS_ST_DIFF_COM
[6 empty] | SPS | 400kV | R401_P546_21M10 | PROTECTION | DIFFERENTIAL BLOCKED | Set | Reset | RS_ST_DIFF_BLK
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | R401_P546_21M2
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | Records;RFLO1 | MX;FltZ;cVal;CMV | MV_hla_Fault_Impd_2 | Z | 400kV | R401_P546_21M2 | RECORDS | Fltz | -100.0 | 100.0 | Fltz | Transmitted to IEC | [7 empty] | Records;RFLO1 | MX;FltZ;cVal;CMV | [14 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P546_21M2
A |  |  | Records;RFLO1 | MX;FltDiskm;mag;MV | MV_Hla_Fault_Dist_1 | Km | 400kV | R401_P546_21M2 | RECORDS | FltDiskm | 0.0 | 1000.0 | FltDiskm | Transmitted to IEC | [7 empty] | Records;RFLO1 | MX;FltDiskm;mag;MV | [14 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P546_21M2
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P546_21M2
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P546_21M2
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | R401_P546_21M2
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R401_P546_21M2
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R401_P546_21M2
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | R401_P546_21M2
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P546_21M2
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P546_21M2
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P546_21M2
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P546_21M2
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D64: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E64: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D95: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E95: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC95: HMI Display : Specify if the data appears in HMI.
Note on AD95: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE95: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D103: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E103: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D109: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E109: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB109: LCD Display : Specify if the data appears in computer LCD.
Note on AC109: HMI Display : Specify if the data appears in HMI.
Note on AD109: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE109: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC172: HMI Display : Specify if the data appears in HMI.
Note on AD172: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE172: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB192: LCD Display : Specify if the data appears in computer LCD.
Note on AC192: HMI Display : Specify if the data appears in HMI.
Note on AD192: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE192: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R401_P743_PU_A
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R401_P743_PU_A |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R401_P743_PU_A
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R401_P743_PU_A
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R401_P743_PU_A | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P743_PU_A
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R401_P743_PU_A | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | [8 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P743_PU_A
A |  |  | System;GosGGIO2 | ST;Ind1;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P743_PU_A | GOOSE | LBB START | Set | Reset | RS_OP_LBB START | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind1;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P743_PU_A
A |  |  | System;OptGGIO1 | ST;Ind7;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P743_PU_A | SYSTEM | LBB INITIATION 3-PH | set | Reset | RS_OP_LBB INI 3P | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind7;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind9;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P743_PU_A | SYSTEM | LBB INITIATION R-PH | set | Reset | RS_OP_LBB INI R | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind9;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind10;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P743_PU_A | SYSTEM | LBB INITIATION Y-PH | set | Reset | RS_OP_LBB INI Y | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind11;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P743_PU_A | SYSTEM | LBB INITIATION B-PH | set | Reset | RS_OP_LBB INI B | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind11;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind12;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P743_PU_A | SYSTEM | TIE LBB TO INIT BB | set | Reset | RS_OP_T LBB OPTD | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind12;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CbfBbpRBRF1 | ST;OpIn;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P743_PU_A | PROTECTION | EXTERNAL BREAKER FAILURE RETRIP | Operated | Reset | RS_OP_CB FAIL S1 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF1 | ST;OpIn;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CbfBbpRBRF2 | ST;OpEx;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P743_PU_A | PROTECTION | EXTERNAL BREAKER FAILURE BACK TRIP | Operated | Reset | RS_OP_CB FAIL S2 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF2 | ST;OpEx;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R401_P743_PU_A | PROTECTION | BREAKER FAILURE RETRIP | Operated | Reset | RS_OP_CB FAIL S3 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF3 | ST;OpIn;general;ACT |  |  | None |  | No | [9 empty] | 1 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R401_P743_PU_A | PROTECTION | BREAKER FAILURE BACK TRIP | Operated | Reset | RS_OP_CB FAIL S4 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF4 | ST;OpEx;general;ACT |  |  | None |  | No | [9 empty] | 1 | #REF!
[8 empty] | R401_P743_PU_A | SYSTEM | B/B PU-B HEALTHY | Healthy | Unhealthy | UN_HL_BB_PU B
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | #REF!
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | R401_P743_PU_A
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_A
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | R401_P743_PU_A
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P743_PU_A
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | R401_P743_PU_A
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R401_P743_PU_A
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R401_P743_PU_A
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | R401_P743_PU_A
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P743_PU_A
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D39: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E39: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D53: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E53: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC53: HMI Display : Specify if the data appears in HMI.
Note on AD53: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE53: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D61: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E61: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D67: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E67: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB67: LCD Display : Specify if the data appears in computer LCD.
Note on AC67: HMI Display : Specify if the data appears in HMI.
Note on AD67: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE67: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC130: HMI Display : Specify if the data appears in HMI.
Note on AD130: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE130: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB150: LCD Display : Specify if the data appears in computer LCD.
Note on AC150: HMI Display : Specify if the data appears in HMI.
Note on AD150: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE150: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R401_P743_PU_B
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R401_P743_PU_B |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R401_P743_PU_B
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R401_P743_PU_B
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R401_P743_PU_B | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P743_PU_B
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R401_P743_PU_B | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | [8 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P743_PU_B
A |  |  | System;GosGGIO2 | ST;Ind1;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P743_PU_B | GOOSE | LBB START | Set | Reset | RS_OP_LBB START | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind1;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R401_P743_PU_B
A |  |  | System;OptGGIO1 | ST;Ind7;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P743_PU_B | SYSTEM | LBB INITIATION 3-PH | set | Reset | RS_OP_LBB INI 3P | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind7;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind9;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P743_PU_B | SYSTEM | LBB INITIATION R-PH | set | Reset | RS_OP_LBB INI R | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind9;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind10;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P743_PU_B | SYSTEM | LBB INITIATION Y-PH | set | Reset | RS_OP_LBB INI Y | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind11;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P743_PU_B | SYSTEM | LBB INITIATION B-PH | set | Reset | RS_OP_LBB INI B | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind11;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind12;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P743_PU_B | SYSTEM | TIE LBB TO INIT BB | set | Reset | RS_OP_T LBB OPTD | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind12;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CbfBbpRBRF1 | ST;OpIn;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P743_PU_B | PROTECTION | EXTERNAL BREAKER FAILURE RETRIP | Operated | Reset | RS_OP_CB FAIL S1 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF1 | ST;OpIn;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CbfBbpRBRF2 | ST;OpEx;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R401_P743_PU_B | PROTECTION | EXTERNAL BREAKER FAILURE BACK TRIP | Operated | Reset | RS_OP_CB FAIL S2 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF2 | ST;OpEx;general;ACT |  |  | None | [11 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | R401_P743_PU_B | PROTECTION | BREAKER FAILURE RETRIP | Operated | Reset | RS_OP_CB FAIL S3 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF3 | ST;OpIn;general;ACT
[6 empty] | SPS | 400kV | R401_P743_PU_B | PROTECTION | BREAKER FAILURE BACK TRIP | Operated | Reset | RS_OP_CB FAIL S4 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF4 | ST;OpEx;general;ACT
[6 empty] | SPS | 400kV | R401_P743_PU_B | PROTECTION | B/B PU-A HEALTHY | Healthy | Unhealthy | UN_HL_BB_PU A
A |  |  |  |  | SPARE | [20 empty] | None |  | No | [9 empty] | 1 | #REF!
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | R401_P743_PU_B
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R401_P743_PU_B
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | R401_P743_PU_B
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R401_P743_PU_B
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | R401_P743_PU_B
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R401_P743_PU_B
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R401_P743_PU_B
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | R401_P743_PU_B
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R401_P743_PU_B
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D39: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E39: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D53: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E53: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC53: HMI Display : Specify if the data appears in HMI.
Note on AD53: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE53: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D61: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E61: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D67: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E67: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB67: LCD Display : Specify if the data appears in computer LCD.
Note on AC67: HMI Display : Specify if the data appears in HMI.
Note on AD67: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE67: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC130: HMI Display : Specify if the data appears in HMI.
Note on AD130: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE130: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB150: LCD Display : Specify if the data appears in computer LCD.
Note on AC150: HMI Display : Specify if the data appears in HMI.
Note on AD150: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE150: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R402_P743_50BF
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R402_P743_50BF |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R402_P743_50BF
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R402_P743_50BF
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R402_P743_50BF | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R402_P743_50BF
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R402_P743_50BF | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R402_P743_50BF
A |  |  | System;OptGGIO1 | ST;Ind1;stVal;SPS | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | R402_P743_50BF | SYSTEM | BCU | Healthy | Unhealthy | UL_HL_BCU | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind1;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R402_P743_50BF
A |  |  | System;OptGGIO1 | ST;Ind5;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R402_P743_50BF | SYSTEM | LBB INITIATION 3-PH | Set | Reset | RS_OP_LBB INI 3P | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind5;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R402_P743_50BF
A |  |  | System;OptGGIO1 | ST;Ind9;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R402_P743_50BF | SYSTEM | LBB INITIATION R-PH | Set | Reset | RS_OP_LBB INI R | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind9;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R402_P743_50BF
A |  |  | System;OptGGIO1 | ST;Ind10;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R402_P743_50BF | SYSTEM | LBB INITIATION B-PH | Set | Reset | RS_OP_LBB INI B | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R402_P743_50BF
A |  |  | System;OptGGIO1 | ST;Ind11;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R402_P743_50BF | SYSTEM | LBB INITIATION Y-PH | Set | Reset | RS_OP_LBB INI Y | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind11;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R402_P743_50BF
A |  |  | Protection;CbfBbpRBRF2 | ST;OpEx;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R402_P743_50BF | PROTECTION | BREAKER FAILURE BACK TRIP | Operated | Reset | RS_OP_CB FAIL S2 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF4 | ST;OpEx;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | BREAKER FAILURE RETRIP TRIP | Operated | Reset | RS_OP_CB FAIL S1 | [12 empty] | None |  | No | [9 empty] | 1 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | BREAKER FAILURE RETRIP RPH | Operated | Reset | RS_OP_CB FAILS1R | [12 empty] | None |  | No | [9 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | R402_P743_50BF | PROTECTION | BREAKER FAILURE RETRIP YPH | Operated | Reset | RS_OP_CB FAILS1Y
A |  |  |  |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | BREAKER FAILURE RETRIP BPH | Operated | Reset | RS_OP_CB FAILS1B | [12 empty] | None |  | No | [9 empty] | 1 | #REF!
[7 empty] | 400kV | R402_P743_50BF | PROTECTION
|  |  | DIGITAL INFORMATION TO IED |  |  |  | 400kV | R402_P743_50BF | PROTECTION
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  | 400kV | R402_P743_50BF | PROTECTION | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | 400kV | R402_P743_50BF | PROTECTION | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R402_P743_50BF
A |  |  |  |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R402_P743_50BF
A |  |  |  |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R402_P743_50BF
A |  |  |  |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R402_P743_50BF
A |  |  |  |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R402_P743_50BF
A |  |  |  |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R402_P743_50BF
A |  |  |  |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R402_P743_50BF
A |  |  |  |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R402_P743_50BF
A |  |  |  |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R402_P743_50BF
A |  |  |  |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R402_P743_50BF
[7 empty] | 400kV | R402_P743_50BF | PROTECTION
|  |  | ANALOG INFORMATION FROM IED |  |  |  | 400kV | R402_P743_50BF | PROTECTION
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  | 400kV | R402_P743_50BF | PROTECTION | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | 400kV | R402_P743_50BF | PROTECTION | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R402_P743_50BF
A |  |  |  |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R402_P743_50BF
A |  |  |  |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R402_P743_50BF
A |  |  |  |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R402_P743_50BF
[7 empty] | 400kV | R402_P743_50BF | PROTECTION
|  |  | ANALOG INFORMATION TO IED |  |  |  | 400kV | R402_P743_50BF | PROTECTION
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  | 400kV | R402_P743_50BF | PROTECTION | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | 400kV | R402_P743_50BF | PROTECTION | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [28 empty] | 13 | ANALOG INFORMATION TO IED IED name R402_P743_50BF
A |  |  |  |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [28 empty] | 13 | ANALOG INFORMATION TO IED IED name R402_P743_50BF
[7 empty] | 400kV | R402_P743_50BF | PROTECTION
|  |  | COUNTER INFORMATION FROM IED |  |  |  | 400kV | R402_P743_50BF | PROTECTION
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  | 400kV | R402_P743_50BF | PROTECTION | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | 400kV | R402_P743_50BF | PROTECTION | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R402_P743_50BF
A |  |  |  |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R402_P743_50BF
A |  |  |  |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R402_P743_50BF
A |  |  |  |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R402_P743_50BF
|  |  | END OF IED DATA |  |  |  | 400kV | R402_P743_50BF | PROTECTION
[7 empty] | 400kV | R402_P743_50BF | PROTECTION
|  |  | DI GROUPS |  |  |  | 400kV | R402_P743_50BF | PROTECTION
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  | 400kV | R402_P743_50BF | PROTECTION | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | 400kV | R402_P743_50BF | PROTECTION | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
[7 empty] | 400kV | R402_P743_50BF | PROTECTION
|  |  | SELF GENERATED DIGITAL INFORMATION |  |  |  | 400kV | R402_P743_50BF | PROTECTION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  | 400kV | R402_P743_50BF | PROTECTION | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | 400kV | R402_P743_50BF | PROTECTION | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | 400kV | R402_P743_50BF | PROTECTION | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
[7 empty] | 400kV | R402_P743_50BF | PROTECTION
|  |  | SELF GENERATED DIGITAL OUTPUT INFORMATION |  |  |  | 400kV | R402_P743_50BF | PROTECTION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  | 400kV | R402_P743_50BF | PROTECTION | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | 400kV | R402_P743_50BF | PROTECTION | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | 400kV | R402_P743_50BF | PROTECTION | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
[7 empty] | 400kV | R402_P743_50BF | PROTECTION
|  |  | SELF GENERATED ANALOG INFORMATION |  |  |  | 400kV | R402_P743_50BF | PROTECTION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  | 400kV | R402_P743_50BF | PROTECTION | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | 400kV | R402_P743_50BF | PROTECTION | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
[7 empty] | 400kV | R402_P743_50BF | PROTECTION
|  |  | SELF GENERATED COUNTER INFORMATION |  |  |  | 400kV | R402_P743_50BF | PROTECTION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  | 400kV | R402_P743_50BF | PROTECTION | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | 400kV | R402_P743_50BF | PROTECTION | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
[7 empty] | 400kV | R402_P743_50BF | PROTECTION
|  |  | SELF GENERATED SETPOINT INFORMATION |  |  |  | 400kV | R402_P743_50BF | PROTECTION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  | 400kV | R402_P743_50BF | PROTECTION | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | 400kV | R402_P743_50BF | PROTECTION | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE |  | 400kV | R402_P743_50BF | PROTECTION | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
[7 empty] | 400kV | R402_P743_50BF | PROTECTION
END OF DATA | [6 empty] | 400kV | R402_P743_50BF | PROTECTION
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D35: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E35: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D49: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E49: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC49: HMI Display : Specify if the data appears in HMI.
Note on AD49: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE49: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D57: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E57: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D63: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E63: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB63: LCD Display : Specify if the data appears in computer LCD.
Note on AC63: HMI Display : Specify if the data appears in HMI.
Note on AD63: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE63: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC126: HMI Display : Specify if the data appears in HMI.
Note on AD126: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE126: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB146: LCD Display : Specify if the data appears in computer LCD.
Note on AC146: HMI Display : Specify if the data appears in HMI.
Note on AD146: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE146: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R407_P643_87T
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R407_P643_87T |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R407_P643_87T
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R407_P643_87T
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P643_87T | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R407_P643_87T
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P643_87T | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind6;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | PROTECTION | OVEREXCITATION HV START | Set | Reset | RS_OP_O/E HV S | Transmitted to IEC | [7 empty] | Protection;VhzWg1PVPH1 | ST;Str;general;ACD |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind4;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | SYSTEM | 86A1 TRIP RELAY | Operated | Reset | RS_OP_86A1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind4;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind5;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | SYSTEM | 86A2 TRIP RELAY | Operated | Reset | RS_OP_86A2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind5;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind6;stVal;SPS | SPE_HLA_Normal_Fail | SPS | 400kV | R407_P643_87T | SYSTEM | DC SOURCE-2 | Fail | Normal | NL_FL_DC S2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind6;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind9;stVal;SPS | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | R407_P643_87T | SYSTEM | 64 RELAY | Healthy | Unhealthy | UL_HL_64 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind9;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind10;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | SYSTEM | BUCHHOLZ TRIP 1&2 | Operated | Reset | RS_OP_BUCH12 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind11;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P643_87T | SYSTEM | PRD 1 2 &3 | Alarm | Normal | RS_OP_PRD123 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind11;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind12;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | SYSTEM | OSR1 | Operated | Reset | RS_OP_OSR-1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind12;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind13;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | SYSTEM | OSR2 | Operated | Reset | RS_OP_OSR-2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind13;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind14;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | SYSTEM | OSR3 | Operated | Reset | RS_OP_OSR-3 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind14;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind15;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | SYSTEM | OTI | Operated | Reset | RS_OP_OTI | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind15;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind16;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | SYSTEM | 86A2 SUPERVISION | Healthy | Unhealthy | RS_OP_86A2 S | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind16;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind17;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | SYSTEM | WTI HV | Operated | Reset | RS_OP_WTI HV | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind17;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind18;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | SYSTEM | WTI LV | Operated | Reset | RS_OP_WTI LV | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind18;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind19;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | SYSTEM | WTI IV | Operated | Reset | RS_OP_WTI IV | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind19;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind20;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | SYSTEM | LOW OIL LEVEL MAIN TANK | Alarm | Normal | RS_OP_MOLG | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind20;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind21;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | SYSTEM | LOW OIL LEVEL OLTC | Alarm | Normal | RS_OP_MOLG O | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind21;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind24;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | SYSTEM | 86A1 SUPERVISION | Healthy | Unhealthy | RS_OP_86A1 S | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind24;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;PTRC1 | ST;Tr;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | PROTECTION | GENERAL TRIP | Operated | Reset | RS_OP_GEN TRIP | Transmitted to IEC | [7 empty] | Protection;PTRC1 | ST;Tr;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DifPDIF1 | ST;Op;phsA;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | PROTECTION | DIFFERENTIAL R-PH TRIP | Operated | Reset | RS_OP_DIFF R PH | Transmitted to IEC | [7 empty] | Protection;DifPDIF1 | ST;Op;phsA;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DifPDIF1 | ST;Op;phsB;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | PROTECTION | DIFFERENTIAL Y-PH TRIP | Operated | Reset | RS_OP_DIFF Y-PH | Transmitted to IEC | [7 empty] | Protection;DifPDIF1 | ST;Op;phsB;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DifPDIF1 | ST;Op;phsC;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | PROTECTION | DIFFERENTIAL B-PH TRIP | Operated | Reset | RS_OP_DIFF B-PH | Transmitted to IEC | [7 empty] | Protection;DifPDIF1 | ST;Op;phsC;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DifPDIF1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | PROTECTION | DIFFERENTIAL TRIP | Operated | Reset | RS_OP_DIFF | Transmitted to IEC | [7 empty] | Protection;DifPDIF1 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;EfmEl1PTOC1 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | PROTECTION | DIFFERENTIAL CURRENT ALARM | Set | Reset | RS_ST_DIFF_CURNT | [12 empty] | None | [11 empty] | 1 | #REF!
A |  |  | Protection;EfmEl1PTOC1 | ST;Str;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | PROTECTION | DIFFERENTIAL PROTECTION START | Set | Reset | RS_ST_DIFF_STRT | [12 empty] | None | [11 empty] | 1 | #REF!
A |  |  | Protection;OcpEI1PTOC1 | ST;Op;phsA;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | PROTECTION | DIFFERENTIAL PROTECTION RPH START | Set | Reset | RS_ST_DIFF_STR_R | [12 empty] | None | [11 empty] | 1 | #REF!
A |  |  | Protection;OcpEI1PTOC1 | ST;Op;phsB;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | PROTECTION | DIFFERENTIAL PROTECTION YPH START | Set | Reset | RS_ST_DIFF_STR_Y | [12 empty] | None | [11 empty] | 1 | #REF!
A |  |  | Protection;OcpEI1PTOC1 | ST;Op;phsC;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | PROTECTION | DIFFERENTIAL PROTECTION BPH START | Set | Reset | RS_ST_DIFF_STR_B | [12 empty] | None | [11 empty] | 1 | #REF!
A |  |  | Protection;OcpEI1PTOC1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_87T | PROTECTION | DIFFERENTIAL BLOCKED | Set | Reset | RS_ST_DIFF_BLK | [12 empty] | None | [11 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | R407_P643_87T | PROTECTION | DIFFERENTIAL PROTECTION TRIP-HS1 | Operated | Reset | RS_OP_DIFF_HS-1
[6 empty] | SPS | 400kV | R407_P643_87T | PROTECTION | DIFFERENTIAL PROTECTION TRIP-HS2 | Operated | Reset | RS_OP_DIFF_HS-2
[6 empty] | SPS | 400kV | R407_P643_87T | PROTECTION | DIFFERENTIAL PROTECTION 2nd HARMONIC BLOCK | Set | Reset | RS_ST_DIFF_HBK 2
[6 empty] | SPS | 400kV | R407_P643_87T | PROTECTION | DIFFERENTIAL PROTECTION 5th HARMONIC BLOCK | Set | Reset | RS_ST_DIFF_HBK 5
A |  |  | Protection;VhzWg1PVPH1 | ST;Op;general;ACT | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P643_87T | PROTECTION | OVEREXCITATION HV ALARM | Set | Reset | NL_AL_O/E HV | Transmitted to IEC | [7 empty] | Protection;VhzWg1PVPH1 | ST;Op;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;VhzWg1PVPH2 | ST;Op;general;ACT | SPE_HLA_Reset_Trip | SPS | 400kV | R407_P643_87T | PROTECTION | OVEREXCITATION HV TRIP | Operated | Reset | RS_TR_O/E HV | Transmitted to IEC | [7 empty] | Protection;VhzWg1PVPH2 | ST;Op;general;ACT |  |  | None | [11 empty] | 1 | #REF!
[8 empty] | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | Description | Scada Interface | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | System;OptGGIO1 | ST;Ind10;stVal;SPS |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [14 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_87T
A |  |  |  |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [14 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_87T
A |  |  |  |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [14 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_87T
A |  |  |  |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [14 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_87T
A |  |  |  |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [14 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_87T
A |  |  |  |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [14 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_87T
A |  |  |  |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [14 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_87T
A |  |  |  |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [14 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_87T
A |  |  |  |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [14 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_87T
A |  |  |  |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [14 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_87T
[8 empty] | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | Description | Scada Interface | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | System;OptGGIO1 | ST;Ind10;stVal;SPS |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE |  |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P643_87T
A |  |  |  |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P643_87T
A |  |  |  |  | SPARE |  |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P643_87T
A |  |  |  |  | SPARE |  |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P643_87T
[8 empty] | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | Description | Scada Interface | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [14 empty] | 13 | ANALOG INFORMATION TO IED IED name R407_P643_87T
A |  |  |  |  | SPARE |  |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [14 empty] | 13 | ANALOG INFORMATION TO IED IED name R407_P643_87T
[8 empty] | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | Description | Scada Interface | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE |  |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P643_87T
A |  |  |  |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P643_87T
A |  |  |  |  | SPARE |  |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P643_87T
A |  |  |  |  | SPARE |  |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P643_87T
|  |  | END OF IED DATA |  |  |  |  | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
[8 empty] | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
|  |  | DI GROUPS |  |  |  |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | Description | Scada Interface | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | System;OptGGIO1 | ST;Ind10;stVal;SPS | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 DI GROUPS
[8 empty] | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
|  |  | SELF GENERATED DIGITAL INFORMATION |  |  |  |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | Description | Scada Interface | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | System;OptGGIO1 | ST;Ind10;stVal;SPS | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
[8 empty] | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
|  |  | SELF GENERATED DIGITAL OUTPUT INFORMATION |  |  |  |  | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | Description | Scada Interface | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | System;OptGGIO1 | ST;Ind10;stVal;SPS |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [8 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [8 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [8 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [8 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [8 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [8 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [8 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [8 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [8 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS | [8 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
[8 empty] | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
|  |  | SELF GENERATED ANALOG INFORMATION |  |  |  |  | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | Description | Scada Interface | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | System;OptGGIO1 | ST;Ind10;stVal;SPS |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE |  |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE |  |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE |  |  | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE |  |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE |  |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE |  |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE |  |  | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE |  |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
[8 empty] | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
|  |  | SELF GENERATED COUNTER INFORMATION |  |  |  |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | Description | Scada Interface | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE |  |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE |  |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE |  |  | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE |  |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE |  |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE |  |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE |  |  | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE |  |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
[8 empty] | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
|  |  | SELF GENERATED SETPOINT INFORMATION |  |  |  |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | Description | Scada Interface | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE |  |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE |  |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE |  |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE |  |  | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE |  |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE |  |  | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE |  |  | R407_P643_87T | SYSTEM | WDG TEMP - HV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE |  |  | R407_P643_87T | SYSTEM | WDG TEMP - IV & LV TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE |  |  | R407_P643_87T | SYSTEM | PRV-2 TRIP | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE |  |  | R407_P643_87T | SYSTEM | OIL TEMP ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  |  |  | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
[8 empty] | R407_P643_87T | SYSTEM | OLTC ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
END OF DATA | [7 empty] | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Trip | Reset | [9 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
[8 empty] | R407_P643_87T | SYSTEM | BUCHHOLZ-1 TRIP | Operated | Reset | RS_TR_BUCH-1 | [8 empty] | System;OptGGIO1 | ST;Ind11;stVal;SPS
[8 empty] | R407_P643_87T | SYSTEM | WTI-HV TRIP | Operated | Reset | RS_TR_WTI-HV | [8 empty] | System;OptGGIO1 | ST;Ind12;stVal;SPS
[8 empty] | R407_P643_87T | SYSTEM | WTI - IV & LV TRIP | Operated | Reset | RS_TR_WTI-LVIV | [8 empty] | System;OptGGIO1 | ST;Ind13;stVal;SPS
[8 empty] | R407_P643_87T | SYSTEM | PRD-2 TRIP | Operated | Reset | RS_TR_PRV2 | [8 empty] | System;OptGGIO1 | ST;Ind14;stVal;SPS
[8 empty] | R407_P643_87T | SYSTEM | OTI ALARM | Alarm | Normal | NL_AL_OTI | [8 empty] | System;OptGGIO1 | ST;Ind15;stVal;SPS
[8 empty] | R407_P643_87T | SYSTEM | PRV OLTC ALARM | Set | Reset | NL_AL_OLTC | [8 empty] | System;OptGGIO1 | ST;Ind17;stVal;SPS
[8 empty] | R407_P643_87T | SYSTEM | OIL LEVEL LOW ALARM | Set | Reset | NL_AL_OLL | [8 empty] | System;OptGGIO1 | ST;Ind18;stVal;SPS
[8 empty] | R407_P643_87T | SYSTEM | BUCHHOLZ-2 ALARM | Set | Reset | RS_ST_BUCH ALM | [8 empty] | System;OptGGIO1 | ST;IndXX;stVal;SPS
[8 empty] | R407_P643_87T | SYSTEM | OSR-1 TRIP | Operated | Reset | RS_OP_OSR-1 TR | [8 empty] | System;OptGGIO1 | ST;IndXX;stVal;SPS
[8 empty] | R407_P643_87T | SYSTEM | FIRE PROTECTION | Operated | Reset | RS_OP_FIRE PRTN | [8 empty] | System;OptGGIO1 | ST;IndXX;stVal;SPS
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on K25: Arnab Ghosh {अर्नब घोष}: Please clarify
Note on K33: Arnab Ghosh {अर्नब घोष}: Please clarify
Note on K39: Arnab Ghosh {अर्नब घोष}: Please clarify
Note on D60: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E60: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D74: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E74: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC74: HMI Display : Specify if the data appears in HMI.
Note on AD74: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE74: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D82: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E82: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D88: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E88: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB88: LCD Display : Specify if the data appears in computer LCD.
Note on AC88: HMI Display : Specify if the data appears in HMI.
Note on AD88: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE88: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC151: HMI Display : Specify if the data appears in HMI.
Note on AD151: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE151: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB171: LCD Display : Specify if the data appears in computer LCD.
Note on AC171: HMI Display : Specify if the data appears in HMI.
Note on AD171: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE171: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R407_P643_64
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R407_P643_64 |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R407_P643_64
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R407_P643_64
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P643_64 | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R407_P643_64
A |  |  | System;GosGGIO2 | ST;Ind7;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_64 | PROTECTION | OVEREXCITATION IV START | Set | Reset | RS_OP_O/E IV S | Transmitted to IEC | [7 empty] | Protection;VhzWg1PVPH1 | ST;Str;general;ACD |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind8;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P643_64 | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind8;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind2;stVal;SPS | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | R407_P643_64 | SYSTEM | 87T RELAY | Healthy | Unhealthy | UL_HL_87T | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind2;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind3;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_64 | SYSTEM | 86B1 TRIP RELAY | Operated | Reset | RS_OP_86B1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind3;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind4;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_64 | SYSTEM | 86B2 TRIP RELAY | Operated | Reset | RS_OP_86B2 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind4;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind6;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P643_64 | SYSTEM | WTI HV | Alarm | Normal | NL_AL_WTI HV | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind6;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind7;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P643_64 | SYSTEM | WTI LV | Alarm | Normal | NL_AL_WTI LV | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind7;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind8;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P643_64 | SYSTEM | WTI IV | Alarm | Normal | NL_AL_WTI IV | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind8;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind9;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P643_64 | SYSTEM | BUCHHOLZ 1&2 | Alarm | Normal | NL_AL_BUCH12 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind9;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind10;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P643_64 | SYSTEM | OTI | Alarm | Normal | NL_AL_OTI | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind11;stVal;SPS | SPE_HLA_Normal_Fail | SPS | 400kV | R407_P643_64 | SYSTEM | DC SOURCE-1 | Fail | Normal | NL_FL_DC S1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind11;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind15;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_64 | SYSTEM | 86A1 SUPERVISION | Healthy | Unhealthy | RS_OP_86B1 S | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind15;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind16;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_64 | SYSTEM | 86A2 SUPERVISION | Healthy | Unhealthy | RS_OP_86B2 S | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind16;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;PTRC1 | ST;Tr;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_64 | PROTECTION | GENERAL TRIP | Operated | Reset | RS_OP_GEN TRIP | Transmitted to IEC | [7 empty] | Protection;PTRC1 | ST;Tr;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;HzrHvwPTOC1 | ST;Op;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_64 | PROTECTION | REF R PH TRIP | Operated | Reset | RS_OP_REF | Transmitted to IEC | [7 empty] | Protection;HzrHvwPTOC1 | ST;Op;general;ACT |  |  | None | [11 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | R407_P643_64 | PROTECTION | REF Y PH TRIP | Operated | Reset | RS_OP_REF | Transmitted to IEC | [7 empty] | Protection;HzrLvwPTOC1 | ST;Op;general;ACT
[6 empty] | SPS | 400kV | R407_P643_64 | PROTECTION | REF B PH TRIP | Operated | Reset | RS_OP_REF | Transmitted to IEC | [7 empty] | Protection;HzrTvwPTOC1 | ST;Op;general;ACT
A |  |  | Protection;OcpEI1PTOC1 | ST;Op;phsA;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_65 | PROTECTION | REF ALARM | Set | Reset | RS_ST_REF ALM | [12 empty] | None | [11 empty] | 1 | #REF!
A |  |  | Protection;OcpEI1PTOC1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P643_64 | PROTECTION | OVEREXCITATION IV START | Set | Reset | RS_ST_O/E IV ST | [12 empty] | None | [11 empty] | 1 | #REF!
A |  |  | Protection;VhzWg1PVPH1 | ST;Op;general;ACT | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P643_64 | PROTECTION | OVEREXCITATION IV ALARM | Set | Reset | NL_AL_O/E IV | Transmitted to IEC | [7 empty] | Protection;VhzWg1PVPH1 | ST;Op;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;VhzWg1PVPH2 | ST;Op;general;ACT | SPE_HLA_Reset_Trip | SPS | 400kV | R407_P643_64 | PROTECTION | OVEREXCITATION IV TRIP | Operated | Reset | RS_TR_O/E IV T | Transmitted to IEC | [7 empty] | Protection;VhzWg1PVPH2 | ST;Op;general;ACT |  |  | None | [11 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM | OIL TEMP TRIP
|  |  | DIGITAL INFORMATION TO IED |  |  | SPS | 400kV | R407_P643_64 | SYSTEM | BUCHHOLZ-2 TRIP
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data | SPS | 400kV | R407_P643_64 | SYSTEM | BUCHHOLZ ALARM | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | SPS | 400kV | R407_P643_64 | SYSTEM | WDG TEMP - HV ALARM | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | WDG TEMP - IV & LV ALARM | [27 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_64
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | OIL FLOW FAIL ALARM | [27 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_64
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_64
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_64
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_64
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_64
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_64
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_64
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_64
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [28 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P643_64
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
|  |  | ANALOG INFORMATION FROM IED |  |  | SPS | 400kV | R407_P643_64 | SYSTEM
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data | SPS | 400kV | R407_P643_64 | SYSTEM | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | SPS | 400kV | R407_P643_64 | SYSTEM | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P643_64
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P643_64
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P643_64
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P643_64
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
|  |  | ANALOG INFORMATION TO IED |  |  | SPS | 400kV | R407_P643_64 | SYSTEM
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data | SPS | 400kV | R407_P643_64 | SYSTEM | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | SPS | 400kV | R407_P643_64 | SYSTEM | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [28 empty] | 13 | ANALOG INFORMATION TO IED IED name R407_P643_64
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [28 empty] | 13 | ANALOG INFORMATION TO IED IED name R407_P643_64
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
|  |  | COUNTER INFORMATION FROM IED |  |  | SPS | 400kV | R407_P643_64 | SYSTEM
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data | SPS | 400kV | R407_P643_64 | SYSTEM | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | SPS | 400kV | R407_P643_64 | SYSTEM | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P643_64
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P643_64
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P643_64
A |  |  |  |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P643_64
|  |  | END OF IED DATA |  |  | SPS | 400kV | R407_P643_64 | SYSTEM
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
|  |  | DI GROUPS |  |  | SPS | 400kV | R407_P643_64 | SYSTEM
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data | SPS | 400kV | R407_P643_64 | SYSTEM | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | SPS | 400kV | R407_P643_64 | SYSTEM | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
|  |  | SELF GENERATED DIGITAL INFORMATION |  |  | SPS | 400kV | R407_P643_64 | SYSTEM
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data | SPS | 400kV | R407_P643_64 | SYSTEM | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | 400kV | R407_P643_64 | SYSTEM | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [16 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
|  |  | SELF GENERATED DIGITAL OUTPUT INFORMATION |  |  | SPS | 400kV | R407_P643_64 | SYSTEM
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data | SPS | 400kV | R407_P643_64 | SYSTEM | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | 400kV | R407_P643_64 | SYSTEM | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [22 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
|  |  | SELF GENERATED ANALOG INFORMATION |  |  | SPS | 400kV | R407_P643_64 | SYSTEM
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data | SPS | 400kV | R407_P643_64 | SYSTEM | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | 400kV | R407_P643_64 | SYSTEM | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
|  |  | SELF GENERATED COUNTER INFORMATION |  |  | SPS | 400kV | R407_P643_64 | SYSTEM
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data | SPS | 400kV | R407_P643_64 | SYSTEM | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | 400kV | R407_P643_64 | SYSTEM | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
|  |  | SELF GENERATED SETPOINT INFORMATION |  |  | SPS | 400kV | R407_P643_64 | SYSTEM
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data | SPS | 400kV | R407_P643_64 | SYSTEM | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | 400kV | R407_P643_64 | SYSTEM | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | SPS | 400kV | R407_P643_64 | SYSTEM | [18 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
END OF DATA | [5 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM | PRD-1 TRIP | Operated | Reset | RS_TR_PRD-1 | [8 empty] | System;OptGGIO1 | ST;Ind5;stVal;SPS
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM | OTI TRIP | Operated | Reset | RS_TR_OTI | [8 empty] | System;OptGGIO1 | ST;Ind6;stVal;SPS
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM | BUCHHOLZ-2 TRIP | Operated | Reset | RS_TR_BUCH-2 | [8 empty] | System;OptGGIO1 | ST;Ind7;stVal;SPS
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM | BUCHHOLZ-1 ALARM | Set | Reset | NL_AL_BUCH | [8 empty] | System;OptGGIO1 | ST;Ind8;stVal;SPS
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM | WTI - HV ALARM | Set | Reset | NL_AL_WTI-HV | [8 empty] | System;OptGGIO1 | ST;Ind9;stVal;SPS
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM | WTI - IV & LV ALARM | Set | Reset | NL_AL_WTI IVLV | [8 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM | OSR-2 TRIP | Operated | Reset | RS_OP_OSR-2 TRP | [8 empty] | System;OptGGIO1 | ST;IndXX;stVal;SPS
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM | PRD-3 TRIP | Operated | Reset | RS_OP_PRD-3 TRP | [8 empty] | System;OptGGIO1 | ST;IndXX;stVal;SPS
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
[6 empty] | SPS | 400kV | R407_P643_64 | SYSTEM
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D45: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E45: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D59: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E59: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC59: HMI Display : Specify if the data appears in HMI.
Note on AD59: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE59: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D67: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E67: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D73: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E73: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB73: LCD Display : Specify if the data appears in computer LCD.
Note on AC73: HMI Display : Specify if the data appears in HMI.
Note on AD73: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE73: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC136: HMI Display : Specify if the data appears in HMI.
Note on AD136: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE136: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB156: LCD Display : Specify if the data appears in computer LCD.
Note on AC156: HMI Display : Specify if the data appears in HMI.
Note on AD156: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE156: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R407_P442_21R
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R412_P442_21R |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R412_P442_21R
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R412_P442_21R
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P442_21R | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R412_P442_21R
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P442_21R | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R412_P442_21R
A |  |  | Protection;PTRC1 | ST;Tr;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P442_21R | PROTECTION | GENERAL TRIP | Operated | Reset | RS_OP_GEN TRIP | Transmitted to IEC | [7 empty] | Protection;PTRC1 | ST;Tr;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CbfRBRF1 | ST;OpEx;general;ACT | SPE_HLA_Normal_Fail | SPS | 400kV | R407_P442_21R | PROTECTION | VT FUSE FAIL | Alarm | Normal | NL_FL_VT FUSE | Transmitted to IEC | [7 empty] | System;AlmGGIO1 | ST;Alm6;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsA;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P442_21R | PROTECTION | BACKUP IMPEDENCE R-PH TRIP | Operated | Reset | RS_OP_B/U IMP R | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phsA;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsB;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P442_21R | PROTECTION | BACKUP IMPEDENCE Y-PH TRIP | Operated | Reset | RS_OP_B/U IMP Y | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phsB;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsC;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P442_21R | PROTECTION | BACKUP IMPEDENCE B-PH TRIP | Operated | Reset | RS_OP_B/U IMP B | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phsC;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P442_21R | PROTECTION | BACKUP IMPEDENCE | Operated | Reset | RS_OP_B/U IMP | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Start | SPS | 400kV | R407_P442_21R | PROTECTION | REACTOR BACKUP IMPEDANE PICKUP | set | Reset | RS_ST_Z1 START | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R407_P442_21R | PROTECTION | BACKUP ZONE-1 TRIP | Operated | Reset | RS_OP_Z1_TRP | [12 empty] | None |  | No | [9 empty] | 1 | #REF!
[6 empty] | SPS |  | R407_P442_21R
|  |  | DIGITAL INFORMATION TO IED |  |  | SPS | IED name | R407_P442_21R
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data | SPS |  | R407_P442_21R |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | SPS | Voltage Level Short Name (16 char) | R407_P442_21R | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [29 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P442_21R
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [29 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P442_21R
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [29 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P442_21R
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [29 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P442_21R
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R |  |  |  |  | R | [24 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P442_21R
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [29 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P442_21R
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [29 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P442_21R
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [29 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P442_21R
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [29 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P442_21R
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [29 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P442_21R
[6 empty] | SPS |  | R407_P442_21R
|  |  | ANALOG INFORMATION FROM IED |  |  | SPS | IED name | R407_P442_21R
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data | SPS |  | R407_P442_21R |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | SPS | Voltage Level Short Name (16 char) | R407_P442_21R | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P442_21R
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P442_21R
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P442_21R
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P442_21R
[6 empty] | SPS |  | R407_P442_21R
|  |  | ANALOG INFORMATION TO IED |  |  | SPS | IED name | R407_P442_21R
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data | SPS |  | R407_P442_21R |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | SPS | Voltage Level Short Name (16 char) | R407_P442_21R | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [29 empty] | 13 | ANALOG INFORMATION TO IED IED name R407_P442_21R
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [29 empty] | 13 | ANALOG INFORMATION TO IED IED name R407_P442_21R
[6 empty] | SPS |  | R407_P442_21R
|  |  | COUNTER INFORMATION FROM IED |  |  | SPS | IED name | R407_P442_21R
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data | SPS |  | R407_P442_21R |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | SPS | Voltage Level Short Name (16 char) | R407_P442_21R | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P442_21R
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P442_21R
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P442_21R
A |  |  |  |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P442_21R
|  |  | END OF IED DATA |  |  | SPS |  | R407_P442_21R
[6 empty] | SPS |  | R407_P442_21R
|  |  | DI GROUPS |  |  | SPS |  | R407_P442_21R
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data | SPS |  | R407_P442_21R |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | SPS | Voltage Level Short Name (16 char) | R407_P442_21R | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
[6 empty] | SPS |  | R407_P442_21R
|  |  | SELF GENERATED DIGITAL INFORMATION |  |  | SPS |  | R407_P442_21R
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data | SPS |  | R407_P442_21R |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | Voltage Level Short Name (16 char) | R407_P442_21R | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS |  | R407_P442_21R | [17 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
[6 empty] | SPS |  | R407_P442_21R
|  |  | SELF GENERATED DIGITAL OUTPUT INFORMATION |  |  | SPS |  | R407_P442_21R
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data | SPS |  | R407_P442_21R |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | Voltage Level Short Name (16 char) | R407_P442_21R | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS |  | R407_P442_21R | [23 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPS |  | R407_P442_21R | [23 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPS |  | R407_P442_21R | [23 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPS |  | R407_P442_21R | [23 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPS |  | R407_P442_21R | [23 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPS |  | R407_P442_21R | [23 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPS |  | R407_P442_21R | [23 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPS |  | R407_P442_21R | [23 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPS |  | R407_P442_21R | [23 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPS |  | R407_P442_21R | [23 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
[6 empty] | SPS |  | R407_P442_21R
|  |  | SELF GENERATED ANALOG INFORMATION |  |  | SPS |  | R407_P442_21R
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data | SPS |  | R407_P442_21R |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | Voltage Level Short Name (16 char) | R407_P442_21R | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
[6 empty] | SPS |  | R407_P442_21R
|  |  | SELF GENERATED COUNTER INFORMATION |  |  | SPS |  | R407_P442_21R
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data | SPS |  | R407_P442_21R |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | Voltage Level Short Name (16 char) | R407_P442_21R | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
[6 empty] | SPS |  | R407_P442_21R
|  |  | SELF GENERATED SETPOINT INFORMATION |  |  | SPS |  | R407_P442_21R
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data | SPS |  | R407_P442_21R |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | Voltage Level Short Name (16 char) | R407_P442_21R | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | SPS |  | R407_P442_21R | [19 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
[6 empty] | SPS |  | R407_P442_21R
END OF DATA | [5 empty] | SPS |  | R407_P442_21R
[6 empty] | SPS | 400kV | R407_P442_21R | PROTECTION | BACKUP OVERCURRENT START | set | Reset | RS_ST_B/U O/C ST
[6 empty] | SPS | 400kV | R407_P442_21R | PROTECTION | BACKUP OVERCURRENT TRIP | Operated | Reset | RS_ST_B/C O/C TR
[6 empty] | SPS | 400kV | R407_P442_21R | PROTECTION | BACKUP EARTHFAULT START | set | Reset | RS_ST_B/U E/F_ST
[6 empty] | SPS | 400kV | R407_P442_21R | PROTECTION | BACKUP EARTHFAULT TRIP | Operated | Reset | RS_ST_B/C E/F TR
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D33: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E33: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D47: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E47: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC47: HMI Display : Specify if the data appears in HMI.
Note on AD47: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE47: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D55: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E55: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D61: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E61: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB61: LCD Display : Specify if the data appears in computer LCD.
Note on AC61: HMI Display : Specify if the data appears in HMI.
Note on AD61: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE61: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC124: HMI Display : Specify if the data appears in HMI.
Note on AD124: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE124: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB144: LCD Display : Specify if the data appears in computer LCD.
Note on AC144: HMI Display : Specify if the data appears in HMI.
Note on AD144: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE144: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R407_P743_PU_A
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R407_P743_PU_A |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R407_P743_PU_A
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R407_P743_PU_A
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P743_PU_A | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R407_P743_PU_A
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P743_PU_A | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | [8 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R407_P743_PU_A
A |  |  | System;GosGGIO2 | ST;Ind1;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P743_PU_A | GOOSE | LBB START | Set | Reset | RS_OP_LBB START | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind1;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R407_P743_PU_A
A |  |  | System;OptGGIO1 | ST;Ind7;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P743_PU_A | SYSTEM | LBB INITIATION 3-PH | set | Reset | RS_OP_LBB INI 3P | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind7;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind12;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P743_PU_A | SYSTEM | TIE LBB TO INIT BB | set | Reset | RS_OP_T LBB OPTD | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind12;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CbfBbpRBRF1 | ST;OpIn;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P743_PU_A | PROTECTION | EXTERNAL CB FAILURE RETRIP | Operated | Reset | RS_OP_CB FAIL S1 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF1 | ST;OpIn;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CbfBbpRBRF2 | ST;OpEx;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P743_PU_A | PROTECTION | EXTERNAL CB FAILURE BACK TRIP | Operated | Reset | RS_OP_CB FAIL S2 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF2 | ST;OpEx;general;ACT |  |  | None | [11 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | R407_P743_PU_A | PROTECTION | CB FAILURE RETRIP | Operated | Reset | RS_OP_CB FAIL S3 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF3 | ST;OpIn;general;ACT
[6 empty] | SPS | 400kV | R407_P743_PU_A | PROTECTION | CB FAILURE BACK TRIP | Operated | Reset | RS_OP_CB FAIL S4 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF4 | ST;OpEx;general;ACT
A |  |  |  |  | SPARE | SPS | 400kV | R407_P743_PU_A | SYSTEM | B/B PU-B HEALTHY | Healthy | Unhealthy | UH_HL_PUB | [8 empty] | System;GosGGIO1 | ST;IndXX;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | #REF!
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | R407_P743_PU_A
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_A
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | R407_P743_PU_A
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P743_PU_A
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | R407_P743_PU_A
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R407_P743_PU_A
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R407_P743_PU_A
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | R407_P743_PU_A
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P743_PU_A
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D33: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E33: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D47: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E47: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC47: HMI Display : Specify if the data appears in HMI.
Note on AD47: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE47: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D55: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E55: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D61: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E61: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB61: LCD Display : Specify if the data appears in computer LCD.
Note on AC61: HMI Display : Specify if the data appears in HMI.
Note on AD61: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE61: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC124: HMI Display : Specify if the data appears in HMI.
Note on AD124: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE124: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB144: LCD Display : Specify if the data appears in computer LCD.
Note on AC144: HMI Display : Specify if the data appears in HMI.
Note on AD144: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE144: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R407_P743_PU_B
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R407_P743_PU_B |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R407_P743_PU_B
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R407_P743_PU_B
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P743_PU_B | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R407_P743_PU_B
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R407_P743_PU_B | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | [8 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R407_P743_PU_B
A |  |  | System;GosGGIO2 | ST;Ind1;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P743_PU_B | GOOSE | LBB START | Set | Reset | RS_OP_LBB START | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind1;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R407_P743_PU_B
A |  |  | System;OptGGIO1 | ST;Ind7;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P743_PU_B | SYSTEM | LBB INITIATION 3-PH | Set | Reset | RS_OP_LBB INI 3P | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind7;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind12;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P743_PU_B | SYSTEM | TIE LBB TO INIT BB | set | Reset | RS_OP_T LBB OPTD | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind12;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CbfBbpRBRF1 | ST;OpIn;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P743_PU_B | PROTECTION | EXTERNAL CB FAILURE RETRIP | Operated | Reset | RS_OP_CB FAIL S1 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF1 | ST;OpIn;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CbfBbpRBRF2 | ST;OpEx;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R407_P743_PU_B | PROTECTION | EXTERNAL CB FAILURE BACK TRIP | Operated | Reset | RS_OP_CB FAIL S2 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF2 | ST;OpEx;general;ACT |  |  | None | [11 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | R407_P743_PU_B | PROTECTION | CB FAILURE RETRIP | Operated | Reset | RS_OP_CB FAIL S3 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF3 | ST;OpIn;general;ACT
[6 empty] | SPS | 400kV | R407_P743_PU_B | PROTECTION | CB FAILURE BACK TRIP | Operated | Reset | RS_OP_CB FAIL S4 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF4 | ST;OpEx;general;ACT
[6 empty] | SPS | 400kV | R407_P743_PU_B | SYSTEM | B/B PU-B HEALTHY | Healthy | Unhealthy | UH_HL_PUA | [8 empty] | System;GosGGIO1 | ST;IndXX;stVal;SPS
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | R407_P743_PU_B
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R407_P743_PU_B
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | R407_P743_PU_B
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R407_P743_PU_B
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | R407_P743_PU_B
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R407_P743_PU_B
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R407_P743_PU_B
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | R407_P743_PU_B
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R407_P743_PU_B
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D32: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E32: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D46: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E46: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC46: HMI Display : Specify if the data appears in HMI.
Note on AD46: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE46: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D54: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E54: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D60: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E60: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB60: LCD Display : Specify if the data appears in computer LCD.
Note on AC60: HMI Display : Specify if the data appears in HMI.
Note on AD60: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE60: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC123: HMI Display : Specify if the data appears in HMI.
Note on AD123: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE123: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB143: LCD Display : Specify if the data appears in computer LCD.
Note on AC143: HMI Display : Specify if the data appears in HMI.
Note on AD143: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE143: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R412_P643_87R
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R412_P643_87R |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R412_P643_87R
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R412_P643_87R
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R412_P643_87R | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R412_P643_87R
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R412_P643_87R | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind1;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P643_87R | SYSTEM | 86A TRIP RELAY | Operated | Reset | RS_OP_86A | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind1;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind8;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P643_87R | SYSTEM | B/U IMPEDENCE | Operated | Reset | RS_OP_B/U IMP | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind8;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind9;stVal;SPS | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | R412_P643_87R | SYSTEM | REF (64R) RELAY | Healthy | Unhealthy | UH_HL_64R(REF) | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind9;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;PTRC1 | ST;Tr;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P643_87R | PROTECTION | GENERAL TRIP | Operated | Reset | RS_OP_GEN TRIP | Transmitted to IEC | [7 empty] | Protection;PTRC1 | ST;Tr;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DifPDIF1 | ST;Op;phsA;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P643_87R | PROTECTION | DIFFERENTIAL R-PH TRIP | Operated | Reset | RS_OP_DIFF R PH | Transmitted to IEC | [7 empty] | Protection;DifPDIF1 | ST;Op;phsA;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DifPDIF1 | ST;Op;phsB;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P643_87R | PROTECTION | DIFFERENTIAL Y-PH TRIP | Operated | Reset | RS_OP_DIFF Y-PH | Transmitted to IEC | [7 empty] | Protection;DifPDIF1 | ST;Op;phsB;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DifPDIF1 | ST;Op;phsC;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P643_87R | PROTECTION | DIFFERENTIAL B-PH TRIP | Operated | Reset | RS_OP_DIFF B-PH | Transmitted to IEC | [7 empty] | Protection;DifPDIF1 | ST;Op;phsC;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DifPDIF1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P643_87R | PROTECTION | DIFFERENTIAL TRIP | Operated | Reset | RS_OP_DIFF | Transmitted to IEC | [7 empty] | Protection;DifPDIF1 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R412_P643_87R | SYSTEM | 86A SUPERVISION | HEALTHY | UNHEALTHY | UL_HL_86A SUP | [8 empty] | System;OptGGIO1 | ST;Ind10;stVal;SPS |  |  | None |  | No | [9 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | R412_P643_87R | PROTECTION | DIFFERENTIAL CURRENT ALARM | Set | Reset | RS_ST_DIFF_CURNT
[6 empty] | SPS | 400kV | R412_P643_87R | PROTECTION | DIFFERENTIAL PROTECTION START | Set | Reset | RS_ST_DIFF_STRT
[6 empty] | SPS | 400kV | R412_P643_87R | PROTECTION | DIFFERENTIAL PROTECTION RPH START | Set | Reset | RS_ST_DIFF_STR_R
[6 empty] | SPS | 400kV | R412_P643_87R | PROTECTION | DIFFERENTIAL PROTECTION YPH START | Set | Reset | RS_ST_DIFF_STR_Y
[6 empty] | SPS | 400kV | R412_P643_87R | PROTECTION | DIFFERENTIAL PROTECTION BPH START | Set | Reset | RS_ST_DIFF_STR_B
[6 empty] | SPS | 400kV | R412_P643_87R | PROTECTION | DIFFERENTIAL BLOCKED | Set | Reset | RS_ST_DIFF_BLK
A |  |  | System;OptGGIO1 | ST;Ind4;stVal;SPS | SPE_HLA_Reset_Trip | SPS | 400kV | R412_P643_87R | SYSTEM | REACTOR BUCHHOLZ | Operated | Reset | RS_TR_BUCHHOLZ1 | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind4;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind5;stVal;SPS | SPE_HLA_Reset_Trip | SPS | 400kV | R412_P643_87R | SYSTEM | REACTOR WTI TRIP | Operated | Reset | RS_TR_WTI | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind5;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind6;stVal;SPS | SPE_HLA_Reset_Trip | SPS | 400kV | R412_P643_87R | SYSTEM | REACTOR PNRV | Trip | Reset | RS_TR_PNRV | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind6;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | R412_P643_87R | SYSTEM | REACTOR PRD | Operated | Reset | RS_OP_PRD-2 | [8 empty] | System;OptGGIO1 | ST;Ind11;stVal;SPS
[6 empty] | SPS | 400kV | R412_P643_87R | SYSTEM | REACTOR OTI ALARM | Set | Reset | RS_ST_OTI ALM
[6 empty] | SPS | 400kV | R412_P643_87R | SYSTEM | REACTOR OSR TRIP | Operated | Reset | RS_OP_OSR_TR
[6 empty] | SPS | 400kV | R412_P643_87R | SYSTEM | REACTOR OIL LOW LEVEL ALARM | Set | Reset | RS_ST_OIL LO_ AL
A |  |  |  |  | SPARE | SPS | 400kV | R412_P643_87R | SYSTEM | FIRE PROTECTION | Operated | Reset | RS_OP_FIRE_PTR | [12 empty] | None |  | No | [9 empty] | 1 | #REF!
|  |  | DIGITAL INFORMATION TO IED |  |  | SPS | 400kV | R412_P643_87R
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data | SPS | 400kV |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | SPS | 400kV | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS | 400kV | [30 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P643_87R
A |  |  |  |  | SPARE | SPS | 400kV | [30 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P643_87R
A |  |  |  |  | SPARE | SPS | 400kV | [30 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P643_87R
A |  |  |  |  | SPARE | SPS | 400kV | [30 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P643_87R
A |  |  |  |  | SPARE | SPS | 400kV | [30 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P643_87R
A |  |  |  |  | SPARE | SPS | 400kV | [30 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P643_87R
A |  |  |  |  | SPARE | SPS | 400kV | [30 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P643_87R
A |  |  |  |  | SPARE | SPS | 400kV | [30 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P643_87R
A |  |  |  |  | SPARE | SPS | 400kV | [30 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P643_87R
A |  |  |  |  | SPARE | SPS | 400kV | [30 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P643_87R
[6 empty] | SPS | 400kV
|  |  | ANALOG INFORMATION FROM IED |  |  | SPS | 400kV | R412_P643_87R
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data | SPS | 400kV |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | SPS | 400kV | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P643_87R
A |  |  |  |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P643_87R
A |  |  |  |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P643_87R
A |  |  |  |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P643_87R
[6 empty] | SPS | 400kV
|  |  | ANALOG INFORMATION TO IED |  |  | SPS | 400kV | R412_P643_87R
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data | SPS | 400kV |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | SPS | 400kV | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS | 400kV | [30 empty] | 13 | ANALOG INFORMATION TO IED IED name R412_P643_87R
A |  |  |  |  | SPARE | SPS | 400kV | [30 empty] | 13 | ANALOG INFORMATION TO IED IED name R412_P643_87R
[6 empty] | SPS | 400kV
|  |  | COUNTER INFORMATION FROM IED |  |  | SPS | 400kV | R412_P643_87R
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data | SPS | 400kV |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | SPS | 400kV | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P643_87R
A |  |  |  |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P643_87R
A |  |  |  |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P643_87R
A |  |  |  |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P643_87R
|  |  | END OF IED DATA |  |  | SPS | 400kV
[6 empty] | SPS | 400kV
|  |  | DI GROUPS |  |  | SPS | 400kV
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data | SPS | 400kV |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | SPS | 400kV | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
[6 empty] | SPS | 400kV
|  |  | SELF GENERATED DIGITAL INFORMATION |  |  | SPS | 400kV
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data | SPS | 400kV |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | 400kV | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | 400kV | [18 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
[6 empty] | SPS | 400kV
|  |  | SELF GENERATED DIGITAL OUTPUT INFORMATION |  |  | SPS | 400kV
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data | SPS | 400kV |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | 400kV | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | 400kV | [24 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPS | 400kV | [24 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPS | 400kV | [24 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPS | 400kV | [24 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPS | 400kV | [24 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPS | 400kV | [24 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPS | 400kV | [24 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPS | 400kV | [24 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPS | 400kV | [24 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPS | 400kV | [24 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
[6 empty] | SPS | 400kV
|  |  | SELF GENERATED ANALOG INFORMATION |  |  | SPS | 400kV
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data | SPS | 400kV |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | 400kV | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
[6 empty] | SPS | 400kV
|  |  | SELF GENERATED COUNTER INFORMATION |  |  | SPS | 400kV
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data | SPS | 400kV |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | 400kV | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
[6 empty] | SPS | 400kV
|  |  | SELF GENERATED SETPOINT INFORMATION |  |  | SPS | 400kV
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data | SPS | 400kV |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | 400kV | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | SPS | 400kV | [20 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
[6 empty] | SPS | 400kV
END OF DATA | [5 empty] | SPS | 400kV
[6 empty] | SPS | 400kV
[6 empty] | SPS | 400kV
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D47: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E47: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D61: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E61: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC61: HMI Display : Specify if the data appears in HMI.
Note on AD61: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE61: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D69: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E69: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D75: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E75: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB75: LCD Display : Specify if the data appears in computer LCD.
Note on AC75: HMI Display : Specify if the data appears in HMI.
Note on AD75: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE75: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC138: HMI Display : Specify if the data appears in HMI.
Note on AD138: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE138: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB158: LCD Display : Specify if the data appears in computer LCD.
Note on AC158: HMI Display : Specify if the data appears in HMI.
Note on AD158: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE158: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R412_P141_64R
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R412_P141_64R |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R412_P141_64R
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R412_P141_64R
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R412_P141_64R | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R412_P141_64R
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R412_P141_64R | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind5;stVal;SPS | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | R412_P141_64R | SYSTEM | B/U IMPEDENCE PROT RELAY | Healthy | Unhealthy | UH_HL_B/U IMP | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind5;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind6;stVal;SPS | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | R412_P141_64R | SYSTEM | 87R (REACTOR DIFFERENTIAL) RELAY | Healthy | Unhealthy | UH_HL_87R(R DIF) | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind6;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind8;stVal;SPS | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | R412_P141_64R | SYSTEM | 86B TRIP RELAY SUPERVISION | Healthy | Unhealthy | UH_HL_86B | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind8;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;PTRC1 | ST;Tr;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P141_64R | PROTECTION | GENERAL TRIP | Operated | Reset | RS_OP_GEN TRIP | Transmitted to IEC | [7 empty] | Protection;PTRC1 | ST;Tr;general;ACT |  |  | None | [11 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | R412_P141_64R | PROTECTION | REF TRIP | Operated | Reset | RS_OP_REF | Transmitted to IEC | [7 empty] | Protection;SenRefPDIF1 | ST;Op;general;general;ACT
[6 empty] | SPS | 400kV | R412_P141_64R | PROTECTION | REF ALARM | Set | Reset | RS_ST_REF ALM
[6 empty] | SPS | 400kV | R412_P141_64R | PROTECTION | REF R PH TRIP | Operated | Reset | RS_OP_REF_R
A |  |  | Protection;SenRefPDIF1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P141_64R | PROTECTION | REF Y PH TRIP | Operated | Reset | RS_OP_REF_Y | [12 empty] | None | [11 empty] | 1 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R412_P141_64R | PROTECTION | REF B PH TRIP | Operated | Reset | RS_OP_REF_B | [12 empty] | None |  | No | [9 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind1;stVal;SPS | SPE_HLA_Reset_Trip | SPS | 400kV | R412_P141_64R | SYSTEM | REACTOR WTI ALARM | Set | Reset | RS_TR_REC PRV | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind1;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | System;OptGGIO1 | ST;Ind2;stVal;SPS | SPE_HLA_Reset_Trip | SPS | 400kV | R412_P141_64R | SYSTEM | REACTOR OTI TRIP | Operated | Reset | RS_TR_REC OTI | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind2;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | R412_P141_64R | SYSTEM | BUCHHOLZ ALARM | Set | Reset | RS_TR_BUCH | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind5;stVal;SPS
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | R412_P141_64R
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P141_64R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P141_64R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P141_64R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P141_64R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P141_64R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P141_64R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P141_64R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P141_64R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P141_64R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P141_64R
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | R412_P141_64R
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P141_64R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P141_64R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P141_64R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P141_64R
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | R412_P141_64R
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R412_P141_64R
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R412_P141_64R
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | R412_P141_64R
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P141_64R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P141_64R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P141_64R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P141_64R
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D37: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E37: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D51: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E51: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC51: HMI Display : Specify if the data appears in HMI.
Note on AD51: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE51: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D59: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E59: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D65: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E65: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB65: LCD Display : Specify if the data appears in computer LCD.
Note on AC65: HMI Display : Specify if the data appears in HMI.
Note on AD65: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE65: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC128: HMI Display : Specify if the data appears in HMI.
Note on AD128: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE128: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB148: LCD Display : Specify if the data appears in computer LCD.
Note on AC148: HMI Display : Specify if the data appears in HMI.
Note on AD148: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE148: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R412_P442_21R
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R412_P442_21R |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R412_P442_21R
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R412_P442_21R
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R412_P442_21R | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R412_P442_21R
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R412_P442_21R | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R412_P442_21R
A |  |  | Protection;PTRC1 | ST;Tr;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P442_21R | PROTECTION | GENERAL TRIP | Operated | Reset | RS_OP_GEN TRIP | Transmitted to IEC | [7 empty] | Protection;PTRC1 | ST;Tr;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CbfRBRF1 | ST;OpEx;general;ACT | SPE_HLA_Normal_Fail | SPS | 400kV | R412_P442_21R | PROTECTION | VT FUSE FAIL | Alarm | Normal | NL_FL_VT FUSE | Transmitted to IEC | [7 empty] | System;AlmGGIO1 | ST;Alm6;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsA;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P442_21R | PROTECTION | BACKUP IMPEDENCE R-PH TRIP | Operated | Reset | RS_OP_B/U IMP R | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phsA;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsB;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P442_21R | PROTECTION | BACKUP IMPEDENCE Y-PH TRIP | Operated | Reset | RS_OP_B/U IMP Y | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phsB;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;phsC;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P442_21R | PROTECTION | BACKUP IMPEDENCE B-PH TRIP | Operated | Reset | RS_OP_B/U IMP B | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;phsC;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P442_21R | PROTECTION | BACKUP IMPEDENCE | Operated | Reset | RS_OP_B/U IMP | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;DisPDIS1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Start | SPS | 400kV | R412_P442_21R | PROTECTION | REACTOR BACKUP IMPEDANE PICKUP | set | Reset | RS_ST_Z1 START | Transmitted to IEC | [7 empty] | Protection;DisPDIS1 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | #REF!
A |  |  |  |  | SPARE | SPS | 400kV | R412_P442_21R | PROTECTION | BACKUP IMPEDANCE Z-1 TRIP | Operated | Reset | RS_OP_Z1 TRP | [12 empty] | None |  | No | [9 empty] | 1 | #REF!
SPS
|  |  | DIGITAL INFORMATION TO IED |  |  | SPS | IED name | R412_P442_21R
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data | SPS |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | SPS | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P442_21R
A |  |  |  |  | SPARE | SPS | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P442_21R
A |  |  |  |  | SPARE | SPS | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P442_21R
A |  |  |  |  | SPARE | SPS | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P442_21R
A |  |  |  |  | SPARE | SPS | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P442_21R
A |  |  |  |  | SPARE | SPS | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P442_21R
A |  |  |  |  | SPARE | SPS | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P442_21R
A |  |  |  |  | SPARE | SPS | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P442_21R
A |  |  |  |  | SPARE | SPS | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P442_21R
A |  |  |  |  | SPARE | SPS | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P442_21R
SPS
|  |  | ANALOG INFORMATION FROM IED |  |  | SPS | IED name | R412_P442_21R
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data | SPS |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | SPS | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P442_21R
A |  |  |  |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P442_21R
A |  |  |  |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P442_21R
A |  |  |  |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P442_21R
SPS
|  |  | ANALOG INFORMATION TO IED |  |  | SPS | IED name | R412_P442_21R
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data | SPS |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | SPS | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS | [31 empty] | 13 | ANALOG INFORMATION TO IED IED name R412_P442_21R
A |  |  |  |  | SPARE | SPS | [31 empty] | 13 | ANALOG INFORMATION TO IED IED name R412_P442_21R
SPS
|  |  | COUNTER INFORMATION FROM IED |  |  | SPS | IED name | R412_P442_21R
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data | SPS |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | SPS | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P442_21R
A |  |  |  |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P442_21R
A |  |  |  |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P442_21R
A |  |  |  |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P442_21R
|  |  | END OF IED DATA |  |  | SPS
SPS
|  |  | DI GROUPS |  |  | SPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data | SPS |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | SPS | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SPS
|  |  | SELF GENERATED DIGITAL INFORMATION |  |  | SPS
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data | SPS |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SPS
|  |  | SELF GENERATED DIGITAL OUTPUT INFORMATION |  |  | SPS
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data | SPS |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPS | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPS | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPS | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPS | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPS | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPS | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPS | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPS | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPS | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SPS
|  |  | SELF GENERATED ANALOG INFORMATION |  |  | SPS
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data | SPS |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SPS
|  |  | SELF GENERATED COUNTER INFORMATION |  |  | SPS
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data | SPS |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SPS
|  |  | SELF GENERATED SETPOINT INFORMATION |  |  | SPS
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data | SPS |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | SPS | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | SPS | [21 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
SPS
END OF DATA | [5 empty] | SPS
[6 empty] | SPS | 400kV | R412_P442_21R | PROTECTION | BACKUP OVERCURRENT START | Start | Reset | RS_ST_O/C | [8 empty] | Protection;OcpPTOC1 | ST;Op;general;general;ACD
[6 empty] | SPS | 400kV | R412_P442_21R | PROTECTION | BACKUP OVERCURRENT TRIP | Operated | Reset | RS_OP_O/C | [8 empty] | Protection;OcpPTOC1 | ST;Str;general;general;ACT
[6 empty] | SPS | 400kV | R412_P442_21R | PROTECTION | BACKUP EARTHFAULT START | Start | Reset | RS_ST_O/C | [8 empty] | Protection;EfdPTOC1 | ST;Op;general;ACD
[6 empty] | SPS | 400kV | R412_P442_21R | PROTECTION | BACKUP EARTHFAULT TRIP | Operated | Reset | RS_OP_O/C | [8 empty] | Protection;EfdPTOC1 | ST;Str;general;ACT
[6 empty] | SPS | 400kV | R412_P442_21R | SYSTEM | NGR OTI ALARM | Set | Reset | RS_ST_NGR_OTI AM | [8 empty] | System;OptGGIO1 | ST;IndXX;stVal;SPS
[6 empty] | SPS | 400kV | R412_P442_21R | SYSTEM | NGR OTI TRIP | Operated | Reset | RS_OP_NGR_OTI OP | [8 empty] | System;OptGGIO1 | ST;IndXX;stVal;SPS
[6 empty] | SPS | 400kV | R412_P442_21R | SYSTEM | NGR PRD TRIP | Operated | Reset | RS_OP_NGR_PRD OP | [8 empty] | System;OptGGIO1 | ST;IndXX;stVal;SPS
N | [5 empty] | SPS | 400kV | R412_P442_21R | SYSTEM | NGR BUCHHOLZ TRIP | Operated | Reset | RS_OP_NGR_BUC TR | [8 empty] | System;OptGGIO1 | ST;IndXX;stVal;SPS
[6 empty] | SPS | 400kV | R412_P442_21R | PROTECTION | NGR BYPASS STAGE | Operated | Reset | RS_OP_NGR_BYP | [8 empty] | System;OptGGIO1 | ST;IndXX;stVal;SPS
[6 empty] | SPS | 400kV | R412_P442_21R | PROTECTION | NGR BYPASS CB CLOSE | Set | Reset | RS_ST_NGR_BYCB | [8 empty] | System;OptGGIO1 | ST;IndXX;stVal;SPS
[6 empty] | SPS | 400kV | R412_P442_21R | SYSTEM | NGR CLOSE COIL SUPERVISION | Healthy | Unhealthy | UHHL_NGR_CB SUP | [8 empty] | System;OptGGIO1 | ST;IndXX;stVal;SPS
[6 empty] | SPS | 400kV | R412_P442_21R
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D33: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E33: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D47: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E47: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC47: HMI Display : Specify if the data appears in HMI.
Note on AD47: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE47: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D55: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E55: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D61: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E61: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB61: LCD Display : Specify if the data appears in computer LCD.
Note on AC61: HMI Display : Specify if the data appears in HMI.
Note on AD61: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE61: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC124: HMI Display : Specify if the data appears in HMI.
Note on AD124: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE124: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB144: LCD Display : Specify if the data appears in computer LCD.
Note on AC144: HMI Display : Specify if the data appears in HMI.
Note on AD144: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE144: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R412_P743_PU_A
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R412_P743_PU_A |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R412_P743_PU_A
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R412_P743_PU_A
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R412_P743_PU_A | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R412_P743_PU_A
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R412_P743_PU_A | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | [8 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R412_P743_PU_A
A |  |  | System;GosGGIO2 | ST;Ind1;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P743_PU_A | GOOSE | LBB START | Set | Reset | RS_OP_LBB START | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind1;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R412_P743_PU_A
A |  |  | System;OptGGIO1 | ST;Ind7;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P743_PU_A | SYSTEM | LBB INITIATION 3-PH | Set | Reset | RS_OP_LBB INI 3P | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind7;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CbfBbpRBRF1 | ST;OpIn;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P743_PU_A | PROTECTION | EXTERNAL CB FAILURE RETRIP | Operated | Reset | RS_OP_CB FAIL S1 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF1 | ST;OpIn;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CbfBbpRBRF2 | ST;OpEx;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P743_PU_A | PROTECTION | EXTERNAL CB FAILURE BACK TRIP | Operated | Reset | RS_OP_CB FAIL S2 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF2 | ST;OpEx;general;ACT |  |  | None | [11 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | R412_P743_PU_A | PROTECTION | CB FAILURE RETRIP | Operated | Reset | RS_OP_CB FAIL S3 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF3 | ST;OpIn;general;ACT
[6 empty] | SPS | 400kV | R412_P743_PU_A | PROTECTION | CB FAILURE BACK TRIP | Operated | Reset | RS_OP_CB FAIL S4 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF4 | ST;OpEx;general;ACT
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | R412_P743_PU_A
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_A
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_A
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | R412_P743_PU_A
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P743_PU_A
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | R412_P743_PU_A
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R412_P743_PU_A
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R412_P743_PU_A
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | R412_P743_PU_A
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P743_PU_A
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P743_PU_A
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on W22: Arnab Ghosh {अर्नब घोष}: Please clarify why it is taken from GosGGIO
Note on D30: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E30: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D44: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E44: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC44: HMI Display : Specify if the data appears in HMI.
Note on AD44: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE44: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D52: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E52: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D58: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E58: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB58: LCD Display : Specify if the data appears in computer LCD.
Note on AC58: HMI Display : Specify if the data appears in HMI.
Note on AD58: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE58: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC121: HMI Display : Specify if the data appears in HMI.
Note on AD121: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE121: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB141: LCD Display : Specify if the data appears in computer LCD.
Note on AC141: HMI Display : Specify if the data appears in HMI.
Note on AD141: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE141: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R412_P743_PU_B
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
IEC Description
Keys :
|  |  | Computer Name |  | R412_P743_PU_B |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R412_P743_PU_B
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name | R412_P743_PU_B
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R412_P743_PU_B | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R412_P743_PU_B
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 400kV | R412_P743_PU_B | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | [8 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R412_P743_PU_B
A |  |  | System;GosGGIO2 | ST;Ind1;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P743_PU_B | GOOSE | LBB START | Set | Reset | RS_OP_LBB START | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind1;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | DIGITAL INFORMATION FROM IED IED name R412_P743_PU_B
A |  |  | System;OptGGIO1 | ST;Ind7;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P743_PU_B | SYSTEM | LBB INITIATION 3-PH | Set | Reset | RS_OP_LBB INI 3P | Transmitted to IEC | [7 empty] | System;OptGGIO1 | ST;Ind7;stVal;SPS |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CbfBbpRBRF1 | ST;OpIn;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P743_PU_B | PROTECTION | EXTERNAL CB FAILURE RETRIP | Operated | Reset | RS_OP_CB FAIL S1 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF1 | ST;OpIn;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;CbfBbpRBRF2 | ST;OpEx;general;ACT | SPE_HLA_Reset_Optd | SPS | 400kV | R412_P743_PU_B | PROTECTION | EXTERNAL CB FAILURE BACK TRIP | Operated | Reset | RS_OP_CB FAIL S2 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF2 | ST;OpEx;general;ACT |  |  | None | [11 empty] | 1 | #REF!
[6 empty] | SPS | 400kV | R412_P743_PU_B | PROTECTION | CB FAILURE RETRIP | Operated | Reset | RS_OP_CB FAIL S3 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF3 | ST;OpIn;general;ACT
[6 empty] | SPS | 400kV | R412_P743_PU_B | PROTECTION | CB FAILURE BACK TRIP | Operated | Reset | RS_OP_CB FAIL S4 | Transmitted to IEC | [7 empty] | Protection;CbfBbpRBRF4 | ST;OpEx;general;ACT
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | R412_P743_PU_B
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_B
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R412_P743_PU_B
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | R412_P743_PU_B
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R412_P743_PU_B
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | R412_P743_PU_B
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R412_P743_PU_B
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R412_P743_PU_B
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | R412_P743_PU_B
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P743_PU_B
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R412_P743_PU_B
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on W22: Arnab Ghosh {अर्नब घोष}: Please clarify why it is taken from GosGGIO
Note on D30: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E30: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D44: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E44: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC44: HMI Display : Specify if the data appears in HMI.
Note on AD44: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE44: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D52: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E52: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D58: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E58: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB58: LCD Display : Specify if the data appears in computer LCD.
Note on AC58: HMI Display : Specify if the data appears in HMI.
Note on AD58: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE58: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC121: HMI Display : Specify if the data appears in HMI.
Note on AD121: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE121: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB141: LCD Display : Specify if the data appears in computer LCD.
Note on AC141: HMI Display : Specify if the data appears in HMI.
Note on AD141: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE141: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## BCU B401_LINE
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
MiCOM C264 DESCRIPTION
Keys :
|  |  | Computer Name |  | B401_LINE |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | C264 |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 0
|  |  | Digital Inputs Board Slot |  | P
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | P | 1 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 2 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 3 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 4 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 5 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 6 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 7 | SPE_HLA_Reset_Optd | SPS | 400kV | B401-LINE | 52 | GEN SF6 LOCKOUT | Operated | Reset | RS_OP_SF6 L/O | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind12;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 8 | SPE_HLA_Normal_Alarm | SPS | 400kV | B401-LINE | 52 | POLE DISCREPANCY | Alarm | Normal | RS_OP_POLE DISC | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind13;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 9 | SPE_HLA_Normal_Alarm | SPS | 400kV | B401-LINE | 52 | LOSS OF SF6 GAS POLE A/B/C-1 | Alarm | Normal | NL_AL_LOSS SF6-1 | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind14;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 10 | SPE_HLA_Normal_Alarm | SPS | 400kV | B401-LINE | 52 | LOSS OF SF6-2 | Alarm | Normal | NL_AL_LOSS SF6-2 | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind2;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 11 | SPE_HLA_Normal_Alarm | SPS | 400kV | B401-LINE | 52 | SF6 LO PRESSURE LOCKOUT | Alarm | Normal | NO_LO_SF6 LO LOW | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind3;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 12 | SPE_HLA_Normal_Alarm | SPS | 400kV | B401-LINE | 52 | POLE DISCREPANCY | Alarm | Normal | NL_AL_POLE DIS | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind4;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 13 | SPE_HLA_Normal_Fail | SPS | 400kV | B401-LINE | 52 | DC SUPPLY-1\2 | Fail | Normal | NL_FL_DC SUP12 | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind5;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 14 | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | 52 | REMOTE POS | Set | Reset | RS_ST_REMOTE | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind6;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 15 | SPE_HLA_Normal_Alarm | SPS | 400kV | B401-LINE | 52 | SPRING CHARGE STATUS B | Alarm | Normal | DS_CH_SPING ST A | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind1;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 16 | SPE_HLA_Normal_Alarm | SPS | 400kV | B401-LINE | 52 | SPRING CHARGE STATUS A | Alarm | Normal | DS_CH_SPING ST B | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind10;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 1
|  |  | Digital Inputs Board Slot |  | O
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | O | 1 | SPE_HLA_Normal_Alarm | SPS | 400kV | B401-LINE | 52 | SPRING CHARGE STATUS C | Alarm | Normal | DS_CH_SPING ST C | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind7;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 2 | SPE_HLa_Dischrgd_Charged | SPS | 400kV | B401-LINE | 52 | AR CB | Charged | Discharged | DS_CH_SPRING | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind11;stVal;SPS |  | 215;216;217; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 3 | SPE_HLA_Normal_Alarm | SPS | 400kV | B401-LINE | 52 | TROUBLE | Alarm | Normal | NL_AL_TROUBLE1 | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind8;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 4 | SPE_HLA_Normal_Alarm | SPS | 400kV | B401-LINE | 52 | TROUBLE | Alarm | Normal | NL_AL_TROUBLE2 | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind9;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 5 | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89A | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI1 | ST;Pos;stVal;DPC |  | 205;206;210; | None |  |  | 58 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 6 | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89A | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI1 | ST;Pos;stVal;DPC |  | 205;206;210; | None |  |  | 58 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 7 | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89AE | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI3 | ST;Pos;stVal;DPC |  | 202;203;204;207;208;209; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 8 | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89AE | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI3 | ST;Pos;stVal;DPC |  | 202;203;204;207;208;209; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 9 | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89AE2 | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI4 | ST;Pos;stVal;DPC |  | 202;203;204;268;269;270;333;334;335;409;410;411;462;463;464;538;539;540;602;603;604; | None | [5 empty] | Yes |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 10 | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89AE2 | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI4 | ST;Pos;stVal;DPC |  | 202;203;204;268;269;270;333;334;335;409;410;411;462;463;464;538;539;540;602;603;604; | None | [5 empty] | Yes |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 11 | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89B | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI2 | ST;Pos;stVal;DPC |  | 205;210; | None |  |  | 59 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 12 | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89B | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI2 | ST;Pos;stVal;DPC |  | 205;210; | None |  |  | 59 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 13 | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89BE | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI1 | ST;Pos;stVal;DPC |  | 202;203;204;207;208;209; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 14 | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89BE | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI1 | ST;Pos;stVal;DPC |  | 202;203;204;207;208;209; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 15 | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89L | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI3 | ST;Pos;stVal;DPC |  | 214;242;244; | None |  |  | 60 |  |  | Yes |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 16 | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89L | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI3 | ST;Pos;stVal;DPC |  | 214;242;244; | None |  |  | 60 |  |  | Yes |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 2
|  |  | Digital Inputs Board Slot |  | N
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | N | 1 | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89LE | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI2 | ST;Pos;stVal;DPC |  | 211;212;213; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 2 | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89LE | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI2 | ST;Pos;stVal;DPC |  | 211;212;213; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 3 | SPE_HLA_Normal_Fail | SPS | 400kV | B401-LINE | PROTECTION | CARRIER SPEECH CHANNEL | Fail | Normal | NL_FL_CARR SPECH | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind8;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 4 | SPE_HLA_Normal_Fail | SPS | 400kV | B401-LINE | PROTECTION | DC SOURCE-1 | Fail | Normal | NL_FL_DC SOURCE1 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind1;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 5 | SPE_HLA_Normal_Fail | SPS | 400kV | B401-LINE | PROTECTION | DC SOURCE-2 | Fail | Normal | NL_FL_DC SOURCE2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind5;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 6 | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | B401-LINE | PROTECTION | PMU | Healthy | Unhealthy | UH_HL_PMU | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind2;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 7 | SPE_HLA_Healthy_Flty | SPS | 400kV | B401-LINE | PROTECTION | CB TC-2 | Faulty | Healthy | HL_FT_CB TC2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind6;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 8 | SPE_HLA_Reset_Optd | SPS | 400kV | B401-LINE | AR FUNCTION | BLOCK CONTACTS | Operated | Reset | RS_OP_AR BLOCK | Transmitted to IEC | [7 empty] | CONTROL1;RREC1 | ST;Ind1;stVal;SPS |  |  | None | [7 empty] | ARFct | AR_Blocking_SPS |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 9 | SPE_HLA_Reset_Optd | SPS | 400kV | B401-LINE | AR FUNCTION | R-PH INITIATION | Operated | Reset | RS_OP_PHR INI | Transmitted to IEC | [7 empty] | CONTROL1;RREC1 | ST;Ind2;stVal;SPS |  | 216; | None | [7 empty] | ARFct | TripPhA_SPS |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 10 | SPE_HLA_Reset_Optd | SPS | 400kV | B401-LINE | AR FUNCTION | Y-PH INITIATION | Operated | Reset | RS_OP_PHY INI | Transmitted to IEC | [7 empty] | CONTROL1;RREC1 | ST;Ind3;stVal;SPS |  | 216; | None | [7 empty] | ARFct | TripPhB_SPS |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 11 | SPE_HLA_Reset_Optd | SPS | 400kV | B401-LINE | AR FUNCTION | B-PH INITIATION | Operated | Reset | RS_OP_PHB INI | Transmitted to IEC | [7 empty] | CONTROL1;RREC1 | ST;Ind4;stVal;SPS |  | 216; | None | [7 empty] | ARFct | TripPhC_SPS |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 12 | SPE_HLA_Reset_Optd | SPS | 400kV | B401-LINE | PROTECTION | A/R LOCKOUT RELAY | Operated | Reset | OP_RS_86LO | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind7;stVal;SPS |  | 201; | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 13 | SPE_HLA_Reset_Optd | SPS | 400kV | B401-LINE | PROTECTION | DT SEND CHANNEL-1 | Operated | Reset | RS_OP_DT SND CH1 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind9;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 14 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 15 | SPE_HLA_Reset_Optd | SPS | 400kV | B401-LINE | PROTECTION | DT SEND CHANNEL-2 | Operated | Reset | RS_OP_DT SND CH2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind10;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 16 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 3
|  |  | Digital Inputs Board Slot |  | M
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | M | 1 | DP_HLA_Trip_Closed | DPS | 400kV | B401-LINE | 52 | EMERGENCY/MANUAL | Closed |  | TP_CL_EMRG/MAN | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;DPCSO1;stVal;DPC |  | 220;221; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 2 | DP_HLA_Trip_Closed | DPS | 400kV | B401-LINE | 52 | EMERGENCY/MANUAL |  | Trip | TP_CL_EMRG/MAN | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;DPCSO1;stVal;DPC |  | 220;221; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 3 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 4 | SPE_HLa_Reset_Out | SPS | 400kV | B401-LINE | PROTECTION | CARR CH-1 | Out | Reset | RS_OT_CARR CH-1 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind3;stVal;SPS |  | 216; | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 5 | SPE_HLa_Reset_Out | SPS | 400kV | B401-LINE | PROTECTION | CARR CH-2 | Out | Reset | RS_OT_CARR CH-2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind4;stVal;SPS |  | 216; | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 6 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 7 | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | SURGE | LA COUNTER R-PH | Set | Reset | RS_ST_LA R-PH | Transmitted to IEC | [7 empty] | CONTROL1;GGIO4 | ST;Ind1;stVal;SPS |  |  | None |  |  |  |  | 222 | [6 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 8 | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | SURGE | LA COUNTER Y-PH | Set | Reset | RS_ST_LA Y-PH | Transmitted to IEC | [7 empty] | CONTROL1;GGIO4 | ST;Ind2;stVal;SPS |  |  | None |  |  |  |  | 222 | [6 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 9 | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | SURGE | LA COUNTER B-PH | Set | Reset | RS_ST_LA B-PH | Transmitted to IEC | [7 empty] | CONTROL1;GGIO4 | ST;Ind3;stVal;SPS |  |  | None |  |  |  |  | 222 | [6 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 10 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 11 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 12 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 13 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 14 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 15 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 16 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 4
|  |  | Digital Inputs Board Slot |  | L
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | L | 1 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 2 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 3 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 4 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 5 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 6 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 7 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 8 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 9 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 10 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 11 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 12 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 13 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 14 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 15 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 16 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 0
|  |  | Digital Outputs Board Slot |  | D
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | D | 1 | DC_SBO_Open_Close | DPC | 400kV | B401-LINE | 52 | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI4 | CO;Pos;sboClass;DPC | [5 empty] | 57 |  |  | NO |  | CB | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 2 | SC_DE_Reset_Set_1 | SPC | 400kV | B401-LINE | PROTECTION | CB TRIP COIL-2 | Set |  | XX_XX_TC2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO3;ctlVal;DPC | [6 empty] | 207 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 3 | DC_SBO_Open_Close | DPC | 400kV | B401-LINE | 52 | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI4 | CO;Pos;sboClass;DPC | [5 empty] | 57 |  |  | NO |  | CB | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 4 | SC_DE_Reset_Set_1 | SPC | 400kV | B401-LINE | PROTECTION | CB CLOSE TO PUA | Set |  | XX_XX_CB CLS PUA | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO8;ctlVal;DPC | [6 empty] | 222 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 5 | SC_DE_Reset_Set_1 | SPC | 400kV | B401-LINE | PROTECTION | CB CLOSE TO PUB | Set |  | XX_XX_CB CLS PUB | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO9;ctlVal;DPC | [6 empty] | 221 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 6 | SC_DE_Reset_Reset | SPC | 400kV | B401-LINE | AR DATA | TO A/R CLSG. CKT | Reset |  | XX_XX_A/R CLSG C | Transmitted to IEC | [7 empty] | CONTROL1;GGIO2 | CO;SPCSO1;ctlVal;DPC | [6 empty] | 335 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 7 | SC_DE_Off_On_1 | SPC | 400kV | B401-LINE | AR DATA | A/R OFF | On | Off | XX_XX_A/R OFF | Transmitted to IEC | [7 empty] | CONTROL1;GGIO2 | CO;SPCSO2;ctlVal;DPC | [6 empty] | 6 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 8 | SC_DE_Reset_Reset | SPC | 400kV | B401-LINE | AR DATA | A/R LOCKOUT TRIP | Reset |  | XX_XX_A/R L/O | Transmitted to IEC | [7 empty] | CONTROL1;GGIO2 | CO;SPCSO3;ctlVal;DPC | [6 empty] | 334 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 9 | SC_DE_Reset_Set | SPC | 400kV | B401-LINE | AR DATA | MAIN CB A/R OPTD | Set |  | XX_XX_MAIN CB AR | Transmitted to IEC | [7 empty] | CONTROL1;GGIO2 | CO;SPCSO5;ctlVal;DPC | [6 empty] | 336 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 10 | SC_DE_Reset_Set | SPC | 400kV | B401-LINE | AR DATA | TO TIE A/R PROIRITY CKT HOLD | Set |  | XX_XX_TI AR CKTH | Transmitted to IEC | [7 empty] | CONTROL1;GGIO2 | CO;SPCSO4;ctlVal;DPC | [6 empty] | 337 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 1
|  |  | Digital Outputs Board Slot |  | E
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | E | 1 | DC_SBO_Open_Close | DPC | 400kV | B401-LINE | 89A | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | CO;Pos;sboClass;DPC | [5 empty] | 58 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 2 | DC_SBO_Open_Close | DPC | 400kV | B401-LINE | 89A | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | CO;Pos;sboClass;DPC | [5 empty] | 58 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 3 | SC_DE_NotPerm_Perm | SPC | 400kV | B401-LINE | IL PERMISSIVE | 89A I/L PERMISSIVE |  |  | XX_XX_89A | Transmitted to IEC | [7 empty] | CONTROL1;GGIO3 | CO;SPCSO1;ctlVal;DPC | [6 empty] | 327 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 4 | SC_DE_NotPerm_Perm | SPC | 400kV | B401-LINE | IL PERMISSIVE | 89AE I/L PERMISSIVE |  |  | XX_XX_89AE | Transmitted to IEC | [7 empty] | CONTROL1;GGIO3 | CO;SPCSO3;ctlVal;DPC | [6 empty] | 328 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 5 | DC_SBO_Open_Close | DPC | 400kV | B401-LINE | 89B | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | CO;Pos;sboClass;DPC | [5 empty] | 59 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 6 | DC_SBO_Open_Close | DPC | 400kV | B401-LINE | 89B | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | CO;Pos;sboClass;DPC | [5 empty] | 59 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 7 | SC_DE_NotPerm_Perm | SPC | 400kV | B401-LINE | IL PERMISSIVE | 89B I/L PERMISSIVE |  |  | XX_XX_89B | Transmitted to IEC | [7 empty] | CONTROL1;GGIO3 | CO;SPCSO2;ctlVal;DPC | [6 empty] | 330 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 8 | SC_DE_NotPerm_Perm | SPC | 400kV | B401-LINE | IL PERMISSIVE | 89BE I/L PERMISSIVE |  |  | XX_XX_89BE | Transmitted to IEC | [7 empty] | CONTROL1;GGIO3 | CO;SPCSO5;ctlVal;DPC | [6 empty] | 331 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 9 | SC_DE_Reset_Set | SPC | 400kV | B401-LINE | PROTECTION | SOTF INI M-1 | Set |  | XX_XX_SOTF_M1 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO10;ctlVal;DPC | [6 empty] | 341 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 10 | SC_DE_Reset_Set | SPC | 400kV | B401-LINE | PROTECTION | SOTF INI M-2 | Set |  | XX_XX_SOTF_M2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO2;ctlVal;DPC | [6 empty] | 340 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 2
|  |  | Digital Outputs Board Slot |  | F
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | F | 1 | DC_SBO_Open_Close | DPC | 400kV | B401-LINE | 89L | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | CO;Pos;sboClass;DPC | [5 empty] | 60 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 2 | DC_SBO_Open_Close | DPC | 400kV | B401-LINE | 89L | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | CO;Pos;sboClass;DPC | [5 empty] | 60 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 3 | SC_DE_NotPerm_Perm | SPC | 400kV | B401-LINE | IL PERMISSIVE | 89L I/L PERMISSIVE |  |  | XX_XX_89L | Transmitted to IEC | [7 empty] | CONTROL1;GGIO3 | CO;SPCSO4;ctlVal;DPC | [6 empty] | 332 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 4 | SC_DE_NotPerm_Perm | SPC | 400kV | B401-LINE | IL PERMISSIVE | 89LE I/L PERMISSIVE |  |  | XX_XX_89LE | Transmitted to IEC | [7 empty] | CONTROL1;GGIO3 | CO;SPCSO6;ctlVal;DPC | [6 empty] | 333 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 5 | SC_DE_Reset_Set_1 | SPC | 400kV | B401-LINE | PROTECTION | 86A TRIP RELAY | Set |  | XX_RS_86A | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO1;ctlVal;DPC | [8 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 6 | SC_DE_Reset_Set_1 | SPC | 400kV | B401-LINE | PROTECTION | 86B TRIP RELAY | Set |  | XX_RS_86B | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO7;ctlVal;DPC | [8 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 7 | SC_DE_NotPerm_Perm_1 | SPC | 400kV | B401-LINE | PROTECTION | 86LO TRIP RELAY |  |  | XX_RS_86LO | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO5;ctlVal;DPC | [8 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 8 | SC_DE_Reset_Set | SPC | 400kV | B401-LINE | PROTECTION | DT SEND CHANNEL-1 | Set |  | XX_XX_DT SND CH1 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO4;ctlVal;DPC | [6 empty] | 338 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 9 | SC_DE_Reset_Set | SPC | 400kV | B401-LINE | PROTECTION | DT SEND CHANNEL-2 | Set |  | XX_XX_DT SND CH2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO6;ctlVal;DPC | [6 empty] | 339 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 10 | SC_DE_NotPerm_Perm | SPC | 400kV | B401-LINE | IL PERMISSIVE | 89BE2 I/L PERMISSIVE |  |  | XX_XX_89BE2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO3 | CO;SPCSO7;ctlVal;DPC | [6 empty] | 329 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 3
|  |  | Digital Outputs Board Slot |  | G
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | G | 1 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 2 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 3 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 4 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 5 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 6 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 7 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 8 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 9 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 10 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
CT/VT ANALOG INPUT BOARD TMU2x0
|  |  | CT/VT Board Number |  | 0
|  |  | CT/VT Board Slot |  | Q
|  |  | CT/VT Board Model |  | TMU220
CT acquisition
VT acquisition
|  |  | Nominal Current |  | 1 | (1A/5A)
|  |  | Nominal Voltage |  | 110 | [1V … 500V]
Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Input type (U/I) |  | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | DF |  | MV_HLa_Frequency_1 | Hz | 400kV | B401-LINE | SYNCH DATA | FREQUENCY DIFFERENCE | 0.0 | 2.0 | FREQUENCY DIFF | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | MX;DifHzClc;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | DV |  | MV_hla_ AuxVoltage_1 | V | 400kV | B401-LINE | SYNCH DATA | VOLTAGE DIFFERENCE | 0.0 | 277.13626 | VOLTAGE DIFF | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | MX;DifVClc;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Dj |  | MV_hla_PhaseDiff | ˚ | 400kV | B401-LINE | SYNCH DATA | PHASE DIFFERENCE | 0.0 | 360.0 | PHASE ANGLE DIFF | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | MX;DifAngClc;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ia |  | MV_HLa_AuxCurrent | A | 400kV | B401-LINE | METERING | I-R PHASE CURRENT | 0.0 | 2400.0 | IR PHASE CURRENT | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;A;phsA;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ib |  | MV_HLa_AuxCurrent | A | 400kV | B401-LINE | METERING | I-Y PHASE CURRENT | 0.0 | 2400.0 | IY PHASE CURRENT | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;A;phsB;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ic |  | MV_HLa_AuxCurrent | A | 400kV | B401-LINE | METERING | I-B PHASE CURRENT | 0.0 | 2400.0 | IB PHASE CURRENT | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;A;phsC;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Vb |  | MV_hla_ AuxVoltage_1 | V | 400kV | B401-LINE | SYNCH DATA | INCOMING SUPPLY | 0.0 | 277.13626 | INCOMING SUPPLY | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU2 | MX;PhV;phsB;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Uab |  | MV_hla_ AuxVoltage | V | 400kV | B401-LINE | METERING | R-Y VOLTAGE | 0.0 | 480.0 | R-Y VOLTAGE | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;PPV;phsAB;DELTA | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ubc |  | MV_HLa_Voltage | kV | 400kV | B401-LINE | METERING | Y-B VOLTAGE | 0.0 | 480.0 | Y-B VOLTAGE | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;PPV;phsBC;DELTA | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Uca |  | MV_HLa_Voltage | kV | 400kV | B401-LINE | METERING | B-R VOLTAGE | 0.0 | 480.0 | B-R VOLTAGE | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;PPV;phsCA;DELTA | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Vbusbar |  | MV_hla_ AuxVoltage_1 | V | 400kV | B401-LINE | SYNCH DATA | RUNNING SUPPLY | 0.0 | 277.13626 | RUNNING SPLY-1 | Transmitted to IEC | [7 empty] | MEASUREMENT1;barMMXU1 | MX;PhV;phsA;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Freq (Line) |  | MV_HLa_Frequency | Hz | 400kV | B401-LINE | METERING | FREQUENCY | 45.0 | 55.0 | FREQUENCY | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;Hz;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | P total (MW) |  | MV_HLa_ActPower | MW | 400kV | B401-LINE | METERING | ACTIVE POWER | -1662.72 | 1662.72 | ACTIVE POWER | Transmitted to IEC | [7 empty] | MEASUREMENT1;powMMXU1 | MX;TotW;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Q total (Mvar) |  | MV_HLa_ActPower | MW | 400kV | B401-LINE | METERING | REACTIVE POWER | -1662.72 | 1662.72 | REACTIVE POWER | Transmitted to IEC | [7 empty] | MEASUREMENT1;powMMXU1 | MX;TotVAr;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | cos ft : Power factor |  | MV_HLa_PowerFactor |  | 400kV | B401-LINE | METERING | POWER FACTOR | -1.2 | 1.2 | POWER FACTOR | Transmitted to IEC | [7 empty] | MEASUREMENT1;powMMXU1 | MX;TotPF;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  |  |  | SPARE | [32 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  |  |  | SPARE | [32 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | 52 ¦ OE_CL_CONTROL | OPEN ORDER | Set | Reset | RS_ST_OPN ORD | Transmitted to IEC | [7 empty] | CONTROL1;CSWI4 | ST;OpnOrd;general;general;ACT |  | 220; | None |  |  |  | 207 |  |  |  | CB | OpenOrderSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B401-LINE | 89A ¦ OE_CL_CONTROL | OPEN INTERLOCK | Permissive | Not Permissive | NP_PE_OPN ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO1 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | SG | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B401-LINE | 89B ¦ OE_CL_CONTROL | OPEN INTERLOCK | Permissive | Not Permissive | NP_PE_OPN ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO2 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | SG | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B401-LINE | 89L ¦ OE_CL_CONTROL | OPEN INTERLOCK | Permissive | Not Permissive | NP_PE_OPN ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO3 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | SG | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPS_hla_Set_Reset | SPS | 400kV | B401-LINE |  | ORDER RUNNING ON THE BAY | Set | Reset | RS_ST_ORD RUNING | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | ST;OrdRun;stVal;SPS |  |  | None | [8 empty] | OrderInProgress |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B401-LINE | 52 ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | NP_PE_CLOSE ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO4 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | CB | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B401-LINE | 89A ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | NP_PE_CLS ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO1 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | SG | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B401-LINE | 89B ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | NP_PE_CLS ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO2 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | SG | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B401-LINE | 89L ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | NP_PE_CLS ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO3 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | SG | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | SYNCH FUNCTION | CLOSE ORDER | Set | Reset | RS_ST_CLS ODR | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;ClsOpSt;stVal;SPS |  |  | None | [7 empty] | IntManualCSFct | CS_CloseOrderState_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPE_HLA_on_off | SPS | 400kV | B401-LINE | SYNCH FUNCTION | ON/OFF SECONDARY SPS | Off | On | RS_ST_ON/OFF SEC | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;EnaSec;origin;SPC |  |  | None |  |  | 191 |  |  |  |  | IntManualCSFct | CS_OnOff_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | SYNCH FUNCTION | POSSIBLE CLOSING | Set | Reset | RS_ST_POS CLS | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;Rel;stVal;SPS |  | 223; | None | [7 empty] | IntManualCSFct | CS_AuthoState_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | SYNCH FUNCTION | PRESENCE OF REFERENCE VOLTAGE | Set | Reset | RS_ST_REF U PRES | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;VRefInd;stVal;SPS |  | 223; | None | [7 empty] | IntManualCSFct | CS_VoltageRefPresence_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | SYNCH FUNCTION | ABSENCE OF REFERENCE VOLTAGE | Set | Reset | RS_ST_REF. U ABS | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;VRefAbs;stVal;SPS |  | 223; | None | [7 empty] | IntManualCSFct | CS_VoltageRefAbsence_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | SYNCH FUNCTION | VOLT ABSENCE | Set | Reset | RS_ST_VOLT ABS | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;VAbs;stVal;SPS |  | 214;223; | None | [7 empty] | IntManualCSFct | CS_VoltageAbsence_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | SYNCH FUNCTION | VOLT PRESENCE | Set | Reset | RS_ST_VOLT PRES | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;VP;stVal;SPS |  | 223; | None | [7 empty] | IntManualCSFct | CS_VoltagePresence_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 17 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B401-LINE | 52 ¦ OE_CL_CONTROL | CLOSE ORDER | Permissive | Not Permissive | RS_ST_CLS ORD | Transmitted to IEC | [7 empty] | CONTROL1;CSWI4 | ST;ClsOrd;general;general;ACT |  | 215;221; | None |  |  |  | 221;222 |  |  |  | CB | CloseOrderSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 18 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | AR DATA | LOCK | Set | Reset | RS_ST_S10_LOCK | Transmitted to IEC | [7 empty] | CONTROL1;GAPC3 | ST;IndSys1;stVal;SPS |  | 216; | None | [8 empty] | MappingSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 19 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | AR DATA | WAIT FOR CB CLOSE | Set | Reset | RS_ST_S7_WT CB C | Transmitted to IEC | [7 empty] | CONTROL1;GAPC3 | ST;IndSys4;stVal;SPS |  | 215; | None | [8 empty] | MappingSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 20 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | AR DATA | RECLAIM_TIMER | Set | Reset | RS_ST_S8_RC TIM | Transmitted to IEC | [7 empty] | CONTROL1;GAPC3 | ST;IndSys3;stVal;SPS |  |  | None | [8 empty] | MappingSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 21 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | AR DATA | LOCK_SHOTS | Set | Reset | RS_ST_S9_LO SHTS | Transmitted to IEC | [7 empty] | CONTROL1;GAPC3 | ST;IndSys2;stVal;SPS |  | 216; | None | [8 empty] | MappingSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 22 |  | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | B401-LINE | 52 | STATUS | Healthy | Unhealthy | UH_HL_STATUS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI4 | ST;IndSys1;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 23 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B401-LINE | 89A | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | ST;IndSys1;stVal;SPS |  | 202<; | None |  |  |  | 327 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 24 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B401-LINE | 89AE | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL2;CSWI3 | ST;IndSys1;stVal;SPS |  | 205<; | None |  |  |  | 328 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 25 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B401-LINE | 89AE2 | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL2;CSWI4 | ST;IndSys1;stVal;SPS |  | 206<; | None |  |  |  | 329 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 26 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B401-LINE | 89B | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | ST;IndSys1;stVal;SPS |  | 207<; | None |  |  |  | 330 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 27 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B401-LINE | 89BE | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL2;CSWI1 | ST;IndSys1;stVal;SPS |  | 210<; | None |  |  |  | 331 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 28 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B401-LINE | 89L | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | ST;IndSys1;stVal;SPS |  | 211<; | None |  |  |  | 332 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 29 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B401-LINE | 89LE | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL2;CSWI2 | ST;IndSys1;stVal;SPS |  | 214<; | None |  |  |  | 333 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 30 |  | SPE_HLA_Reset_Optd | SPS | 400kV | B401-LINE | AR DATA | LOCKOUT FROM AR LOGIC | Operated | Reset | RS_OP_AR LO FBD | Transmitted to IEC | [7 empty] | CONTROL1;GAPC3 | ST;IndSys5;stVal;SPS |  | 216<; | None |  |  |  | 334 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 31 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | AR DATA | A/R OPTD FROM FBD | Set | Reset | RS_ST_AR OPTD FB | Transmitted to IEC | [7 empty] | CONTROL1;GAPC3 | ST;IndSys6;stVal;SPS |  | 215<; | None |  |  |  | 335;336 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 32 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | AR DATA | PRIORITY CIRCUIT HOLD | Set | Reset | RS_ST_PRI HLD ON | Transmitted to IEC | [7 empty] | CONTROL1;GAPC3 | ST;IndSys7;stVal;SPS |  | 217<; | None |  |  |  | 337 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 33 |  | SPE_HLA_Reset_Optd | SPS | 400kV | B401-LINE | PROTECTION | DT SEND FBD | Operated | Reset | RS_OP_DT SND FBD | Transmitted to IEC | [7 empty] | CONTROL1;GAPC2 | ST;IndSys2;stVal;SPS |  | 220<; | None |  |  |  | 338;339 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 34 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | PROTECTION | SOTF TO RELAY | Set | Reset | RS_ST_SOTF TO RL | Transmitted to IEC | [7 empty] | CONTROL1;GAPC2 | ST;IndSys1;stVal;SPS |  | 221<; | None |  |  |  | 340;341 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 35 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | SYNCH DATA | CLOSE PERMISSIVE | Set | Reset | RS_ST_CB CLOSE | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | ST;IndSys5;stVal;SPS |  | 223<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 36 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | SYNCH DATA | DEAD INCOMING DEAD RUNNING | Set | Reset | RS_ST_DINC_DRUN | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | ST;IndSys4;stVal;SPS |  | 223<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 37 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | SYNCH DATA | DEAD INCOMING LIVE RUNNING | Set | Reset | RS_ST_DINC_LRUN | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | ST;IndSys3;stVal;SPS |  | 223<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 38 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | SYNCH DATA | LIVE INCOMING DEAD RUNNING | Set | Reset | RS_ST_LINC_DRUN | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | ST;IndSys2;stVal;SPS |  | 223<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 39 |  | SPE_HLa_Reset_Set | SPS | 400kV | B401-LINE | SYNCH DATA | LIVE INCOMING LIVE RUNNING | Set | Reset | RS_ST_LINC_LRUN | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | ST;IndSys1;stVal;SPS |  | 223<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 40 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B401-LINE | 52 | POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI4 | ST;Pos;stVal;DPC |  | 202;203;204;207;208;209;211;212;213;242;244; | None |  |  | 57 |  | 219 | Yes |  | CB | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 41 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B401-LINE | 52 | POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI4 | ST;Pos;stVal;DPC |  | 202;203;204;207;208;209;211;212;213;242;244; | None |  |  | 57 |  | 219 | Yes |  | CB | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 42 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B401-LINE | 89A | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 43 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B401-LINE | 89A | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 44 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89AE | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL2;CSWI3 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 45 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89AE | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL2;CSWI3 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 46 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89AE2 | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL2;CSWI4 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 47 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89AE2 | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL2;CSWI4 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 48 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B401-LINE | 89B | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 49 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B401-LINE | 89B | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 50 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89BE | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL2;CSWI1 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 51 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89BE | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL2;CSWI1 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 52 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B401-LINE | 89L | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 53 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B401-LINE | 89L | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 54 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89LE | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL2;CSWI2 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 55 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B401-LINE | 89LE | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL2;CSWI2 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 56 |  | DP_HLA_On_Off | DPS | 400kV | B401-LINE | AR FUNCTION | ON/OFF STATUS |  | On | OF_ON_AR STATUS | Transmitted to IEC | [7 empty] | CONTROL1;RREC1 | ST;Ena;origin;DPC |  | 217; | None |  |  | 61 | 6 |  |  |  | ARFct | AR_OnOff_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 57 |  | DP_HLA_On_Off | DPS | 400kV | B401-LINE | AR FUNCTION | ON/OFF STATUS | Off |  | OF_ON_AR STATUS | Transmitted to IEC | [7 empty] | CONTROL1;RREC1 | ST;Ena;origin;DPC |  | 217; | None |  |  | 61 | 6 |  |  |  | ARFct | AR_OnOff_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 58 |  | DP_HLa_LocRem_Bay | DPS | 400kV | B401-LINE |  | BCU MODE |  | Local | LC_RM_BCU MODE | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | ST;Loc;origin;DPC |  |  | None |  |  | 62 | [5 empty] | LocRemBay |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 59 |  | DP_HLa_LocRem_Bay | DPS | 400kV | B401-LINE |  | BCU MODE | Remote |  | LC_RM_BCU MODE | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | ST;Loc;origin;DPC |  |  | None |  |  | 62 | [5 empty] | LocRemBay |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 60 |  | DP_HLa_LocRem_Bay | DPS |  |  |  | Local/remote DPS |  | Local | Local/remote DPS | [8 empty] | CONTROL1;GGSS1 | ST;LocSubst;origin;DPC |  |  | None |  |  | 181 | [5 empty] | LocRemSubstation |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 61 |  | DP_HLa_LocRem_Bay | DPS |  |  |  | Local/remote DPS | Remote |  | Local/remote DPS | [8 empty] | CONTROL1;GGSS1 | ST;LocSubst;origin;DPC |  |  | None |  |  | 181 | [5 empty] | LocRemSubstation |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 62 |  | MP_HLA_AR_Fault | MPS | 400kV | B401-LINE | AR FUNCTION | AUTORECLOSER FAULT STATUS |  |  | AUTORECLOSER FLT | Transmitted to IEC | [7 empty] | CONTROL1;RREC1 | ST;ARFlt;stVal;INS |  |  | None | [7 empty] | ARFct | AR_FaultReason_MPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 63 |  | MP_HLA_AR_Status | MPS | 400kV | B401-LINE | AR FUNCTION | AUTORECLOSER STATUS |  |  | AUTORECLOSER ST | Transmitted to IEC | [7 empty] | CONTROL1;RREC1 | ST;ARSt;stVal;INS |  | 217; | None | [7 empty] | ARFct | AR_Status_MPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 64 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SC_DE_Off_On | SPC | 400kV | B401-LINE | SYNCH FUNCTION | ON/OFF SECONDARY CONTROL SPC | On | Off | OF_ON_ON/OFF SEC | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | CO;EnaSec;ctlVal;DPC | [5 empty] | 191 |  |  |  |  | IntManualCSFct | CS_CtrlOnOff_SPC |  |  | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | DC_DE_AROff_AROn_1 | DPC | 400kV | B401-LINE | AR FUNCTION | OFF |  | Off | OF_ON_A/R OFF | Transmitted to IEC | [7 empty] | CONTROL1;RREC1 | CO;Ena;ctlVal;DPC | [5 empty] | 61 |  |  |  |  | ARFct | AR_CtrlOnOff_DPC |  |  | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | DC_DE_AROff_AROn_1 | DPC | 400kV | B401-LINE | AR FUNCTION | OFF | On |  | OF_ON_A/R OFF | Transmitted to IEC | [7 empty] | CONTROL1;RREC1 | CO;Ena;ctlVal;DPC | [5 empty] | 61 |  |  |  |  | ARFct | AR_CtrlOnOff_DPC |  |  | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | DC_DE_LocRem_BayCtrl | DPC | 400kV | B401-LINE |  | BCU MODE |  | Local | LC_RM_BCU MODE | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | CO;Loc;ctlVal;DPC | [5 empty] | 62 | [5 empty] | LocRemBay_DPC |  |  | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | DC_DE_LocRem_BayCtrl | DPC | 400kV | B401-LINE |  | BCU MODE | Remote |  | LC_RM_BCU MODE | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | CO;Loc;ctlVal;DPC | [5 empty] | 62 | [5 empty] | LocRemBay_DPC |  |  | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | DC_DE_LocRem_BayCtrl_1 | DPC |  |  |  | Local/remote control DPC |  | Local | Loc/rem ctrl DPC | [8 empty] | CONTROL1;GGSS1 | CO;LocSubst;ctlVal;DPC | [5 empty] | 181 | [5 empty] | LocRemSubstation_DPC |  |  | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | DC_DE_LocRem_BayCtrl_1 | DPC |  |  |  | Local/remote control DPC | Remote |  | Loc/rem ctrl DPC | [8 empty] | CONTROL1;GGSS1 | CO;LocSubst;ctlVal;DPC | [5 empty] | 181 | [5 empty] | LocRemSubstation_DPC |  |  | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | MV_HLa_Unused |  | 400kV | B401-LINE | CB_COUNTER | Count_Close | 0.0 | 10000.0 | Count_Close | Transmitted to IEC | [7 empty] | CONTROL2;GAPC1 | MX;AnIn5;mag;MV | [10 empty] | UsrFct | UserFunctionMV |  |  | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | MV_HLa_Unused |  | 400kV | B401-LINE | CB_COUNTER | Count_Open | 0.0 | 10000.0 | Count_Open | Transmitted to IEC | [7 empty] | CONTROL2;GAPC1 | MX;AnIn4;mag;MV | [10 empty] | UsrFct | UserFunctionMV |  |  | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | MV_HLa_Unused |  | 400kV | B401-LINE | SURGE COUNTER | Count_BPH | 0.0 | 10000.0 | Count_BPH | [8 empty] | CONTROL2;GAPC1 | MX;AnIn3;mag;MV | [10 empty] | UsrFct | UserFunctionMV |  |  | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | MV_HLa_Unused |  | 400kV | B401-LINE | SURGE COUNTER | Count_RPH | 0.0 | 10000.0 | Count_RPH | [8 empty] | CONTROL2;GAPC1 | MX;AnIn2;mag;MV | [10 empty] | UsrFct | UserFunctionMV |  |  | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | MV_HLa_Unused |  | 400kV | B401-LINE | SURGE COUNTER | Count_YPH | 0.0 | 10000.0 | Count_YPH | [8 empty] | CONTROL2;GAPC1 | MX;AnIn1;mag;MV | [10 empty] | UsrFct | UserFunctionMV |  |  | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on AC199: HMI Display : Specify if the data appears in HMI.
Note on AD199: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE199: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC322: HMI Display : Specify if the data appears in HMI.
Note on AD322: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE322: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB342: LCD Display : Specify if the data appears in computer LCD.
Note on AC342: HMI Display : Specify if the data appears in HMI.
Note on AD342: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE342: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## BCU B402_TIE
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
MiCOM C264 DESCRIPTION
Keys :
|  |  | Computer Name |  | B402_TIE |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | C264 |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 0
|  |  | Digital Inputs Board Slot |  | P
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | P | 1 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 2 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 3 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 4 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 5 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 6 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 7 | SPE_HLA_Reset_Optd | SPS | 400kV | B402-TIE | 52 | GEN SF6 LOCKOUT | Operated | Reset | RS_OP_SF6 L/O | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind8;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 8 | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | 52 | POLE DISCREPANCY | Alarm | Normal | RS_OP_POLE DISC | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind12;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 9 | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | 52 | LOSS OF SF6 GAS POLE A/B/C-1 | Alarm | Normal | NL_AL_LOSS SF6-1 | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind11;stVal;SPS |  | 240; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 10 | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | 52 | LOSS OF SF6-2 | Alarm | Normal | NL_AL_LOSS SF6-2 | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind13;stVal;SPS |  | 240; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 11 | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | 52 | SF6 LO PRESSURE LOCKOUT | Alarm | Normal | NO_LO_SF6 LO LOW | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind9;stVal;SPS |  | 235; | None |  |  |  |  | 236 |  |  | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 12 | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | 52 | POLE DISCREPANCY | Alarm | Normal | NL_AL_POLE DIS | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind1;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 13 | SPE_HLA_Normal_Fail | SPS | 400kV | B402-TIE | 52 | DC SUPPLY-1\2 | Fail | Normal | NL_FL_DC SUP12 | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind14;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 14 | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | 52 | REMOTE POS | Set | Reset | RS_ST_REMOTE | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind10;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 15 | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | 52 | SPRING CHARGE STATUS B | Alarm | Normal | DS_CH_SPING ST A | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind4;stVal;SPS |  | 225; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 16 | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | 52 | SPRING CHARGE STATUS A | Alarm | Normal | DS_CH_SPING ST B | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind3;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 1
|  |  | Digital Inputs Board Slot |  | O
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | O | 1 | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | 52 | SPRING CHARGE STATUS C | Alarm | Normal | DS_CH_SPING ST C | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind5;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 2 | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | 52 | NL_AL_TROUBLE | Alarm | Normal | NL_AL_TROUBLE1 | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind2;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 3 | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | 52 | NL_AL_TROUBLE | Alarm | Normal | NL_AL_TROUBLE2 | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind6;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 4 | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | 52 | NL_AL_TROUBLE | Alarm | Normal | NL_AL_TROUBLE3 | Transmitted to IEC | [7 empty] | CONTROL2;XCBR1 | ST;Ind7;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 5 | DP_HLa_ESOpen_Close | DPS | 400kV | B402-TIE | 89A | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI1 | ST;Pos;stVal;DPC |  | 229;233; | None |  |  | 64 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 6 | DP_HLa_ESOpen_Close | DPS | 400kV | B402-TIE | 89A | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI1 | ST;Pos;stVal;DPC |  | 229;233; | None |  |  | 64 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 7 | DP_HLa_ESOpen_Close | DPS | 400kV | B402-TIE | 89AE | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI2 | ST;Pos;stVal;DPC |  | 226;227;228;230;231;232; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 8 | DP_HLa_ESOpen_Close | DPS | 400kV | B402-TIE | 89AE | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI2 | ST;Pos;stVal;DPC |  | 226;227;228;230;231;232; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 9 | DP_HLa_ESOpen_Close | DPS | 400kV | B402-TIE | 89B | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI2 | ST;Pos;stVal;DPC |  | 229;233; | None |  |  | 65 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 10 | DP_HLa_ESOpen_Close | DPS | 400kV | B402-TIE | 89B | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI2 | ST;Pos;stVal;DPC |  | 229;233; | None |  |  | 65 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 11 | DP_HLa_ESOpen_Close | DPS | 400kV | B402-TIE | 89BE | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI1 | ST;Pos;stVal;DPC |  | 226;227;228;230;231;232;254;255;256; | None | [5 empty] | Yes |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 12 | DP_HLa_ESOpen_Close | DPS | 400kV | B402-TIE | 89BE | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI1 | ST;Pos;stVal;DPC |  | 226;227;228;230;231;232;254;255;256; | None | [5 empty] | Yes |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 13 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 14 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 15 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 16 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 2
|  |  | Digital Inputs Board Slot |  | N
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | N | 1 | SPE_HLA_Normal_Fail | SPS | 400kV | B402-TIE | PROTECTION | DC SOURCE-1 | Fail | Normal | NL_FL_DC SOURCE1 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind1;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 2 | SPE_HLA_Normal_Fail | SPS | 400kV | B402-TIE | PROTECTION | DC SOURCE-2 | Fail | Normal | NL_FL_DC SOURCE2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind2;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 3 | SPE_HLA_Healthy_Flty | SPS | 400kV | B402-TIE | PROTECTION | CB TRIP COIL-1 | Faulty | Healthy | HL_FT_CB TC1 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind6;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 4 | SPE_HLA_Healthy_Flty | SPS | 400kV | B402-TIE | PROTECTION | CB TRIP COIL-2 | Faulty | Healthy | HL_FT_CB TC2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind3;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 5 | SPE_HLA_Reset_Optd | SPS | 400kV | B402-TIE | PROTECTION | A/R LOCKOUT RELAY | Operated | Reset | RS_OP_86LO | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind4;stVal;SPS |  | 225; | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 6 | SPE_HLA_Reset_Optd | SPS | 400kV | B402-TIE | AR FUNCTION | R-PHASE INITIATION | Operated | Reset | RS_OP_PHR INI | Transmitted to IEC | [7 empty] | CONTROL1;GGIO5 | ST;Ind2;stVal;SPS |  | 235; | None |  |  |  |  | 236 | [6 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 7 | SPE_HLA_Reset_Optd | SPS | 400kV | B402-TIE | AR FUNCTION | Y-PHASE INITIATION | Operated | Reset | RS_OP_PHY INI | Transmitted to IEC | [7 empty] | CONTROL1;GGIO5 | ST;Ind3;stVal;SPS |  | 235; | None |  |  |  |  | 236 | [6 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 8 | SPE_HLA_Reset_Optd | SPS | 400kV | B402-TIE | AR FUNCTION | B-PHASE INITIATION | Operated | Reset | RS_OP_PHB INI | Transmitted to IEC | [7 empty] | CONTROL1;GGIO5 | ST;Ind4;stVal;SPS |  | 235; | None |  |  |  |  | 236 | [6 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 9 | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | AR DATA | PRIORITY CIRCUIT HOLD | Set | Reset | RS_ST_PRI HLD ON | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | ST;Ind1;stVal;SPS |  |  | None |  |  |  |  | 236 | [6 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 10 | SPE_HLA_Reset_Optd | SPS | 400kV | B402-TIE | AR FUNCTION | BLOCK | Operated | Reset | RS_OP_AR BLOCK | Transmitted to IEC | [7 empty] | CONTROL1;GGIO5 | ST;Ind1;stVal;SPS |  |  | None |  |  |  |  | 236 | [6 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 11 | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | B402-TIE | PROTECTION | LBB RELAY | Healthy | Unhealthy | UH_HL_LBB RELAY | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind5;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 12 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 13 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 14 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 15 | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | PROTECTION | AC KIOSK FIRE DETECTED | Alarm | Normal | NL_AL_FIRE DETEC | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind7;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 16 | SPE_HLA_Off_On | SPS | 400kV | B402-TIE | PROTECTION | AC KIOSK COMPRESSOR 1&2 | On | Off | OF_ON_COMPR1&2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind8;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 3
|  |  | Digital Inputs Board Slot |  | M
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | M | 1 | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | CSD | CSD DEVICE NOT READY | Alarm | Normal | NL_AL_CSD NR | Transmitted to IEC | [7 empty] | CONTROL1;GGIO4 | ST;Ind2;stVal;SPS |  | 238; | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 2 | SPE_HLa_In_Out | SPS | 400kV | B402-TIE | CSD | CSD | In | Out | IN_OT_CSD | Transmitted to IEC | [7 empty] | CONTROL1;GGIO4 | ST;Ind1;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 3 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 4 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 5 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 6 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 7 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 8 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 9 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 10 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 11 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 12 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 13 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 14 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 15 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 16 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 4
|  |  | Digital Inputs Board Slot |  | L
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | L | 1 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 2 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 3 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 4 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 5 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 6 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 7 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 8 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 9 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 10 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 11 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 12 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 13 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 14 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 15 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 16 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 0
|  |  | Digital Outputs Board Slot |  | D
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | D | 1 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 2 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 3 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 4 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 5 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 6 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 7 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 8 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 9 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | D | 10 | SC_DE_Reset_Set_1 | SPC | 400kV | B402-TIE | PROTECTION | CB TRIP COIL-2 | Set |  | XX_XX_TC2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO1;ctlVal;DPC | [6 empty] | 208 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 1
|  |  | Digital Outputs Board Slot |  | E
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | E | 1 | DC_SBO_Open_Close | DPC | 400kV | B402-TIE | 52 | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | CO;Pos;sboClass;DPC | [5 empty] | 63 |  | 236 | NO |  | CB | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 2 | DC_SBO_Open_Close | DPC | 400kV | B402-TIE | 52 | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | CO;Pos;sboClass;DPC | [5 empty] | 63 |  | 236 | NO |  | CB | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 3 | SC_DE_Reset_Set | SPC | 400kV | B402-TIE | CSD | CSD BYPASS | Set |  | XX_XX_CSD BYPASS | Transmitted to IEC | [7 empty] | CONTROL1;GGIO4 | CO;SPCSO1;ctlVal;DPC | [6 empty] | 349 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 4 | SC_DE_Reset_Set_2 | SPC | 400kV | B402-TIE | VT SELECTION | 400KV BUS-2 SELECT1 | Set |  | XX_XX_BUS2 SL1 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO3 | CO;SPCSO3;ctlVal;DPC | [6 empty] | 355 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 5 | SC_DE_Reset_Set_2 | SPC | 400kV | B402-TIE | VT SELECTION | 400KV BUS-2 SELECT2 | Set |  | XX_XX_BUS2 SL2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO3 | CO;SPCSO4;ctlVal;DPC | [6 empty] | 353 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 6 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 7 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 8 | SC_DE_Reset_Set_2 | SPC | 400kV | B402-TIE | AR DATA | TO DR | Set |  | XX_XX_TO DR | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | CO;SPCSO3;ctlVal;DPC | [6 empty] | 347 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 9 | SC_DE_Reset_Set | SPC | 400kV | B402-TIE | PROTECTION | DT SEND CHANNEL-1 LINE | Set |  | XX_XX_DT SND CH1 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO2;ctlVal;DPC | [6 empty] | 226 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 10 | SC_DE_Reset_Set | SPC | 400kV | B402-TIE | PROTECTION | DT SEND CHANNEL-2 LINE | Set |  | XX_XX_DT SND CH2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO4;ctlVal;DPC | [6 empty] | 225 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 2
|  |  | Digital Outputs Board Slot |  | F
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | F | 1 | SC_DE_Reset_Set_1 | SPC | 400kV | B402-TIE | VT SELECTION | 400KV BUS-2 SELECT1 FOR PSD | Set |  | XX_XX_BUS2 SL1 P | Transmitted to IEC | [7 empty] | CONTROL1;GGIO3 | CO;SPCSO5;ctlVal;DPC | [6 empty] | 354 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 2 | SC_DE_Reset_Set_1 | SPC | 400kV | B402-TIE | VT SELECTION | 400KV BUS-2 SELECT-2 FOR PSD | Set |  | XX_XX_BUS2 SL2 P | Transmitted to IEC | [7 empty] | CONTROL1;GGIO3 | CO;SPCSO6;ctlVal;DPC | [6 empty] | 352 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 3 | DC_SBO_Open_Close | DPC | 400kV | B402-TIE | 89A | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | CO;Pos;sboClass;DPC | [5 empty] | 64 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 4 | DC_SBO_Open_Close | DPC | 400kV | B402-TIE | 89A | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | CO;Pos;sboClass;DPC | [5 empty] | 64 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 5 | SC_DE_NotPerm_Perm | SPC | 400kV | B402-TIE | IL PERMISSIVE | 89A I/L PERMISSIVE |  |  | XX_XX_89A | Transmitted to IEC | [7 empty] | CONTROL1;GGIO2 | CO;SPCSO1;ctlVal;DPC | [6 empty] | 342 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 6 | SC_DE_NotPerm_Perm | SPC | 400kV | B402-TIE | IL PERMISSIVE | 89AE I/L PERMISSIVE |  |  | XX_XX_89AE | Transmitted to IEC | [7 empty] | CONTROL1;GGIO2 | CO;SPCSO3;ctlVal;DPC | [6 empty] | 343 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 7 | DC_SBO_Open_Close | DPC | 400kV | B402-TIE | 89B | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | CO;Pos;sboClass;DPC | [5 empty] | 65 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 8 | DC_SBO_Open_Close | DPC | 400kV | B402-TIE | 89B | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | CO;Pos;sboClass;DPC | [5 empty] | 65 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 9 | SC_DE_NotPerm_Perm | SPC | 400kV | B402-TIE | IL PERMISSIVE | 89B I/L PERMISSIVE |  |  | XX_XX_89B | Transmitted to IEC | [7 empty] | CONTROL1;GGIO2 | CO;SPCSO2;ctlVal;DPC | [6 empty] | 344 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 10 | SC_DE_NotPerm_Perm | SPC | 400kV | B402-TIE | IL PERMISSIVE | 89BE I/L PERMISSIVE |  |  | XX_XX_89BE | Transmitted to IEC | [7 empty] | CONTROL1;GGIO2 | CO;SPCSO4;ctlVal;DPC | [6 empty] | 345 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 3
|  |  | Digital Outputs Board Slot |  | G
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | G | 1 | SC_DE_NotPerm_Perm_1 | SPC | 400kV | B402-TIE | PROTECTION | 86LO TRIP RELAY |  |  | XX_RS_86LO | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO3;ctlVal;DPC | [8 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 2 | SC_DE_Reset_Set_2 | SPC | 400kV | B402-TIE | AR DATA | LOCKOUT TRIP | Set |  | XX_XX_AR LO TRIP | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | CO;SPCSO2;ctlVal;DPC | [6 empty] | 346 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 3 | SC_DE_Off_On_2 | SPC | 400kV | B402-TIE | AR DATA | A/R OFF | On | Off | XX_XX_A/R_OFF | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | CO;SPCSO1;ctlVal;DPC | [6 empty] | 7 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 4 | SC_DE_Reset_Reset | SPC | 400kV | B402-TIE | AR DATA | TO A/R CLSG. CKT | Reset |  | XX_XX_A/R CLSG C | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | CO;SPCSO4;ctlVal;DPC | [6 empty] | 348 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 5 | SC_DE_Reset_Set_1 | SPC | 400kV | B402-TIE | PROTECTION | CLS CMD TO SOTF M1 | Set |  | XX_XX_SOTF M1 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO6;ctlVal;DPC | [6 empty] | 224 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 6 | SC_DE_Reset_Set_1 | SPC | 400kV | B402-TIE | PROTECTION | CLS CMD TO SOTF M2 | Set |  | XX_XX_SOTF M2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO5;ctlVal;DPC | [6 empty] | 223 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 7 | SC_DE_Reset_Set_1 | SPC | 400kV | B402-TIE | VT SELECTION | 400KV LINE SELECT1 | Set |  | XX_XX_LINE SL1 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO3 | CO;SPCSO7;ctlVal;DPC | [8 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 8 | SC_DE_Reset_Set_1 | SPC | 400kV | B402-TIE | VT SELECTION | 400KV LINE SELECT2 | Set |  | XX_XX_LINE SL2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO3 | CO;SPCSO8;ctlVal;DPC | [8 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 9 | SC_DE_Reset_Set_2 | SPC | 400kV | B402-TIE | VT SELECTION | 765KV ICT SELECT1 | Set |  | XX_XX_ICT SL1 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO3 | CO;SPCSO1;ctlVal;DPC | [6 empty] | 350 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 10 | SC_DE_Reset_Set_2 | SPC | 400kV | B402-TIE | VT SELECTION | 765KV ICT SELECT2 | Set |  | XX_XX_ICT SL2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO3 | CO;SPCSO2;ctlVal;DPC | [6 empty] | 351 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
CT/VT ANALOG INPUT BOARD TMU2x0
|  |  | CT/VT Board Number |  | 0
|  |  | CT/VT Board Slot |  | Q
|  |  | CT/VT Board Model |  | TMU220
CT acquisition
VT acquisition
|  |  | Nominal Current |  | 1 | (1A/5A)
|  |  | Nominal Voltage |  | 110 | [1V … 500V]
Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Input type (U/I) |  | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | DF |  | MV_HLa_Frequency_1 | Hz | 400kV | B402-TIE | SYNCH DATA | FREQUENCY DIFFERENCE | 0.0 | 2.0 | FREQUENCY DIFF | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | MX;DifHzClc;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | DV |  | MV_hla_ AuxVoltage_1 | V | 400kV | B402-TIE | SYNCH DATA | VOLTAGE DIFFERENCE | 0.0 | 277.13626 | VOLTAGE DIFF | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | MX;DifVClc;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Dj |  | MV_hla_PhaseDiff | ˚ | 400kV | B402-TIE | SYNCH DATA | PHASE DIFFERENCE | 0.0 | 360.0 | PHASE ANGLE DIFF | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | MX;DifAngClc;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ia |  | MV_HLa_AuxCurrent | A | 400kV | B402-TIE | METERING-TIE_400 | I-R PHASE CURRENT | 0.0 | 2400.0 | IR PHASE CURRENT | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU2 | MX;A;phsA;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ib |  | MV_HLa_AuxCurrent | A | 400kV | B402-TIE | METERING-TIE_400 | I-Y PHASE CURRENT | 0.0 | 2400.0 | IY PHASE CURRENT | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU2 | MX;A;phsB;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ic |  | MV_HLa_AuxCurrent | A | 400kV | B402-TIE | METERING-TIE_400 | I-B PHASE CURRENT | 0.0 | 2400.0 | IB PHASE CURRENT | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU2 | MX;A;phsC;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Vb |  | MV_hla_ AuxVoltage_1 | V | 400kV | B402-TIE | SYNCH DATA | INCOMING SUPPLY | 0.0 | 277.13626 | INCOMING SUPPLY | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;PhV;phsB;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Vbusbar |  | MV_hla_ AuxVoltage_1 | V | 400kV | B402-TIE | SYNCH DATA | RUNNING SUPPLY | 0.0 | 277.13626 | RUNNING SPLY-1 | Transmitted to IEC | [7 empty] | MEASUREMENT1;barMMXU1 | MX;PhV;phsA;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Freq (Line) |  | MV_HLa_Frequency | Hz | 400kV | B402-TIE | METERING-TIE_400 | FREQUENCY | 45.0 | 55.0 | FREQUENCY | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU2 | MX;Hz;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | cos ft : Power factor |  | MV_HLa_PowerFactor |  | 400kV | B402-TIE | METERING-TIE_400 | POWER FACTOR | -1.2 | 1.2 | POWER FACTOR | Transmitted to IEC | [7 empty] | MEASUREMENT1;powMMXU1 | MX;TotPF;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  |  |  | SPARE | [32 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  |  |  | SPARE | [32 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  |  |  | SPARE | [32 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  |  |  | SPARE | [32 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  |  |  | SPARE | [32 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  |  |  | SPARE | [32 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  |  |  | SPARE | [32 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | 52 ¦ OE_CL_CONTROL | OPEN ORDER | Set | Reset | RS_ST_OPN ORD | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | ST;OpnOrd;general;general;ACT |  | 239; | None |  |  |  | 208 |  |  |  | CB | OpenOrderSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B402-TIE | 89A ¦ OE_CL_CONTROL | OPEN INTERLOCK | Permissive | Not Permissive | NP_PE_OPN ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO1 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | SG | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B402-TIE | 89B ¦ OE_CL_CONTROL | OPEN INTERLOCK | Permissive | Not Permissive | NP_PE_OPN ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO2 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | SG | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPS_hla_Set_Reset | SPS | 400kV | B402-TIE |  | ORDER RUNNING ON THE BAY | Set | Reset | RS_ST_ORD RUNING | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | ST;OrdRun;stVal;SPS |  |  | None | [8 empty] | OrderInProgress |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B402-TIE | 52 ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | NP_PE_CLOSE ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO3 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | CB | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B402-TIE | 89A ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | NP_PE_CLS ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO1 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | SG | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B402-TIE | 89B ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | NP_PE_CLS ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO2 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | SG | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | SYNCH FUNCTION | CLOSE ORDER | Set | Reset | RS_ST_CLS ODR | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;ClsOpSt;stVal;SPS |  |  | None | [7 empty] | IntManualCSFct | CS_CloseOrderState_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPE_HLA_on_off | SPS | 400kV | B402-TIE | SYNCH FUNCTION | ON/OFF SECONDARY SPS | Off | On | RS_ST_ON/OFF SEC | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;EnaSec;origin;SPC |  |  | None |  |  | 193 |  |  |  |  | IntManualCSFct | CS_OnOff_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | SYNCH FUNCTION | POSSIBLE CLOSING | Set | Reset | RS_ST_POS CLS | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;Rel;stVal;SPS |  | 241; | None | [7 empty] | IntManualCSFct | CS_AuthoState_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | SYNCH FUNCTION | PRESENCE OF REFERENCE VOLTAGE | Set | Reset | RS_ST_REF U PRES | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;VRefInd;stVal;SPS |  | 241; | None | [7 empty] | IntManualCSFct | CS_VoltageRefPresence_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | SYNCH FUNCTION | ABSENCE OF REFERENCE VOLTAGE | Set | Reset | RS_ST_REF. U ABS | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;VRefAbs;stVal;SPS |  | 241; | None | [7 empty] | IntManualCSFct | CS_VoltageRefAbsence_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | SYNCH FUNCTION | RS_ST_V CHOICE | Set | Reset | RS_ST_V CHOICE | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;BusVC;stVal;SPS |  | 242<; | None | [7 empty] | IntManualCSFct | CS_BusBarVChoice_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | SYNCH FUNCTION | VOLT ABSENCE | Set | Reset | RS_ST_VOLT ABS | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;VAbs;stVal;SPS |  | 241; | None | [7 empty] | IntManualCSFct | CS_VoltageAbsence_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | SYNCH FUNCTION | VOLT PRESENCE | Set | Reset | RS_ST_VOLT PRES | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;VP;stVal;SPS |  | 241; | None | [7 empty] | IntManualCSFct | CS_VoltagePresence_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B402-TIE | 52 ¦ OE_CL_CONTROL | CLOSE ORDER | Permissive | Not Permissive | RS_ST_CLS ORD | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | ST;ClsOrd;general;general;ACT |  | 234; | None |  |  |  | 223;224;225;226 |  |  |  | CB | CloseOrderSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 17 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | AR DATA | LOCK | Set | Reset | RS_ST_S10_LOCK | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | ST;IndSys1;stVal;SPS |  | 235; | None | [8 empty] | MappingSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 18 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | AR DATA | WAIT FOR CB CLOSE | Set | Reset | RS_ST_S7_WT CB C | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | ST;IndSys3;stVal;SPS |  | 234; | None | [8 empty] | MappingSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 19 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | AR DATA | LOCK_SHOTS | Set | Reset | RS_ST_S9_LO SHTS | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | ST;IndSys2;stVal;SPS |  | 235; | None | [8 empty] | MappingSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 20 |  | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | 52 | LOSS OF SF6 GAS POLE A/B/C | Alarm | Normal | NL_AL_LOSS SF6 | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | ST;IndSys1;stVal;SPS |  | 240<; | None | [7 empty] | CB |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 21 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B402-TIE | 89A | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | ST;IndSys1;stVal;SPS |  | 226<; | None |  |  |  | 342 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 22 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B402-TIE | 89AE | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL2;CSWI2 | ST;IndSys1;stVal;SPS |  | 229<; | None |  |  |  | 343 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 23 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B402-TIE | 89B | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | ST;IndSys1;stVal;SPS |  | 230<; | None |  |  |  | 344 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 24 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B402-TIE | 89BE | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL2;CSWI1 | ST;IndSys1;stVal;SPS |  | 233<; | None |  |  |  | 345 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 25 |  | SPE_HLA_Reset_Optd | SPS | 400kV | B402-TIE | AR DATA | LOCKOUT FROM AR LOGIC | Operated | Reset | RS_OP_AR LO FBD | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | ST;IndSys4;stVal;SPS |  | 235<; | None |  |  |  | 346 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 26 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | AR DATA | AR LOCK | Set | Reset | RS_ST_AR LOCK IS | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | ST;SPCSO1;origin;SPC |  |  | None |  |  | 192 |  | 236 | [6 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 27 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | AR DATA | A/R OPTD FROM FBD | Set | Reset | RS_ST_AR OPTD FB | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | ST;IndSys5;stVal;SPS |  | 234<; | None |  |  |  | 347;348 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 28 |  | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | CSD | RPH-1 | Alarm | Normal | NL_AL_RPH1 | Transmitted to IEC | [7 empty] | CONTROL1;GAPC4 | ST;IndSys1;stVal;SPS |  |  | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 29 |  | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | CSD | RPH-2 | Alarm | Normal | NL_AL_RPH2 | Transmitted to IEC | [7 empty] | CONTROL1;GAPC4 | ST;IndSys2;stVal;SPS |  |  | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 30 |  | SPE_HLA_Normal_Alarm | SPS | 400kV | B402-TIE | CSD | RPH-3 | Alarm | Normal | NL_AL_RPH3 | Transmitted to IEC | [7 empty] | CONTROL1;GAPC4 | ST;IndSys3;stVal;SPS |  |  | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 31 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | CSD | CSD BYPASS | Set | Reset | RS_ST_CSD BYPASS | Transmitted to IEC | [7 empty] | CONTROL1;GAPC4 | ST;IndSys4;stVal;SPS |  | 238<; | None |  |  |  | 349 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 32 |  | SPE_HLa_Reset_Select | SPS | 400kV | B402-TIE | INTER TRIPPING | TO HV ICT 706-52 OPEN ORDER | Selected | Reset | TO HV ICT 706-52 | Transmitted to IEC | [7 empty] | CONTROL1;GAPC5 | ST;IndSys1;stVal;SPS |  | 239<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 33 |  | SPE_HLa_Reset_Select | SPS | 400kV | B402-TIE | INTER TRIPPING | TO HV TIE 705-52 OPEN ORDER | Selected | Reset | TO HV TIE 705-52 | Transmitted to IEC | [7 empty] | CONTROL1;GAPC5 | ST;IndSys2;stVal;SPS |  | 239<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 34 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | SYNCH DATA | CLOSE PERMISSIVE | Set | Reset | RS_ST_CB CLOSE | Transmitted to IEC | [7 empty] | CONTROL1;GAPC2 | ST;IndSys5;stVal;SPS |  | 241<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 35 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | SYNCH DATA | DEAD INCOMING DEAD RUNNING | Set | Reset | RS_ST_DINC_DRUN | Transmitted to IEC | [7 empty] | CONTROL1;GAPC2 | ST;IndSys4;stVal;SPS |  | 241<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 36 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | SYNCH DATA | DEAD INCOMING LIVE RUNNING | Set | Reset | RS_ST_DINC_LRUN | Transmitted to IEC | [7 empty] | CONTROL1;GAPC2 | ST;IndSys3;stVal;SPS |  | 241<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 37 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | SYNCH DATA | LIVE INCOMING DEAD RUNNING | Set | Reset | RS_ST_LINC_DRUN | Transmitted to IEC | [7 empty] | CONTROL1;GAPC2 | ST;IndSys2;stVal;SPS |  | 241<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 38 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | SYNCH DATA | LIVE INCOMING LIVE RUNNING | Set | Reset | RS_ST_LINC_LRUN | Transmitted to IEC | [7 empty] | CONTROL1;GAPC2 | ST;IndSys1;stVal;SPS |  | 241<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 39 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | VT SELECTION | 765KV HV SELECT | Set | Reset | RS_ST_765KV HV | Transmitted to IEC | [7 empty] | CONTROL1;GAPC3 | ST;IndSys3;stVal;SPS |  | 244<; | None |  |  |  | 350;351 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 40 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | VT SELECTION | BUS1 SELECT | Set | Reset | RS_ST_BUS1 | Transmitted to IEC | [7 empty] | CONTROL1;GAPC3 | ST;IndSys1;stVal;SPS |  | 244<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 41 |  | SPE_HLa_Reset_Set | SPS | 400kV | B402-TIE | VT SELECTION | BUS2 SELECT | Set | Reset | RS_ST_BUS2 | Transmitted to IEC | [7 empty] | CONTROL1;GAPC3 | ST;IndSys2;stVal;SPS |  |  | None |  |  |  | 352;353;354;355 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 42 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B402-TIE | 52 | POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | ST;Pos;stVal;DPC |  | 211;212;213;226;227;228;230;231;232;254;255;256; | None |  |  | 63 |  | 236;237 | Yes |  | CB | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 43 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B402-TIE | 52 | POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | ST;Pos;stVal;DPC |  | 211;212;213;226;227;228;230;231;232;254;255;256; | None |  |  | 63 |  | 236;237 | Yes |  | CB | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 44 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B402-TIE | 89A | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 45 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B402-TIE | 89A | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 46 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B402-TIE | 89AE | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL2;CSWI2 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 47 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B402-TIE | 89AE | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL2;CSWI2 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 48 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B402-TIE | 89B | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 49 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B402-TIE | 89B | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 50 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B402-TIE | 89BE | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL2;CSWI1 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 51 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B402-TIE | 89BE | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL2;CSWI1 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 52 |  | DP_HLA_On_Off | DPS | 400kV | B402-TIE | AR FUNCTION | ON/OFF STATUS |  | On | OF_ON_AR STATUS | Transmitted to IEC | [7 empty] | CONTROL1;GAPC6 | ST;DPCSO1;stVal;DPC |  | 235; | None |  |  | 66 | 7 | 236 | [6 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 53 |  | DP_HLA_On_Off | DPS | 400kV | B402-TIE | AR FUNCTION | ON/OFF STATUS | Off |  | OF_ON_AR STATUS | Transmitted to IEC | [7 empty] | CONTROL1;GAPC6 | ST;DPCSO1;stVal;DPC |  | 235; | None |  |  | 66 | 7 | 236 | [6 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 54 |  | DP_HLa_LocRem_Bay | DPS | 400kV | B402-TIE |  | BCU MODE |  | Local | LC_RM_BCU MODE | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | ST;Loc;origin;DPC |  |  | None |  |  | 67 | [5 empty] | LocRemBay |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 55 |  | DP_HLa_LocRem_Bay | DPS | 400kV | B402-TIE |  | BCU MODE | Remote |  | LC_RM_BCU MODE | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | ST;Loc;origin;DPC |  |  | None |  |  | 67 | [5 empty] | LocRemBay |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 56 |  | MP_HLA_AR_Fault | MPS | 400kV | B402-TIE | AR_1PH_1SHOT_ISA | AUTORECLOSER FAULT STATUS |  |  | AUTORECLOSER FLT | Transmitted to IEC | [7 empty] | CONTROL2;GAPC2 | ST;IntSys2;stVal;INS |  |  | None | [7 empty] | UsrFct | UserFunctionMPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 57 |  | MP_HLA_AR_Status | MPS | 400kV | B402-TIE | AR_1PH_1SHOT_ISA | AUTORECLOSER STATUS |  |  | AUTORECLOSER ST | Transmitted to IEC | [7 empty] | CONTROL2;GAPC2 | ST;IntSys1;stVal;INS |  |  | None | [7 empty] | UsrFct | UserFunctionMPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 58 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SC_DE_Reset_Set_Int_1 | SPC | 400kV | B402-TIE | AR DATA | A/R LOCK | Set |  | UL_LO_AR | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | CO;SPCSO1;ctlVal;DPC | [5 empty] | 192 |  | 236 | [6 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SC_DE_Reset_Set | SPC | 400kV | B402-TIE | CSD | CSD OUT FROM HMI | Set |  | XX_ST_CSD OUT H | Transmitted to IEC | [7 empty] | CONTROL1;GAPC4 | CO;SPCSO1;ctlVal;DPC |  | 238; | [12 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SC_DE_Off_On | SPC | 400kV | B402-TIE | SYNCH FUNCTION | ON/OFF SECONDARY CONTROL SPC | On | Off | OF_ON_ON/OFF SEC | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | CO;EnaSec;ctlVal;DPC | [5 empty] | 193 |  |  |  |  | IntManualCSFct | CS_CtrlOnOff_SPC |  |  | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | DC_DE_AROff_AROn | DPC | 400kV | B402-TIE | AR FUNCTION | OFF |  | Off | OF_ON_A/R OFF | Transmitted to IEC | [7 empty] | CONTROL1;GAPC6 | CO;DPCSO1;ctlVal;DPC | [5 empty] | 66 | [8 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | DC_DE_AROff_AROn | DPC | 400kV | B402-TIE | AR FUNCTION | OFF | On |  | OF_ON_A/R OFF | Transmitted to IEC | [7 empty] | CONTROL1;GAPC6 | CO;DPCSO1;ctlVal;DPC | [5 empty] | 66 | [8 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | DC_DE_LocRem_BayCtrl | DPC | 400kV | B402-TIE |  | BCU MODE |  | Local | LC_RM_BCU MODE | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | CO;Loc;ctlVal;DPC | [5 empty] | 67 | [5 empty] | LocRemBay_DPC |  |  | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | DC_DE_LocRem_BayCtrl | DPC | 400kV | B402-TIE |  | BCU MODE | Remote |  | LC_RM_BCU MODE | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | CO;Loc;ctlVal;DPC | [5 empty] | 67 | [5 empty] | LocRemBay_DPC |  |  | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | MV_HLa_Unused |  | 400kV | B402-TIE | CB_COUNTER | Count_Close | 0.0 | 10000.0 | Count_Close | Transmitted to IEC | [7 empty] | CONTROL2;GAPC2 | MX;AnIn2;mag;MV | [10 empty] | UsrFct | UserFunctionMV |  |  | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | MV_HLa_Unused |  | 400kV | B402-TIE | CB_COUNTER | Count_Open | 0.0 | 10000.0 | Count_Open | Transmitted to IEC | [7 empty] | CONTROL2;GAPC2 | MX;AnIn1;mag;MV | [10 empty] | UsrFct | UserFunctionMV |  |  | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on AC199: HMI Display : Specify if the data appears in HMI.
Note on AD199: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE199: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC316: HMI Display : Specify if the data appears in HMI.
Note on AD316: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE316: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB336: LCD Display : Specify if the data appears in computer LCD.
Note on AC336: HMI Display : Specify if the data appears in HMI.
Note on AD336: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE336: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## BCU B409_ICT1
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
MiCOM C264 DESCRIPTION
Keys :
|  |  | Computer Name |  | B409_ICT1 |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | C264 |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 0
|  |  | Digital Inputs Board Slot |  | P
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  | 1 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH MOG LOW OIL LEVEL ALARM | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 2 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH MOG LOW OIL LEVEL ALARM | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 3 | SPARE | SPS | 400kV | B409-ICT-1 |  | BPH MOG LOW OIL LEVEL ALARM | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 4 | SPARE | SPS | 400kV | B409-ICT-1 |  | SP-PH MOG LOW OIL LEVEL ALARM | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 5 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH MOG HIGH OIL LEVEL ALARM | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 6 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH MOG HIGH OIL LEVEL ALARM | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 1 | SPARE | SPS | 400kV | B409-ICT-1 |  | BPH MOG HIGH OIL LEVEL ALARM | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 2 | SPARE | SPS | 400kV | B409-ICT-1 |  | SP-PH MOG HIGH OIL LEVEL ALARM | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 3 | SPARE | SPS | 400kV | B409-ICT-1 |  | R-PH OIL FLOW SENSITIVE VALVE ALARM | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 4 | SPARE | SPS | 400kV | B409-ICT-1 |  | Y-PH OIL FLOW SENSITIVE VALVE ALARM | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 5 | SPARE | SPS | 400kV | B409-ICT-1 |  | B-PH OIL FLOW SENSITIVE VALVE ALARM | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 6 | SPARE | SPS | 400kV | B409-ICT-1 |  | SP-PH OIL FLOW SENSITIVE VALVE ALARM | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 1 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH PUMP FAIL - BANK A | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 2 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH PUMP FAIL - BANK B | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 1 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH PUMP FAIL - BANK C | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 2 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH PUMP FAIL - BANK D | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 3 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH PUMP FAIL - BANK A | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 4 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH PUMP FAIL - BANK B | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 5 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH PUMP FAIL - BANK C | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 6 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH PUMP FAIL - BANK D | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 1 | SPARE | SPS | 400kV | B409-ICT-1 |  | BPH PUMP FAIL - BANK A | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 2 | SPARE | SPS | 400kV | B409-ICT-1 |  | BPH PUMP FAIL - BANK B | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 3 | SPARE | SPS | 400kV | B409-ICT-1 |  | BPH PUMP FAIL - BANK C | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 4 | SPARE | SPS | 400kV | B409-ICT-1 |  | BPH PUMP FAIL - BANK D | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 5 | SPARE | SPS | 400kV | B409-ICT-1 |  | SPH PUMP FAIL - BANK A | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 6 | SPARE | SPS | 400kV | B409-ICT-1 |  | SPH PUMP FAIL - BANK B | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 1 | SPARE | SPS | 400kV | B409-ICT-1 |  | SPH PUMP FAIL - BANK C | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 2 | SPARE | SPS | 400kV | B409-ICT-1 |  | SPH PUMP FAIL - BANK D | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 3 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH THERMAL OVERLOAD TRIP - BANK A | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 4 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH THERMAL OVERLOAD TRIP - BANK B | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 5 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH THERMAL OVERLOAD TRIP - BANK C | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 6 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH THERMAL OVERLOAD TRIP - BANK D | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 1 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH THERMAL OVERLOAD TRIP - BANK A | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 2 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH THERMAL OVERLOAD TRIP - BANK B | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 3 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH THERMAL OVERLOAD TRIP - BANK C | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 4 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH THERMAL OVERLOAD TRIP - BANK D | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 5 | SPARE | SPS | 400kV | B409-ICT-1 |  | BPH THERMAL OVERLOAD TRIP - BANK A | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 6 | SPARE | SPS | 400kV | B409-ICT-1 |  | BPH THERMAL OVERLOAD TRIP - BANK B | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 1 | SPARE | SPS | 400kV | B409-ICT-1 |  | BPH THERMAL OVERLOAD TRIP - BANK C | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 2 | SPARE | SPS | 400kV | B409-ICT-1 |  | BPH THERMAL OVERLOAD TRIP - BANK D | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 3 | SPARE | SPS | 400kV | B409-ICT-1 |  | SPH THERMAL OVERLOAD TRIP - BANK A | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 4 | SPARE | SPS | 400kV | B409-ICT-1 |  | SPH THERMAL OVERLOAD TRIP - BANK B | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 5 | SPARE | SPS | 400kV | B409-ICT-1 |  | SPH THERMAL OVERLOAD TRIP - BANK C | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 6 | SPARE | SPS | 400kV | B409-ICT-1 |  | SPH THERMAL OVERLOAD TRIP - BANK D | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 1 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH LOW OIL FLOW/REVERSE FLOW - BANK A | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 2 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH LOW OIL FLOW/REVERSE FLOW - BANK B | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 3 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH LOW OIL FLOW/REVERSE FLOW - BANK C | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 4 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH LOW OIL FLOW/REVERSE FLOW - BANK D | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 5 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH LOW OIL FLOW/REVERSE FLOW - BANK A | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 6 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH LOW OIL FLOW/REVERSE FLOW - BANK B | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 1 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH LOW OIL FLOW/REVERSE FLOW - BANK C | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 2 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH LOW OIL FLOW/REVERSE FLOW - BANK D | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 1 | SPARE | SPS | 400kV | B409-ICT-1 |  | BPH LOW OIL FLOW/REVERSE FLOW - BANK A | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 2 | SPARE | SPS | 400kV | B409-ICT-1 |  | BPH LOW OIL FLOW/REVERSE FLOW - BANK B | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 3 | SPARE | SPS | 400kV | B409-ICT-1 |  | BPH LOW OIL FLOW/REVERSE FLOW - BANK C | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 4 | SPARE | SPS | 400kV | B409-ICT-1 |  | BPH LOW OIL FLOW/REVERSE FLOW - BANK D | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 5 | SPARE | SPS | 400kV | B409-ICT-1 |  | SPH LOW OIL FLOW/REVERSE FLOW - BANK A | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 6 | SPARE | SPS | 400kV | B409-ICT-1 |  | SPH LOW OIL FLOW/REVERSE FLOW - BANK B | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 1 | SPARE | SPS | 400kV | B409-ICT-1 |  | SPH LOW OIL FLOW/REVERSE FLOW - BANK C | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 2 | SPARE | SPS | 400kV | B409-ICT-1 |  | SPH LOW OIL FLOW/REVERSE FLOW - BANK D | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 3 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH COOLER CONTROL SUPPLY FAIL | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 4 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH COOLER CONTROL SUPPLY FAIL | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 5 | SPARE | SPS | 400kV | B409-ICT-1 |  | BPH COOLER CONTROL SUPPLY FAIL | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 6 | SPARE | SPS | 400kV | B409-ICT-1 |  | SPH COOLER CONTROL SUPPLY FAIL | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 1 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH SUPPLY CHANGE OVER FAIL | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 2 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH SUPPLY CHANGE OVER FAIL | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
[6 empty] | SPS | 400kV | B409-ICT-1 |  | BPH SUPPLY CHANGE OVER FAIL
[6 empty] | SPS | 400kV | B409-ICT-1 |  | SPH SUPPLY CHANGE OVER FAIL
[6 empty] | SPS | 400kV | B409-ICT-1 |  | RPH SUPPLY - A FAIL
[6 empty] | SPS | 400kV | B409-ICT-1 |  | YPH SUPPLY - A FAIL
[6 empty] | SPS | 400kV | B409-ICT-1 |  | BPH SUPPLY - A FAIL
[6 empty] | SPS | 400kV | B409-ICT-1 |  | SPH SUPPLY - A FAIL
[6 empty] | SPS | 400kV | B409-ICT-1 |  | RPH SUPPLY - B FAIL
[6 empty] | SPS | 400kV | B409-ICT-1 |  | YPH SUPPLY - B FAIL
[6 empty] | SPS | 400kV | B409-ICT-1 |  | BPH SUPPLY - B FAIL
[6 empty] | SPS | 400kV | B409-ICT-1 |  | SPH SUPPLY - B FAIL
[6 empty] | SPS | 400kV | B409-ICT-1 |  | RPH OLTC MOTOR OVERLOAD
A |  |  |  | 3 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH TAP CHANGE IN PROGRESS | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 4 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH TAP CHANGE IN COMPLETE | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 5 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH OLTC IN LOCAL | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 6 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH OLTC IN REMOTE | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 1 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH TAP CHANGE CONTROL SUPPLY FAIL | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 2 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH LOWEST POSITION REACHDED | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 3 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH HIGHESHT POSITION REACHDED | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 4 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH OLTC RAISE COMMAND | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 5 | SPARE | SPS | 400kV | B409-ICT-1 |  | RPH OLTC LOWER COMMAND | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 6 | SPARE | SPS | 400kV | B409-ICT-1 |  | YPH OLTC MOTOR OVERLOAD | [15 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 7 | SPE_HLA_Reset_Optd | SPS | 400kV | B409-ICT-1 | 52 | YPH TAP CHANGE IN PROGRESS | Operated | Reset | RS_OP_SF6 L/O | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;Ind12;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 8 | SPE_HLA_Normal_Alarm | SPS | 400kV | B409-ICT-1 | 52 | YPH TAP CHANGE IN COMPLETE | Alarm | Normal | RS_OP_POLE DISC | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;Ind8;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 9 | SPE_HLA_Normal_Alarm | SPS | 400kV | B409-ICT-1 | 52 | YPH OLTC IN LOCAL | Alarm | Normal | NL_AL_LOSS SF6-1 | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;Ind9;stVal;SPS |  | 403; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 10 | SPE_HLA_Normal_Alarm | SPS | 400kV | B409-ICT-1 | 52 | YPH OLTC IN REMOTE | Alarm | Normal | NL_AL_LOSS SF6-2 | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;Ind13;stVal;SPS |  | 403; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 11 | SPE_HLA_Normal_Alarm | SPS | 400kV | B409-ICT-1 | 52 | YPH TAP CHANGE CONTROL SUPPLY FAIL | Alarm | Normal | NO_LO_SF6 LO LOW | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;Ind6;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 12 | SPE_HLA_Normal_Alarm | SPS | 400kV | B409-ICT-1 | 52 | YPH LOWEST POSITION REACHDED | Alarm | Normal | NL_AL_POLE DIS | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;Ind7;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 13 | SPE_HLA_Normal_Fail | SPS | 400kV | B409-ICT-1 | 52 | YPH HIGHESHT POSITION REACHDED | Fail | Normal | NL_FL_DC SUP12 | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;Ind1;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 14 | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | 52 | YPH OLTC RAISE COMMAND | Set | Reset | RS_ST_REMOTE | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;Ind2;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 15 | SPE_HLA_Normal_Alarm | SPS | 400kV | B409-ICT-1 | 52 | YPH OLTC LOWER COMMAND | Alarm | Normal | DS_CH_SPING ST A | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;Ind3;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 16 | SPE_HLA_Normal_Alarm | SPS | 400kV | B409-ICT-1 | 52 | BPH OLTC MOTOR OVERLOAD | Alarm | Normal | DS_CH_SPING ST B | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;Ind4;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
BPH TAP CHANGE IN PROGRESS
|  |  | DIGITAL INPUT BOARD DIU2xx | [6 empty] | BPH TAP CHANGE IN COMPLETE
|  |  | Digital Inputs Board Number |  | 1 |  |  |  |  | BPH OLTC IN LOCAL
|  |  | Digital Inputs Board Slot |  | O |  |  |  |  | BPH OLTC IN REMOTE
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | BPH TAP CHANGE CONTROL SUPPLY FAIL | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | BPH LOWEST POSITION REACHDED | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | O | 1 | SPE_HLA_Normal_Alarm | SPS | 400kV | B409-ICT-1 | 52 | BPH HIGHESHT POSITION REACHDED | Alarm | Normal | DS_CH_SPING ST C | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;Ind5;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 2 | SPE_HLA_Normal_Alarm | SPS | 400kV | B409-ICT-1 | 52 | BPH OLTC RAISE COMMAND | Alarm | Normal | NL_AL_CB TROUBL4 | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;Ind11;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 3 | SPE_HLA_Normal_Alarm | SPS | 400kV | B409-ICT-1 | 52 | BPH OLTC LOWER COMMAND | Alarm | Normal | NL_AL_CB TROUB 1 | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;Ind14;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 4 | SPE_HLA_Normal_Alarm | SPS | 400kV | B409-ICT-1 | 52 | SPH OLTC MOTOR OVERLOAD | Alarm | Normal | NL_AL_CB TROUBL3 | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;Ind10;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 5 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89A | SPH TAP CHANGE IN PROGRESS |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI1 | ST;Pos;stVal;DPC |  | 370;374; | None |  |  | 101 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 6 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89A | SPH TAP CHANGE IN COMPLETE | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI1 | ST;Pos;stVal;DPC |  | 370;374; | None |  |  | 101 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 7 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89AE | SPH OLTC IN LOCAL |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL3;XSWI6 | ST;Pos;stVal;DPC |  | 367;368;369;371;372;373; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 8 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89AE | SPH OLTC IN REMOTE | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL3;XSWI6 | ST;Pos;stVal;DPC |  | 367;368;369;371;372;373; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 9 | DP_HLA_CBOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | SPH TAP CHANGE CONTROL SUPPLY FAIL |  | Open | 7_Z_TSR POS | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;DPCSO8;stVal;DPC |  | 398; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 10 | DP_HLA_CBOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | SPH LOWEST POSITION REACHDED | Closed |  | 7_Z_TSR POS | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;DPCSO8;stVal;DPC |  | 398; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 11 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89B | SPH HIGHESHT POSITION REACHDED |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI6 | ST;Pos;stVal;DPC |  | 370;374; | None |  |  | 102 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 12 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89B | SPH OLTC RAISE COMMAND | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI6 | ST;Pos;stVal;DPC |  | 370;374; | None |  |  | 102 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 13 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89BE | SPH OLTC LOWER COMMAND |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL3;XSWI4 | ST;Pos;stVal;DPC |  | 367;368;369;371;372;373; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 14 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89BE | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL3;XSWI4 | ST;Pos;stVal;DPC |  | 367;368;369;371;372;373; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 15 | DP_HLA_CBOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | 7_Z_TE R POS |  | Open | 7_Z_TE R POS | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;DPCSO7;stVal;DPC |  | 376;377;378;379;380;381; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 16 | DP_HLA_CBOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | 7_Z_TE R POS | Closed |  | 7_Z_TE R POS | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;DPCSO7;stVal;DPC |  | 376;377;378;379;380;381; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 2
|  |  | Digital Inputs Board Slot |  | N
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | N | 1 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89T-R | POSITION |  | Open | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI1 | ST;Pos;stVal;DPC |  | 375;386;391;392;393;409; | None |  |  | 104 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 2 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89T-R | POSITION | Closed |  | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI1 | ST;Pos;stVal;DPC |  | 375;386;391;392;393;409; | None |  |  | 104 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 3 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TE-R | POSITION |  | Open | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL3;XSWI1 | ST;Pos;stVal;DPC |  | 379;380;381; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 4 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TE-R | POSITION | Closed |  | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL3;XSWI1 | ST;Pos;stVal;DPC |  | 379;380;381; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 5 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89T-Y | POSITION |  | Open | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI2 | ST;Pos;stVal;DPC |  | 375;387;395;396;397;409; | None |  |  | 108 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 6 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89T-Y | POSITION | Closed |  | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI2 | ST;Pos;stVal;DPC |  | 375;387;395;396;397;409; | None |  |  | 108 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 7 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TE-Y | POSITION |  | Open | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL3;XSWI2 | ST;Pos;stVal;DPC |  | 382;383;384; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 8 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TE-Y | POSITION | Closed |  | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL3;XSWI2 | ST;Pos;stVal;DPC |  | 382;383;384; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 9 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89T-B | POSITION |  | Open | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI7 | ST;Pos;stVal;DPC |  | 375;385;388;389;390;409; | None |  |  | 103 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 10 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89T-B | POSITION | Closed |  | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI7 | ST;Pos;stVal;DPC |  | 375;385;388;389;390;409; | None |  |  | 103 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 11 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TE-B | POSITION |  | Open | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI2 | ST;Pos;stVal;DPC |  | 376;377;378; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 12 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TE-B | POSITION | Closed |  | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI2 | ST;Pos;stVal;DPC |  | 376;377;378; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 13 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TS-R | POSITION |  | Open | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI4 | ST;Pos;stVal;DPC |  | 375;379;380;381;388;389;390;394;395;396;397;398;409;517;518;519;520;521;522;523;524;525;526;666;667;668;669;670;671;672;673;674;675; | None |  |  | 106 |  |  | Yes |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 14 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TS-R | POSITION | Closed |  | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI4 | ST;Pos;stVal;DPC |  | 375;379;380;381;388;389;390;394;395;396;397;398;409;517;518;519;520;521;522;523;524;525;526;666;667;668;669;670;671;672;673;674;675; | None |  |  | 106 |  |  | Yes |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 15 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TS-Y | POSITION |  | Open | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI5 | ST;Pos;stVal;DPC |  | 375;382;383;384;388;389;390;391;392;393;394;398;409;517;518;519;520;521;522;523;524;525;526;666;667;668;669;670;671;672;673;674;675; | None |  |  | 107 |  |  | Yes |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 16 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TS-Y | POSITION | Closed |  | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI5 | ST;Pos;stVal;DPC |  | 375;382;383;384;388;389;390;391;392;393;394;398;409;517;518;519;520;521;522;523;524;525;526;666;667;668;669;670;671;672;673;674;675; | None |  |  | 107 |  |  | Yes |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 3
|  |  | Digital Inputs Board Slot |  | M
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | M | 1 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TS-B | POSITION |  | Open | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI3 | ST;Pos;stVal;DPC |  | 375;376;377;378;391;392;393;394;395;396;397;398;409;517;518;519;520;521;522;523;524;525;526;666;667;668;669;670;671;672;673;674;675; | None |  |  | 105 |  |  | Yes |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 2 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TS-B | POSITION | Closed |  | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI3 | ST;Pos;stVal;DPC |  | 375;376;377;378;391;392;393;394;395;396;397;398;409;517;518;519;520;521;522;523;524;525;526;666;667;668;669;670;671;672;673;674;675; | None |  |  | 105 |  |  | Yes |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 3 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TS-RE | POSITION |  | Open | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL3;XSWI3 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 4 | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TS-RE | POSITION | Closed |  | OP_CL_POS | Transmitted to IEC | [7 empty] | CONTROL3;XSWI3 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 5 | SPE_HLA_Normal_Fail | SPS | 400kV | B409-ICT-1 | PROTECTION | DC SUPPLY-1 | Fail | Normal | NL_FL_DC SUP1 | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | ST;Ind11;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 6 | SPE_HLA_Normal_Fail | SPS | 400kV | B409-ICT-1 | PROTECTION | DC SUPPLY-2 | Fail | Normal | NL_FL_DC SUP-2 | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | ST;Ind1;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 7 | SPE_HLA_Healthy_Flty | SPS | 400kV | B409-ICT-1 | PROTECTION | TRIP COIL-1 | Faulty | Healthy | HL_FT_TC1 | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | ST;Ind10;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 8 | SPE_HLA_Healthy_Flty | SPS | 400kV | B409-ICT-1 | PROTECTION | TRIP COIL-2 | Faulty | Healthy | HL_FT_TC2 | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | ST;Ind9;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 9 | SPE_HLA_Healthy_Flty | SPS | 400kV | B409-ICT-1 | PROTECTION | PUA RELAY | Faulty | Healthy | HL_FT_PUA RLY | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | ST;Ind2;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 10 | SPE_HLA_Healthy_Flty | SPS | 400kV | B409-ICT-1 | PROTECTION | PUB RELAY | Faulty | Healthy | HL_FT_PUB RLY | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | ST;Ind3;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 11 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | -12 | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | PROTECTION | AT SELECT | Set | Reset | RS_ST_AT SELECT | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | ST;Ind4;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | -13 | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | PROTECTION | R/Y/B AT SELECT | Set | Reset | RS_ST_R/Y/B AT | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | ST;Ind5;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 14 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 15 | DP_HLA_Trip_Closed | DPS | 400kV | B409-ICT-1 | 52 | EMERGENCY/MANUAL |  | Trip | TP_CL_EMRG/MAN | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;DPCSO1;stVal;DPC |  | 404; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 16 | DP_HLA_Trip_Closed | DPS | 400kV | B409-ICT-1 | 52 | EMERGENCY/MANUAL | Closed |  | TP_CL_EMRG/MAN | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;DPCSO1;stVal;DPC |  | 404; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 4
|  |  | Digital Inputs Board Slot |  | L
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | L | 1 | SPE_HLA_Normal_Alarm | SPS | 400kV | B409-ICT-1 | CSD | CSD DEVICE NOT READY | Alarm | Normal | NL_AL_CSD NR | Transmitted to IEC | [7 empty] | CONTROL2;GGIO3 | ST;Ind2;stVal;SPS |  | 400; | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 2 | SPE_HLa_In_Out | SPS | 400kV | B409-ICT-1 | CSD | CSD | In | Out | IN_OT_CSD | Transmitted to IEC | [7 empty] | CONTROL2;GGIO3 | ST;Ind1;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 3 | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | PROTECTION | LA COUNTER R PHASE | Set | Reset | RS_ST_LA COUN R | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | ST;Ind6;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 4 | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | PROTECTION | LA COUNTER Y PHASE | Set | Reset | RS_ST_LA COUN Y | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | ST;Ind7;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 5 | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | PROTECTION | LA COUNTER B PHASE | Set | Reset | RS_ST_LA COUN B | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | ST;Ind8;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 6 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 7 | DP_HLA_CBOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | 7_Y_52 POS |  | Open | 7_Y_52 POS | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;DPCSO2;stVal;DPC |  | 376;377;378;379;380;381;382;383;384;388;389;390;391;392;393;395;396;397; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 8 | DP_HLA_CBOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | 7_Y_52 POS | Closed |  | 7_Y_52 POS | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;DPCSO2;stVal;DPC |  | 376;377;378;379;380;381;382;383;384;388;389;390;391;392;393;395;396;397; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 9 | DP_HLA_CBOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | 7_Z_52 POS |  | Open | 7_Z_52 POS | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;DPCSO3;stVal;DPC |  | 376;377;378;379;380;381;382;383;384;388;389;390;391;392;393;395;396;397; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 10 | DP_HLA_CBOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | 7_Z_52 POS | Closed |  | 7_Z_52 POS | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;DPCSO3;stVal;DPC |  | 376;377;378;379;380;381;382;383;384;388;389;390;391;392;393;395;396;397; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 11 | DP_HLA_CBOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | 7_Z_TR POS |  | Open | 7_Z_TR POS | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;DPCSO4;stVal;DPC |  | 386; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 12 | DP_HLA_CBOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | 7_Z_TR POS | Closed |  | 7_Z_TR POS | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;DPCSO4;stVal;DPC |  | 386; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 13 | DP_HLA_CBOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | 7_Z_TY POS |  | Open | 7_Z_TY POS | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;DPCSO5;stVal;DPC |  | 387; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 14 | DP_HLA_CBOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | 7_Z_TY POS | Closed |  | 7_Z_TY POS | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;DPCSO5;stVal;DPC |  | 387; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 15 | DP_HLA_CBOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | 7_Z_TB POS |  | Open | 7_Z_TB POS | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;DPCSO6;stVal;DPC |  | 385; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 16 | DP_HLA_CBOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | 7_Z_TB POS | Closed |  | 7_Z_TB POS | Transmitted to IEC | [7 empty] | CONTROL4;XCBR1 | ST;DPCSO6;stVal;DPC |  | 385; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 5
|  |  | Digital Inputs Board Slot |  | K
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | K | 1 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | K | 2 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | K | 3 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | K | 4 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | K | 5 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | K | 6 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | K | 7 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | K | 8 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | K | 9 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | K | 10 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | K | 11 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | K | 12 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | K | 13 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | K | 14 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | K | 15 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | K | 16 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 0
|  |  | Digital Outputs Board Slot |  | E
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | E | 1 | DC_SBO_Open_Close | DPC | 400kV | B409-ICT-1 | 52 | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI9 | CO;Pos;sboClass;DPC | [5 empty] | 100 |  |  | NO |  | CB | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 2 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 3 | DC_SBO_Open_Close | DPC | 400kV | B409-ICT-1 | 52 | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI9 | CO;Pos;sboClass;DPC | [5 empty] | 100 |  |  | NO |  | CB | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 4 | SC_DE_Reset_Set_1 | SPC | 400kV | B409-ICT-1 | PROTECTION | CB CLOSE TO PUA | Set |  | XX_XX_CB CLS PUA | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | CO;SPCSO2;ctlVal;DPC | [6 empty] | 239 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 5 | SC_DE_Reset_Set_1 | SPC | 400kV | B409-ICT-1 | PROTECTION | CB CLOSE TO PUB | Set |  | XX_XX_CB CLS PUB | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | CO;SPCSO3;ctlVal;DPC | [6 empty] | 240 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 6 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 7 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 8 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 9 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 10 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 1
|  |  | Digital Outputs Board Slot |  | F
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | F | 1 | DC_SBO_Open_Close | DPC | 400kV | B409-ICT-1 | 89A | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | CO;Pos;sboClass;DPC | [5 empty] | 101 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 2 | DC_SBO_Open_Close | DPC | 400kV | B409-ICT-1 | 89A | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | CO;Pos;sboClass;DPC | [5 empty] | 101 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 3 | SC_DE_NotPerm_Perm | SPC | 400kV | B409-ICT-1 | IL PERMISSIVE | 89A I/L PERMISSIVE |  |  | XX_XX_89A | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO1;ctlVal;DPC | [6 empty] | 384 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 4 | SC_DE_NotPerm_Perm | SPC | 400kV | B409-ICT-1 | IL PERMISSIVE | 89AE I/L PERMISSIVE |  |  | XX_XX_89AE | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO11;ctlVal;DPC | [6 empty] | 385 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 5 | DC_SBO_Open_Close | DPC | 400kV | B409-ICT-1 | 89B | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI6 | CO;Pos;sboClass;DPC | [5 empty] | 102 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 6 | DC_SBO_Open_Close | DPC | 400kV | B409-ICT-1 | 89B | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI6 | CO;Pos;sboClass;DPC | [5 empty] | 102 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 7 | SC_DE_NotPerm_Perm | SPC | 400kV | B409-ICT-1 | IL PERMISSIVE | 89B I/L PERMISSIVE |  |  | XX_XX_89B | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO10;ctlVal;DPC | [6 empty] | 386 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 8 | SC_DE_NotPerm_Perm | SPC | 400kV | B409-ICT-1 | IL PERMISSIVE | 89BE I/L PERMISSIVE |  |  | XX_XX_89BE | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO12;ctlVal;DPC | [6 empty] | 387 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 9 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 10 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 2
|  |  | Digital Outputs Board Slot |  | G
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | G | 1 | DC_SBO_Open_Close_1 | DPC | 400kV | B409-ICT-1 | 89T-R | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI8 | CO;Pos;sboClass;DPC | [5 empty] | 104 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 2 | DC_SBO_Open_Close_1 | DPC | 400kV | B409-ICT-1 | 89T-R | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI8 | CO;Pos;sboClass;DPC | [5 empty] | 104 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 3 | SC_DE_NotPerm_Perm | SPC | 400kV | B409-ICT-1 | IL PERMISSIVE | 89T-R IL PERM |  |  | XX_XX_89T-R | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO13;ctlVal;DPC | [6 empty] | 392 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 4 | SC_DE_NotPerm_Perm | SPC | 400kV | B409-ICT-1 | IL PERMISSIVE | 89TE-R IL PERM |  |  | XX_XX_89TE-R | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO3;ctlVal;DPC | [6 empty] | 390 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 5 | DC_SBO_Open_Close_1 | DPC | 400kV | B409-ICT-1 | 89T-Y | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | CO;Pos;sboClass;DPC | [5 empty] | 108 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 6 | DC_SBO_Open_Close_1 | DPC | 400kV | B409-ICT-1 | 89T-Y | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | CO;Pos;sboClass;DPC | [5 empty] | 108 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 7 | SC_DE_NotPerm_Perm | SPC | 400kV | B409-ICT-1 | IL PERMISSIVE | 89T-Y IL PERM |  |  | XX_XX_89T-Y | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO14;ctlVal;DPC | [6 empty] | 397 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 8 | SC_DE_NotPerm_Perm | SPC | 400kV | B409-ICT-1 | IL PERMISSIVE | 89TE-Y IL PERM |  |  | XX_XX_89TE-Y | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO4;ctlVal;DPC | [6 empty] | 391 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 9 | SC_DE_NotPerm_Perm_1 | SPC | 400kV | B409-ICT-1 | VT SELECTION | 765KV AT CVT |  |  | 7_AT_CVT_SEL | Transmitted to IEC | [7 empty] | CONTROL2;GGIO4 | CO;SPCSO7;ctlVal;DPC |  | 409<; |  |  |  |  | 408 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 10 | SC_DE_NotPerm_Perm_1 | SPC | 400kV | B409-ICT-1 | VT SELECTION | 765KV AT CVT |  |  | 7_AT_CVT_DE-SEL | Transmitted to IEC | [7 empty] | CONTROL2;GGIO4 | CO;SPCSO8;ctlVal;DPC |  | 409<; |  |  |  |  | 409 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 3
|  |  | Digital Outputs Board Slot |  | H
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | H | 1 | DC_SBO_Open_Close_1 | DPC | 400kV | B409-ICT-1 | 89T-B | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI7 | CO;Pos;sboClass;DPC | [5 empty] | 103 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 2 | DC_SBO_Open_Close_1 | DPC | 400kV | B409-ICT-1 | 89T-B | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI7 | CO;Pos;sboClass;DPC | [5 empty] | 103 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 3 | SC_DE_NotPerm_Perm | SPC | 400kV | B409-ICT-1 | IL PERMISSIVE | 89T-B IL PERM |  |  | XX_XX_89T-B | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO9;ctlVal;DPC | [6 empty] | 388 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 4 | SC_DE_NotPerm_Perm | SPC | 400kV | B409-ICT-1 | IL PERMISSIVE | 89TE-B IL PERM |  |  | XX_XX_89TE-B | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO2;ctlVal;DPC | [6 empty] | 389 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 5 | SC_DE_Reset_Set_Int_2 | SPC | 400kV | B409-ICT-1 | VT SELECTION | 400KV BUS-1 VT | Set |  | BUS-1_VT_SELECT | Transmitted to IEC | [7 empty] | CONTROL2;GGIO4 | CO;SPCSO2;ctlVal;DPC |  | 409<; |  |  |  |  | 410 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 6 | SC_DE_Reset_Set_Int_2 | SPC | 400kV | B409-ICT-1 | VT SELECTION | 400KV BUS-1 VT | Set |  | BUS-1_VT_DE-SEL | Transmitted to IEC | [7 empty] | CONTROL2;GGIO4 | CO;SPCSO1;ctlVal;DPC |  | 409<; |  |  |  |  | 409 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 7 | SC_DE_Reset_Set_Int_2 | SPC | 400kV | B409-ICT-1 | VT SELECTION | 400KV BUS-2 VT | Set |  | BUS-2_VT_SELECT | Transmitted to IEC | [7 empty] | CONTROL2;GGIO4 | CO;SPCSO4;ctlVal;DPC |  | 409<; |  |  |  |  | 412 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 8 | SC_DE_Reset_Set_Int_2 | SPC | 400kV | B409-ICT-1 | VT SELECTION | 400KV BUS-2 VT | Set |  | BUS-2_VT_DE-SEL | Transmitted to IEC | [7 empty] | CONTROL2;GGIO4 | CO;SPCSO3;ctlVal;DPC |  | 409<; |  |  |  |  | 411 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 9 | SC_DE_Reset_Set_Int_2 | SPC | 400kV | B409-ICT-1 | VT SELECTION | 400KV LINE | Set |  | LINE_SELECT | Transmitted to IEC | [7 empty] | CONTROL2;GGIO4 | CO;SPCSO5;ctlVal;DPC |  | 409<; |  |  |  |  | 414 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 10 | SC_DE_Reset_Set_Int_2 | SPC | 400kV | B409-ICT-1 | VT SELECTION | 400KV LINE | Set |  | LINE_DE-SELECT | Transmitted to IEC | [7 empty] | CONTROL2;GGIO4 | CO;SPCSO6;ctlVal;DPC |  | 409<; |  |  |  |  | 413 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 4
|  |  | Digital Outputs Board Slot |  | I
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | I | 1 | DC_SBO_Open_Close_1 | DPC | 400kV | B409-ICT-1 | 89TS-R | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI4 | CO;Pos;sboClass;DPC | [5 empty] | 106 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 2 | DC_SBO_Open_Close_1 | DPC | 400kV | B409-ICT-1 | 89TS-R | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI4 | CO;Pos;sboClass;DPC | [5 empty] | 106 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 3 | SC_DE_NotPerm_Perm | SPC | 400kV | B409-ICT-1 | IL PERMISSIVE | 89TS-R IL PERM |  |  | XX_XX_89TS-R | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO5;ctlVal;DPC | [6 empty] | 394 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 4 | DC_SBO_Open_Close_1 | DPC | 400kV | B409-ICT-1 | 89TS-Y | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI5 | CO;Pos;sboClass;DPC | [5 empty] | 107 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 5 | DC_SBO_Open_Close_1 | DPC | 400kV | B409-ICT-1 | 89TS-Y | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI5 | CO;Pos;sboClass;DPC | [5 empty] | 107 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 6 | SC_DE_Reset_Reset_1 | SPC | 400kV | B409-ICT-1 | IL PERMISSIVE | 89TS-Y IL PERM | Reset |  | XX_XX_89TS-Y | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO6;ctlVal;DPC | [6 empty] | 396 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 7 | DC_SBO_Open_Close_1 | DPC | 400kV | B409-ICT-1 | 89TS-B | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | CO;Pos;sboClass;DPC | [5 empty] | 105 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 8 | DC_SBO_Open_Close_1 | DPC | 400kV | B409-ICT-1 | 89TS-B | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | CO;Pos;sboClass;DPC | [5 empty] | 105 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 9 | SC_DE_NotPerm_Perm | SPC | 400kV | B409-ICT-1 | IL PERMISSIVE | 89TS-B IL PERM |  |  | XX_XX_89TS-B | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO8;ctlVal;DPC | [6 empty] | 393 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 10 | SC_DE_NotPerm_Perm | SPC | 400kV | B409-ICT-1 | IL PERMISSIVE | 89TS-RE IL PERM |  |  | XX_XX_89TS-RE | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO7;ctlVal;DPC | [6 empty] | 395 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 5
|  |  | Digital Outputs Board Slot |  | J
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | J | 1 | SC_DE_Reset_Set_1 | SPC | 400kV | B409-ICT-1 | AT_SELECTION | AT#1 SELECT | Set |  | XX_XX_AT#1 SELEC | Transmitted to IEC | [7 empty] | CONTROL2;GGIO5 | CO;SPCSO8;ctlVal;DPC | [6 empty] | 405 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 2 | SC_DE_Reset_Set_1 | SPC | 400kV | B409-ICT-1 | AT_SELECTION | AT#1 DESELECT | Set |  | XX_XX_AT#1 DSELE | Transmitted to IEC | [7 empty] | CONTROL2;GGIO5 | CO;SPCSO7;ctlVal;DPC | [6 empty] | 404 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 3 | SC_DE_Reset_Set_1 | SPC | 400kV | B409-ICT-1 | AT_SELECTION | AT#1 R PH SELECT | Set |  | XX_XX_AT#1 R SEL | Transmitted to IEC | [7 empty] | CONTROL2;GGIO5 | CO;SPCSO6;ctlVal;DPC | [6 empty] | 401 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 4 | SC_DE_Reset_Set_1 | SPC | 400kV | B409-ICT-1 | AT_SELECTION | AT#1 R PH DESELECT | Set |  | XX_XX_AT#1 R DSE | Transmitted to IEC | [7 empty] | CONTROL2;GGIO5 | CO;SPCSO5;ctlVal;DPC | [6 empty] | 400 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 5 | SC_DE_Reset_Set_1 | SPC | 400kV | B409-ICT-1 | AT_SELECTION | AT#1 Y PH SELECT | Set |  | XX_XX_AT#1 Y SEL | Transmitted to IEC | [7 empty] | CONTROL2;GGIO5 | CO;SPCSO4;ctlVal;DPC | [6 empty] | 403 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 6 | SC_DE_Reset_Set_1 | SPC | 400kV | B409-ICT-1 | AT_SELECTION | AT#1 Y PH DESELECT | Set |  | XX_XX_AT#1 Y DSE | Transmitted to IEC | [7 empty] | CONTROL2;GGIO5 | CO;SPCSO3;ctlVal;DPC | [6 empty] | 402 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 7 | SC_DE_Reset_Set_1 | SPC | 400kV | B409-ICT-1 | AT_SELECTION | AT#1 B PH SELECT | Set |  | XX_XX_AT#1 B SEL | Transmitted to IEC | [7 empty] | CONTROL2;GGIO5 | CO;SPCSO2;ctlVal;DPC | [6 empty] | 399 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 8 | SC_DE_Reset_Set_1 | SPC | 400kV | B409-ICT-1 | AT_SELECTION | AT#1 B PH DESELECT | Set |  | XX_XX_AT#1 B DSE | Transmitted to IEC | [7 empty] | CONTROL2;GGIO5 | CO;SPCSO1;ctlVal;DPC | [6 empty] | 398 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 9 | SC_DE_Reset_Set | SPC | 400kV | B409-ICT-1 | CSD | CSD BYPASS | Set |  | XX_XX_CSD BYPASS | Transmitted to IEC | [7 empty] | CONTROL2;GGIO3 | CO;SPCSO1;ctlVal;DPC | [6 empty] | 406 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 10 | SC_DE_Reset_Set_1 | SPC | 400kV | B409-ICT-1 | PROTECTION | CB TRIP COIL-2 | Set |  | XX_XX_TC2 | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | CO;SPCSO1;ctlVal;DPC | [6 empty] | 213 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
ANALOG INPUT BOARD AIU21x
|  |  | Analog Input Board Number |  | 0
|  |  | Analog Input Board Slot |  | D
Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Channel | Transducer Type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 2 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 3 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 4 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 5 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 6 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 7 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 8 | 4/20 mA | MV_hla_Temp | ˚ Cel | 400kV | B409-ICT-1 | PROTECTION | AC KIOSK TEMP | 0.0 | 100.0 | AC KIOSK TEMP | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | MX;AnIn1;mag;MV | [14 empty] | 6 | ANALOG INPUT BOARD AIU21x
CT/VT ANALOG INPUT BOARD TMU2x0
|  |  | CT/VT Board Number |  | 0
|  |  | CT/VT Board Slot |  | Q
|  |  | CT/VT Board Model |  | TMU220
CT acquisition
VT acquisition
|  |  | Nominal Current |  | 1 | (1A/5A)
|  |  | Nominal Voltage |  | 110 | [1V … 500V]
Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Input type (U/I) |  | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | DF |  | MV_HLa_Frequency_1 | Hz | 400kV | B409-ICT-1 | SYNCH DATA | FREQUENCY DIFFERENCE | 0.0 | 2.0 | FREQUENCY DIFF | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | MX;DifHzClc;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | DV |  | MV_hla_ AuxVoltage_1 | V | 400kV | B409-ICT-1 | SYNCH DATA | VOLTAGE DIFFERENCE | 0.0 | 277.13626 | VOLTAGE DIFF | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | MX;DifVClc;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Dj |  | MV_hla_PhaseDiff | ˚ | 400kV | B409-ICT-1 | SYNCH DATA | PHASE DIFFERENCE | 0.0 | 360.0 | PHASE ANGLE DIFF | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | MX;DifAngClc;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ia |  | MV_HLa_AuxCurrent | A | 400kV | B409-ICT-1 | METERING | I-R PHASE CURRENT | 0.0 | 3600.0 | IR PHASE CURRENT | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;A;phsA;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ib |  | MV_HLa_AuxCurrent_1 | A | 400kV | B409-ICT-1 | METERING | I-Y PHASE CURRENT | 0.0 | 3600.0 | IY PHASE CURRENT | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;A;phsB;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ic |  | MV_HLa_AuxCurrent | A | 400kV | B409-ICT-1 | METERING | I-B PHASE CURRENT | 0.0 | 3600.0 | IB PHASE CURRENT | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;A;phsC;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Vb |  | MV_hla_ AuxVoltage_1 | V | 400kV | B409-ICT-1 | SYNCH DATA | INCOMING SUPPLY | 0.0 | 277.13626 | INCOMING SUPPLY | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU2 | MX;PhV;phsB;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Uab |  | MV_hla_ AuxVoltage | V | 400kV | B409-ICT-1 | METERING | R-Y VOLTAGE | 0.0 | 480.0 | R-Y VOLTAGE | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;PPV;phsAB;DELTA | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ubc |  | MV_HLa_Voltage | kV | 400kV | B409-ICT-1 | METERING | Y-B VOLTAGE | 0.0 | 480.0 | Y-B VOLTAGE | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;PPV;phsBC;DELTA | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Uca |  | MV_HLa_Voltage | kV | 400kV | B409-ICT-1 | METERING | B-R VOLTAGE | 0.0 | 480.0 | B-R VOLTAGE | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;PPV;phsCA;DELTA | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Vbusbar |  | MV_hla_ AuxVoltage_1 | V | 400kV | B409-ICT-1 | SYNCH DATA | RUNNING SUPPLY | 0.0 | 277.13626 | RUNNING SPLY-1 | Transmitted to IEC | [7 empty] | MEASUREMENT1;barMMXU1 | MX;PhV;phsA;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Freq (Line) |  | MV_HLa_Frequency | Hz | 400kV | B409-ICT-1 | METERING | FREQUENCY | 45.0 | 55.0 | FREQUENCY | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;Hz;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | P total (MW) |  | MV_HLa_ActPower | MW | 400kV | B409-ICT-1 | METERING | ACTIVE POWER | -1662.72 | 1662.72 | ACTIVE POWER | Transmitted to IEC | [7 empty] | MEASUREMENT1;powMMXU1 | MX;TotW;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Q total (Mvar) |  | MV_HLa_ActPower | MW | 400kV | B409-ICT-1 | METERING | REACTIVE POWER | -1662.72 | 1662.72 | REACTIVE POWER | Transmitted to IEC | [7 empty] | MEASUREMENT1;powMMXU1 | MX;TotVAr;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | cos ft : Power factor |  | MV_HLa_PowerFactor |  | 400kV | B409-ICT-1 | METERING | POWER FACTOR | -1.2 | 1.2 | POWER FACTOR | Transmitted to IEC | [7 empty] | MEASUREMENT1;powMMXU1 | MX;TotPF;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  |  |  | SPARE | [32 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  |  |  | SPARE | [32 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | 52 ¦ OE_CL_CONTROL | OPEN ORDER | Set | Reset | RS_ST_OPN ORD | Transmitted to IEC | [7 empty] | CONTROL1;CSWI9 | ST;OpnOrd;general;general;ACT |  | 401; | None |  |  |  | 213 |  |  |  | CB | OpenOrderSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89A ¦ OE_CL_CONTROL | OPEN INTERLOCK | Permissive | Not Permissive | NP_PE_OPN ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO1 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | SG | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89B ¦ OE_CL_CONTROL | OPEN INTERLOCK | Permissive | Not Permissive | NP_PE_OPN ILK | Transmitted to IEC | [7 empty] | CONTROL3;CILO4 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | SG | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89T-B ¦ OE_CL_CONTROL | OPEN INTERLOCK | Permissive | Not Permissive | OPEN INTERLOCK | Transmitted to IEC | [7 empty] | CONTROL3;CILO5 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | SG | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89T-R ¦ OE_CL_CONTROL | OPEN INTERLOCK | Permissive | Not Permissive | OPEN INTERLOCK | Transmitted to IEC | [7 empty] | CONTROL3;CILO6 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | SG | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89TS-B ¦ OE_CL_CONTROL | OPEN INTERLOCK | Permissive | Not Permissive | OPEN INTERLOCK | Transmitted to IEC | [7 empty] | CONTROL3;CILO1 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | SG | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89TS-R ¦ OE_CL_CONTROL | OPEN INTERLOCK | Permissive | Not Permissive | OPEN INTERLOCK | Transmitted to IEC | [7 empty] | CONTROL3;CILO2 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | SG | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89TS-Y ¦ OE_CL_CONTROL | OPEN INTERLOCK | Permissive | Not Permissive | OPEN INTERLOCK | Transmitted to IEC | [7 empty] | CONTROL3;CILO3 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | SG | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89T-Y ¦ OE_CL_CONTROL | OPEN INTERLOCK | Permissive | Not Permissive | OPEN INTERLOCK | Transmitted to IEC | [7 empty] | CONTROL2;CILO2 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | SG | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPS_hla_Set_Reset | SPS | 400kV | B409-ICT-1 |  | ORDER RUNNING ON THE BAY | Set | Reset | RS_ST_ORD RUNING | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | ST;OrdRun;stVal;SPS |  |  | None | [8 empty] | OrderInProgress |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 52 ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | NP_PE_CLOSE ILK | Transmitted to IEC | [7 empty] | CONTROL4;CILO1 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | CB | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89A ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | NP_PE_CLS ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO1 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | SG | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89B ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | NP_PE_CLS ILK | Transmitted to IEC | [7 empty] | CONTROL3;CILO4 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | SG | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89T-B ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | CLOSE INTERLOCK | Transmitted to IEC | [7 empty] | CONTROL3;CILO5 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | SG | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89T-R ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | CLOSE INTERLOCK | Transmitted to IEC | [7 empty] | CONTROL3;CILO6 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | SG | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89TS-B ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | CLOSE INTERLOCK | Transmitted to IEC | [7 empty] | CONTROL3;CILO1 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | SG | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 17 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89TS-R ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | CLOSE INTERLOCK | Transmitted to IEC | [7 empty] | CONTROL3;CILO2 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | SG | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 18 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89TS-Y ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | CLOSE INTERLOCK | Transmitted to IEC | [7 empty] | CONTROL3;CILO3 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | SG | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 19 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89T-Y ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | CLOSE INTERLOCK | Transmitted to IEC | [7 empty] | CONTROL2;CILO2 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | SG | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 20 |  | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | SYNCH FUNCTION | CLOSE ORDER | Set | Reset | RS_ST_CLS ODR | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;ClsOpSt;stVal;SPS |  |  | None | [7 empty] | IntManualCSFct | CS_CloseOrderState_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 21 |  | SPE_HLA_on_off | SPS | 400kV | B409-ICT-1 | SYNCH FUNCTION | ON/OFF SECONDARY SPS | Off | On | RS_ST_ON/OFF SEC | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;EnaSec;origin;SPC |  |  | None |  |  | 201 |  |  |  |  | IntManualCSFct | CS_OnOff_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 22 |  | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | SYNCH FUNCTION | POSSIBLE CLOSING | Set | Reset | RS_ST_POS CLS | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;Rel;stVal;SPS |  | 405; | None | [7 empty] | IntManualCSFct | CS_AuthoState_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 23 |  | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | SYNCH FUNCTION | PRESENCE OF REFERENCE VOLTAGE | Set | Reset | RS_ST_REF U PRES | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;VRefInd;stVal;SPS |  | 405; | None | [7 empty] | IntManualCSFct | CS_VoltageRefPresence_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 24 |  | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | SYNCH FUNCTION | ABSENCE OF REFERENCE VOLTAGE | Set | Reset | RS_ST_REF. U ABS | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;VRefAbs;stVal;SPS |  | 405; | None | [7 empty] | IntManualCSFct | CS_VoltageRefAbsence_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 25 |  | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | SYNCH FUNCTION | VOLT ABSENCE | Set | Reset | RS_ST_VOLT ABS | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;VAbs;stVal;SPS |  | 405; | None | [7 empty] | IntManualCSFct | CS_VoltageAbsence_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 26 |  | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | SYNCH FUNCTION | VOLT PRESENCE | Set | Reset | RS_ST_VOLT PRES | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;VP;stVal;SPS |  | 405; | None | [7 empty] | IntManualCSFct | CS_VoltagePresence_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 27 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 52 ¦ OE_CL_CONTROL | CLOSE ORDER | Permissive | Not Permissive | RS_ST_CLS ORD | Transmitted to IEC | [7 empty] | CONTROL1;CSWI9 | ST;ClsOrd;general;general;ACT |  | 404; | None |  |  |  | 239;240 |  |  |  | CB | CloseOrderSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 28 |  | SPE_HLA_Normal_Alarm | SPS | 400kV | B409-ICT-1 | 52 | LOSS OF SF6 GAS POLE A/B/C | Alarm | Normal | NL_AL_LOSS SF6 | Transmitted to IEC | [7 empty] | CONTROL1;CSWI9 | ST;IndSys2;stVal;SPS |  | 403<; | None | [7 empty] | CB |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 29 |  | SPE_HLA_Normal_Alarm | SPS | 400kV | B409-ICT-1 | 52 | SPRING CHARGE STATUS | Alarm | Normal | NL_AL_SPING ST 2 | Transmitted to IEC | [7 empty] | CONTROL1;CSWI9 | ST;IndSys1;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 30 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89A | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | ST;IndSys1;stVal;SPS |  | 367<; | None |  |  |  | 384 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 31 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89AE | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL3;CSWI6 | ST;IndSys1;stVal;SPS |  | 370<; | None |  |  |  | 385 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 32 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89B | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL1;CSWI6 | ST;IndSys1;stVal;SPS |  | 371<; | None |  |  |  | 386 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 33 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89BE | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL3;CSWI4 | ST;IndSys1;stVal;SPS |  | 374<; | None |  |  |  | 387 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 34 |  | SPE_HLA_Reset_Optd | SPS | 400kV | B409-ICT-1 | 89T | POS_CLOSE_FBD | Operated | Reset | RS_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;GAPC1 | ST;IndSys2;stVal;SPS |  | 375<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 35 |  | SPE_HLA_Reset_Optd | SPS | 400kV | B409-ICT-1 | 89T | POS_OPEN_FBD | Operated | Reset | RS_OE_POS | Transmitted to IEC | [7 empty] | CONTROL2;GAPC1 | ST;IndSys1;stVal;SPS |  | 375<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 36 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89T-B | INTERLOCK | Permissive | Not Permissive | NP_PE_I/L | Transmitted to IEC | [7 empty] | CONTROL1;CSWI7 | ST;IndSys1;stVal;SPS |  | 376<; | None |  |  |  | 388 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 37 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89TE-B | INTERLOCK | Permissive | Not Permissive | NP_PE_I/L | Transmitted to IEC | [7 empty] | CONTROL2;CSWI1 | ST;IndSys1;stVal;SPS |  | 385<; | None |  |  |  | 389 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 38 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89TE-R | INTERLOCK | Permissive | Not Permissive | NP_PE_I/L | Transmitted to IEC | [7 empty] | CONTROL3;CSWI1 | ST;IndSys1;stVal;SPS |  | 386<; | None |  |  |  | 390 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 39 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89TE-Y | INTERLOCK | Permissive | Not Permissive | NP_PE_I/L | Transmitted to IEC | [7 empty] | CONTROL3;CSWI2 | ST;IndSys1;stVal;SPS |  | 387<; | None |  |  |  | 391 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 40 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89T-R | INTERLOCK | Permissive | Not Permissive | NP_PE_I/L | Transmitted to IEC | [7 empty] | CONTROL1;CSWI8 | ST;IndSys1;stVal;SPS |  | 379<; | None |  |  |  | 392 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 41 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89TS-B | INTERLOCK | Permissive | Not Permissive | NP_PE_I/L | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | ST;IndSys1;stVal;SPS |  | 388<; | None |  |  |  | 393 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 42 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89TS-R | INTERLOCK | Permissive | Not Permissive | NP_PE_I/L | Transmitted to IEC | [7 empty] | CONTROL1;CSWI4 | ST;IndSys1;stVal;SPS |  | 391<; | None |  |  |  | 394 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 43 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89TS-RE | INTERLOCK | Permissive | Not Permissive | NP_PE_I/L | Transmitted to IEC | [7 empty] | CONTROL3;CSWI3 | ST;IndSys1;stVal;SPS |  | 394<; | None |  |  |  | 395 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 44 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89TS-Y | INTERLOCK | Permissive | Not Permissive | NP_PE_I/L | Transmitted to IEC | [7 empty] | CONTROL1;CSWI5 | ST;IndSys1;stVal;SPS |  | 395<; | None |  |  |  | 396 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 45 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B409-ICT-1 | 89T-Y | INTERLOCK | Permissive | Not Permissive | NP_PE_I/L | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | ST;IndSys1;stVal;SPS |  | 382<; | None |  |  |  | 397 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 46 |  | SPE_HLa_Dselect_Select | SPS | 400kV | B409-ICT-1 | AT_SELECTION | AT B-PH | Selected | Deselected | T_B-PH_DE-SEL | Transmitted to IEC | [7 empty] | CONTROL2;GAPC7 | ST;IndSys3;stVal;SPS |  | 398;398<; | None |  |  |  | 398 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 47 |  | SPE_HLa_Reset_Select | SPS | 400kV | B409-ICT-1 | AT_SELECTION | AT B-PH | Selected | Reset | T_B-PH_SEL | Transmitted to IEC | [7 empty] | CONTROL2;GAPC7 | ST;IndSys4;stVal;SPS |  | 398;398<; | None |  |  |  | 399 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 48 |  | SPE_HLa_Dselect_Select | SPS | 400kV | B409-ICT-1 | AT_SELECTION | AT R-PH | Selected | Deselected | T_R-PH_DE-SEL | Transmitted to IEC | [7 empty] | CONTROL2;GAPC7 | ST;IndSys5;stVal;SPS |  | 398;398<; | None |  |  |  | 400 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 49 |  | SPE_HLa_Reset_Select | SPS | 400kV | B409-ICT-1 | AT_SELECTION | AT R-PH | Selected | Reset | T_R-PH_SEL | Transmitted to IEC | [7 empty] | CONTROL2;GAPC7 | ST;IndSys6;stVal;SPS |  | 398;398<; | None |  |  |  | 401 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 50 |  | SPE_HLa_Reset_Select | SPS | 400kV | B409-ICT-1 | AT_SELECTION | AT Y-PH | Selected | Reset | T_Y-PH_DE-SEL | Transmitted to IEC | [7 empty] | CONTROL2;GAPC7 | ST;IndSys7;stVal;SPS |  | 398;398<; | None |  |  |  | 402 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 51 |  | SPE_HLa_Reset_Select | SPS | 400kV | B409-ICT-1 | AT_SELECTION | AT Y-PH | Selected | Reset | T_Y-PH_SEL | Transmitted to IEC | [7 empty] | CONTROL2;GAPC7 | ST;IndSys8;stVal;SPS |  | 398;398<; | None |  |  |  | 403 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 52 |  | SPE_HLa_Dselect_Select | SPS | 400kV | B409-ICT-1 | AT_SELECTION | AT-1 | Selected | Deselected | T-1_DE-SELECT | Transmitted to IEC | [7 empty] | CONTROL2;GAPC7 | ST;IndSys2;stVal;SPS |  | 398<; | None |  |  |  | 404 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 53 |  | SPE_HLa_Reset_Select | SPS | 400kV | B409-ICT-1 | AT_SELECTION | AT-1 | Selected | Reset | T-1_SELECT | Transmitted to IEC | [7 empty] | CONTROL2;GAPC7 | ST;IndSys1;stVal;SPS |  | 398<; | None |  |  |  | 405 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 54 |  | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | CSD | CSD BYPASS | Set | Reset | RS_ST_CSD BYPASS | Transmitted to IEC | [7 empty] | CONTROL2;GAPC4 | ST;IndSys1;stVal;SPS |  | 400<; | None |  |  |  | 406 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 55 |  | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | INTER TRIPPING | HV ICT CB OPEN ORDER-1 | Set | Reset | RS_ST_HV ICT CB1 | Transmitted to IEC | [7 empty] | CONTROL2;GAPC5 | ST;IndSys1;stVal;SPS |  | 401<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 56 |  | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | INTER TRIPPING | HV ICT CB OPEN ORDER-2 | Set | Reset | RS_ST_HV ICT CB2 | Transmitted to IEC | [7 empty] | CONTROL2;GAPC5 | ST;IndSys2;stVal;SPS |  | 401<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 57 |  | SPE_HLA_Reset_Optd | SPS | 400kV | B409-ICT-1 | PROTECTION | 86A TRIP RELAY | Operated | Reset | RS_OP_86A | Transmitted to IEC | [7 empty] | CONTROL2;GAPC3 | ST;IndSys3;stVal;SPS |  | 351;366;402<; | None | [5 empty] | Yes | [5 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 58 |  | SPE_HLA_Reset_Optd | SPS | 400kV | B409-ICT-1 | PROTECTION | 86A1 TRIP RELAY | Operated | Reset | RS_OP_86A1 | Transmitted to IEC | [7 empty] | CONTROL2;GAPC3 | ST;IndSys5;stVal;SPS |  | 402; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 59 |  | SPE_HLA_Reset_Optd | SPS | 400kV | B409-ICT-1 | PROTECTION | 86A2 TRIP RELAY | Operated | Reset | RS_OP_86A2 | Transmitted to IEC | [7 empty] | CONTROL2;GAPC3 | ST;IndSys6;stVal;SPS |  | 402; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 60 |  | SPE_HLA_Reset_Optd | SPS | 400kV | B409-ICT-1 | PROTECTION | 86B TRIP RELAY | Operated | Reset | RS_OP_86B | Transmitted to IEC | [7 empty] | CONTROL2;GAPC3 | ST;IndSys4;stVal;SPS |  | 351;366;402<; | None | [5 empty] | Yes | [5 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 61 |  | SPE_HLA_Reset_Optd | SPS | 400kV | B409-ICT-1 | PROTECTION | 86B1 TRIP RELAY | Operated | Reset | RS_OP_86B1 | Transmitted to IEC | [7 empty] | CONTROL2;GAPC3 | ST;IndSys7;stVal;SPS |  | 402; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 62 |  | SPE_HLA_Reset_Optd | SPS | 400kV | B409-ICT-1 | PROTECTION | 86B2 TRIP RELAY | Operated | Reset | RS_OP_86B2 | Transmitted to IEC | [7 empty] | CONTROL2;GAPC3 | ST;IndSys8;stVal;SPS |  | 402; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 63 |  | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | PROTECTION | SOTF TO RELAY | Set | Reset | RS_ST_SOTF TO RL | Transmitted to IEC | [7 empty] | CONTROL2;GAPC3 | ST;IndSys1;stVal;SPS |  | 404<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 64 |  | SPE_HLA_Unhlthy_Hlthy | SPS | 400kV | B409-ICT-1 | PROTECTION | 33KV 50/59N RELAY | Healthy | Unhealthy | UH_HL_33KV50/59N | Transmitted to IEC | [7 empty] | CONTROL2;GAPC3 | ST;IndSys2;stVal;SPS |  |  | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 65 |  | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | SYNCH DATA | CLOSE PERMISSIVE | Set | Reset | RS_ST_CB CLOSE | Transmitted to IEC | [7 empty] | CONTROL2;GAPC2 | ST;IndSys5;stVal;SPS |  | 405<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 66 |  | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | SYNCH DATA | DEAD INCOMING DEAD RUNNING | Set | Reset | RS_ST_DINC_DRUN | Transmitted to IEC | [7 empty] | CONTROL2;GAPC2 | ST;IndSys4;stVal;SPS |  | 405<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 67 |  | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | SYNCH DATA | DEAD INCOMING LIVE RUNNING | Set | Reset | RS_ST_DINC_LRUN | Transmitted to IEC | [7 empty] | CONTROL2;GAPC2 | ST;IndSys3;stVal;SPS |  | 405<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 68 |  | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | SYNCH DATA | LIVE INCOMING DEAD RUNNING | Set | Reset | RS_ST_LINC_DRUN | Transmitted to IEC | [7 empty] | CONTROL2;GAPC2 | ST;IndSys2;stVal;SPS |  | 405<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 69 |  | SPE_HLa_Reset_Set | SPS | 400kV | B409-ICT-1 | SYNCH DATA | LIVE INCOMING LIVE RUNNING | Set | Reset | RS_ST_LINC_LRUN | Transmitted to IEC | [7 empty] | CONTROL2;GAPC2 | ST;IndSys1;stVal;SPS |  | 405<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 70 |  | SPE_HLa_Reset_DSelect | SPS | 400kV | B409-ICT-1 | VT SELECTION | 765KV AT CVT | Deselected | Reset | 7_AT_CVT_DE-SEL | Transmitted to IEC | [7 empty] | CONTROL2;GAPC6 | ST;IndSys8;stVal;SPS |  | 409<; | None |  |  |  | 409 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 71 |  | SPE_HLa_Reset_Select | SPS | 400kV | B409-ICT-1 | VT SELECTION | 765KV AT CVT | Selected | Reset | 7_AT_CVT_SEL | Transmitted to IEC | [7 empty] | CONTROL2;GAPC6 | ST;IndSys7;stVal;SPS |  | 409<; | None |  |  |  | 408 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 72 |  | SPE_HLa_Reset_DSelect | SPS | 400kV | B409-ICT-1 | VT SELECTION | 765KV BUS-1 VT | Deselected | Reset | BUS-1_VT_DE-SEL | Transmitted to IEC | [7 empty] | CONTROL2;GAPC6 | ST;IndSys1;stVal;SPS |  | 409<; | None |  |  |  | 409 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 73 |  | SPE_HLa_Reset_Select | SPS | 400kV | B409-ICT-1 | VT SELECTION | 765KV BUS-1 VT | Selected | Reset | BUS-1_VT_SELECT | Transmitted to IEC | [7 empty] | CONTROL2;GAPC6 | ST;IndSys2;stVal;SPS |  | 409<; | None |  |  |  | 410 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 74 |  | SPE_HLa_Reset_Select | SPS | 400kV | B409-ICT-1 | VT SELECTION | 765KV BUS-2 VT | Selected | Reset | BUS-2_VT_DE-SEL | Transmitted to IEC | [7 empty] | CONTROL2;GAPC6 | ST;IndSys3;stVal;SPS |  | 409<; | None |  |  |  | 411 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 75 |  | SPE_HLa_Reset_Select | SPS | 400kV | B409-ICT-1 | VT SELECTION | 765KV BUS-2 VT | Selected | Reset | BUS-2_VT_SELECT | Transmitted to IEC | [7 empty] | CONTROL2;GAPC6 | ST;IndSys4;stVal;SPS |  | 409<; | None |  |  |  | 412 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 76 |  | SPE_HLa_Reset_Select | SPS | 400kV | B409-ICT-1 | VT SELECTION | LINE | Selected | Reset | LINE_DE-SELECT | Transmitted to IEC | [7 empty] | CONTROL2;GAPC6 | ST;IndSys6;stVal;SPS |  | 409<; | None |  |  |  | 413 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 77 |  | SPE_HLa_Reset_Select | SPS | 400kV | B409-ICT-1 | VT SELECTION | LINE | Selected | Reset | LINE_SELECT | Transmitted to IEC | [7 empty] | CONTROL2;GAPC6 | ST;IndSys5;stVal;SPS |  | 409<; | None |  |  |  | 414 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 78 |  | DP_HLA_CBOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | 7_Z_TE Y POS |  | Open | 7_Z_TE Y POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI9 | ST;DPCSO1;stVal;DPC |  | 382;383;384; | None | [7 empty] | CB |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 79 |  | DP_HLA_CBOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | 7_Z_TE Y POS | Closed |  | 7_Z_TE Y POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI9 | ST;DPCSO1;stVal;DPC |  | 382;383;384; | None | [7 empty] | CB |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 80 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI9 | ST;Pos;stVal;DPC |  | 350;365;366;367;368;369;371;372;373;376;377;378;379;380;381;382;383;384;388;389;390;391;392;393;395;396;397;409; | None |  |  | 100 |  | 399 | Yes |  | CB | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 81 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 52 | POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI9 | ST;Pos;stVal;DPC |  | 350;365;366;367;368;369;371;372;373;376;377;378;379;380;381;382;383;384;388;389;390;391;392;393;395;396;397;409; | None |  |  | 100 |  | 399 | Yes |  | CB | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 82 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89A | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 83 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89A | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 84 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89AE | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL3;CSWI6 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 85 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89AE | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL3;CSWI6 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 86 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89B | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI6 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 87 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89B | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI6 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 88 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89BE | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL3;CSWI4 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 89 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89BE | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL3;CSWI4 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 90 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89T | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;GAPC1 | ST;DPCSO1;stVal;DPC |  | 365; | None | [5 empty] | Yes | [5 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 91 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89T | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;GAPC1 | ST;DPCSO1;stVal;DPC |  | 365; | None | [5 empty] | Yes | [5 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 92 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89T-B | Computed switchgear position |  | Open | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI7 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 93 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89T-B | Computed switchgear position | Closed |  | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI7 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 94 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TE | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL3;CSWI5 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 95 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TE | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL3;CSWI5 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 96 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TE | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL3;XSWI5 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | SwitchPos |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 97 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TE | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL3;XSWI5 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | SwitchPos |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 98 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TE-B | Computed switchgear position |  | Open | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL2;CSWI1 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 99 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TE-B | Computed switchgear position | Closed |  | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL2;CSWI1 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 0 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TE-R | Computed switchgear position |  | Open | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL3;CSWI1 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 101 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TE-R | Computed switchgear position | Closed |  | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL3;CSWI1 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 0 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TE-Y | Computed switchgear position |  | Open | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL3;CSWI2 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 101 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TE-Y | Computed switchgear position | Closed |  | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL3;CSWI2 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 102 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89T-R | Computed switchgear position |  | Open | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI8 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 103 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89T-R | Computed switchgear position | Closed |  | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI8 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 104 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89TS-B | Computed switchgear position |  | Open | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 105 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89TS-B | Computed switchgear position | Closed |  | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 106 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89TS-R | Computed switchgear position |  | Open | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI4 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 107 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89TS-R | Computed switchgear position | Closed |  | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI4 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 108 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TS-RE | Computed switchgear position |  | Open | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL3;CSWI3 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 109 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B409-ICT-1 | 89TS-RE | Computed switchgear position | Closed |  | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL3;CSWI3 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 110 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89TS-Y | Computed switchgear position |  | Open | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI5 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 111 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89TS-Y | Computed switchgear position | Closed |  | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI5 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 112 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89T-Y | Computed switchgear position |  | Open | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 113 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B409-ICT-1 | 89T-Y | Computed switchgear position | Closed |  | OP_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 114 |  | DP_HLa_LocRem_Bay | DPS | 400kV | B409-ICT-1 |  | BCU MODE |  | Local | LC_RM_BCU MODE | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | ST;Loc;origin;DPC |  |  | None |  |  | 109 | [5 empty] | LocRemBay |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 115 |  | DP_HLa_LocRem_Bay | DPS | 400kV | B409-ICT-1 |  | BCU MODE | Remote |  | LC_RM_BCU MODE | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | ST;Loc;origin;DPC |  |  | None |  |  | 109 | [5 empty] | LocRemBay |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 116 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SC_DE_Reset_Set | SPC | 400kV | B409-ICT-1 | CSD | CSD OUT FROM HMI | Set |  | XX_ST_CSD OUT H | Transmitted to IEC | [7 empty] | CONTROL2;GAPC4 | CO;SPCSO1;ctlVal;DPC |  | 400; | [12 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SC_DE_Reset_Set_1 | SPC | 400kV | B409-ICT-1 | PROTECTION | 86A TRIP RELAY | Set |  | XX_RS_86A | Transmitted to IEC | [7 empty] | CONTROL2;GAPC3 | CO;SPCSO1;ctlVal;DPC | [14 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SC_DE_Reset_Set_1 | SPC | 400kV | B409-ICT-1 | PROTECTION | 86B TRIP RELAY | Set |  | XX_RS_86B | Transmitted to IEC | [7 empty] | CONTROL2;GAPC3 | CO;SPCSO2;ctlVal;DPC | [14 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SC_DE_Off_On | SPC | 400kV | B409-ICT-1 | SYNCH FUNCTION | ON/OFF SECONDARY CONTROL SPC | On | Off | OF_ON_ON/OFF SEC | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | CO;EnaSec;ctlVal;DPC | [5 empty] | 201 |  |  |  |  | IntManualCSFct | CS_CtrlOnOff_SPC |  |  | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | DC_DE_LocRem_BayCtrl | DPC | 400kV | B409-ICT-1 |  | BCU MODE |  | Local | LC_RM_BCU MODE | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | CO;Loc;ctlVal;DPC | [5 empty] | 109 | [5 empty] | LocRemBay_DPC |  |  | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | DC_DE_LocRem_BayCtrl | DPC | 400kV | B409-ICT-1 |  | BCU MODE | Remote |  | LC_RM_BCU MODE | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | CO;Loc;ctlVal;DPC | [5 empty] | 109 | [5 empty] | LocRemBay_DPC |  |  | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | MV_HLa_Unused |  | 400kV | B409-ICT-1 | CB_COUNTER | Count_Close | 0.0 | 10000.0 | Count_Close | Transmitted to IEC | [7 empty] | CONTROL4;GAPC1 | MX;AnIn2;mag;MV | [10 empty] | UsrFct | UserFunctionMV |  |  | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | MV_HLa_Unused |  | 400kV | B409-ICT-1 | CB_COUNTER | Count_Open | 0.0 | 10000.0 | Count_Open | Transmitted to IEC | [7 empty] | CONTROL4;GAPC1 | MX;AnIn1;mag;MV | [10 empty] | UsrFct | UserFunctionMV |  |  | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on AC329: HMI Display : Specify if the data appears in HMI.
Note on AD329: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE329: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC348: HMI Display : Specify if the data appears in HMI.
Note on AD348: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE348: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on K452: Arnab Ghosh {अर्नब घोष}: Please clarify if this is in scheme
Note on AC525: HMI Display : Specify if the data appears in HMI.
Note on AD525: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE525: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB545: LCD Display : Specify if the data appears in computer LCD.
Note on AC545: HMI Display : Specify if the data appears in HMI.
Note on AD545: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE545: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## BCU B412_BR
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF! |  |  |  | CCCC
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
MiCOM C264 DESCRIPTION
Keys :
|  |  | Computer Name |  | B412_BR |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | C264 |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 400KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 0
|  |  | Digital Inputs Board Slot |  | P
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | P | 1 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 2 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 3 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 4 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 5 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 6 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 7 | SPE_HLA_Normal_Alarm | SPS | 400kV | B412-BR | 52 | GEN SF6 LOCKOUT | Alarm | Normal | RS_OP_SF6 L/O | Transmitted to IEC | [7 empty] | CONTROL1;XCBR1 | ST;Ind7;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 8 | SPE_HLA_Normal_Alarm | SPS | 400kV | B412-BR | 52 | POLE DISCREPANCY | Alarm | Normal | RS_OP_POLE DISC | Transmitted to IEC | [7 empty] | CONTROL1;XCBR1 | ST;Ind8;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 9 | SPE_HLA_Normal_Alarm | SPS | 400kV | B412-BR | 52 | LOSS OF SF6 GAS POLE A/B/C-1 | Alarm | Normal | NL_AL_LOSS SF6-1 | Transmitted to IEC | [7 empty] | CONTROL1;XCBR1 | ST;Ind9;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 10 | SPE_HLA_Normal_Alarm | SPS | 400kV | B412-BR | 52 | LOSS OF SF6-2 | Alarm | Normal | LOSS OF SF6-2 | Transmitted to IEC | [7 empty] | CONTROL1;XCBR1 | ST;Ind10;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 11 | SPE_HLA_Normal_Alarm | SPS | 400kV | B412-BR | 52 | SF6 LO PRESSURE LOCKOUT | Alarm | Normal | NO_LO_SF6 LO LOW | Transmitted to IEC | [7 empty] | CONTROL1;XCBR1 | ST;Ind11;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 12 | SPE_HLA_Normal_Alarm | SPS | 400kV | B412-BR | 52 | POLE DISCREPANCY | Alarm | Normal | NL_AL_POLE DIS | Transmitted to IEC | [7 empty] | CONTROL1;XCBR1 | ST;Ind12;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 13 | SPE_HLA_Normal_Alarm | SPS | 400kV | B412-BR | 52 | DC SUPPLY-1\2 | Alarm | Normal | NL_FL_DC SUP12 | Transmitted to IEC | [7 empty] | CONTROL1;XCBR1 | ST;Ind13;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 14 | SPE_HLA_Normal_Alarm | SPS | 400kV | B412-BR | 52 | REMOTE POS | Alarm | Normal | RS_ST_REMOTE | Transmitted to IEC | [7 empty] | CONTROL1;XCBR1 | ST;Ind14;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 15 | SPE_HLA_Normal_Alarm | SPS | 400kV | B412-BR | 52 | SPRING CHARGE STATUS B | Alarm | Normal | DS_CH_SPING ST A | Transmitted to IEC | [7 empty] | CONTROL1;XCBR1 | ST;Ind1;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | P | 16 | SPE_HLA_Normal_Alarm | SPS | 400kV | B412-BR | 52 | SPRING CHARGE STATUS A | Alarm | Normal | DS_CH_SPING ST B | Transmitted to IEC | [7 empty] | CONTROL1;XCBR1 | ST;Ind2;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 1
|  |  | Digital Inputs Board Slot |  | O
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | O | 1 | SPE_HLA_Normal_Alarm | SPS | 400kV | B412-BR | 52 | SPRING CHARGE STATUS C | Alarm | Normal | DS_CH_SPING ST C | Transmitted to IEC | [7 empty] | CONTROL1;XCBR1 | ST;Ind4;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 2 | SPE_HLA_Normal_Alarm | SPS | 400kV | B412-BR | 52 | CB TROUBLE-4 | Alarm | Normal | NL_AL_CB TROUBL4 | Transmitted to IEC | [7 empty] | CONTROL1;XCBR1 | ST;Ind3;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 3 | SPE_HLA_Normal_Alarm | SPS | 400kV | B412-BR | 52 | CB TROUBLE-5 | Alarm | Normal | NL_AL_CB TROUBL5 | Transmitted to IEC | [7 empty] | CONTROL1;XCBR1 | ST;Ind6;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 4 | SPE_HLA_Normal_Alarm | SPS | 400kV | B412-BR | 52 | CB TROUBLE-4 | Alarm | Normal | CB TROUBLE-4 | Transmitted to IEC | [7 empty] | CONTROL1;XCBR1 | ST;Ind5;stVal;SPS |  |  | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 5 | DP_HLA_ ISOOpen_Close | DPS | 400kV | B412-BR | 89A | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI1 | ST;Pos;stVal;DPC |  | 446;450;451; | None |  |  | 120 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 6 | DP_HLA_ ISOOpen_Close | DPS | 400kV | B412-BR | 89A | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL1;XSWI1 | ST;Pos;stVal;DPC |  | 446;450;451; | None |  |  | 120 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 7 | DP_HLa_ESOpen_Close | DPS | 400kV | B412-BR | 89AE | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI5 | ST;Pos;stVal;DPC |  | 443;444;445;447;448;449; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 8 | DP_HLa_ESOpen_Close | DPS | 400kV | B412-BR | 89AE | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI5 | ST;Pos;stVal;DPC |  | 443;444;445;447;448;449; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 9 | DP_HLA_ ISOOpen_Close | DPS | 400kV | B412-BR | 89B | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI1 | ST;Pos;stVal;DPC |  | 446;450; | None |  |  | 121 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 10 | DP_HLA_ ISOOpen_Close | DPS | 400kV | B412-BR | 89B | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI1 | ST;Pos;stVal;DPC |  | 446;450; | None |  |  | 121 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 11 | DP_HLa_ESOpen_Close | DPS | 400kV | B412-BR | 89BE | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI3 | ST;Pos;stVal;DPC |  | 443;444;445;447;448;449; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 12 | DP_HLa_ESOpen_Close | DPS | 400kV | B412-BR | 89BE | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI3 | ST;Pos;stVal;DPC |  | 443;444;445;447;448;449; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 13 | DP_HLA_ ISOOpen_Close | DPS | 400kV | B412-BR | 89R | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI2 | ST;Pos;stVal;DPC |  | 454; | None |  |  | 122 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 14 | DP_HLA_ ISOOpen_Close | DPS | 400kV | B412-BR | 89R | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI2 | ST;Pos;stVal;DPC |  | 454; | None |  |  | 122 |  |  |  |  | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 15 | DP_HLa_ESOpen_Close | DPS | 400kV | B412-BR | 89RE | POSITION |  | Open | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI6 | ST;Pos;stVal;DPC |  | 451;452;453; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | O | 16 | DP_HLa_ESOpen_Close | DPS | 400kV | B412-BR | 89RE | POSITION | Closed |  | OE_CL_POS | Transmitted to IEC | [7 empty] | CONTROL2;XSWI6 | ST;Pos;stVal;DPC |  | 451;452;453; | None | [7 empty] | SG | SwitchPos |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 2
|  |  | Digital Inputs Board Slot |  | N
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | N | 1 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 2 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 3 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 4 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 5 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 6 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | -7 | SPE_HLA_Normal_Fail | SPS | 400kV | B412-BR | PROTECTION | DC SOURCE-1 | Fail | Normal | NL_FL_DC SOURCE1 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind4;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | -8 | SPE_HLA_Normal_Fail | SPS | 400kV | B412-BR | PROTECTION | DC SOURCE-2 | Fail | Normal | NL_FL_DC SOURCE2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind3;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | -9 | SPE_HLA_Healthy_Flty | SPS | 400kV | B412-BR | PROTECTION | CB TRIP COIL-2 | Faulty | Healthy | HL_FT_CB TC1 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind2;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | -10 | SPE_HLA_Healthy_Flty | SPS | 400kV | B412-BR | PROTECTION | CB TRIP COIL-2 | Faulty | Healthy | HL_FT_CB TC2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | ST;Ind1;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 11 | DP_HLA_Trip_Closed | DPS | 400kV | B412-BR | 52 | EMERGENCY/MANUAL | Closed |  | TP_CL_EMRG/MAN | Transmitted to IEC | [7 empty] | CONTROL1;XCBR1 | ST;DPCSO1;stVal;DPC |  | 457; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 12 | DP_HLA_Trip_Closed | DPS | 400kV | B412-BR | 52 | EMERGENCY/MANUAL |  | Trip | TP_CL_EMRG/MAN | Transmitted to IEC | [7 empty] | CONTROL1;XCBR1 | ST;DPCSO1;stVal;DPC |  | 457; | None | [7 empty] | CB |  |  |  | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 13 | SPE_HLA_Normal_Alarm | SPS | 400kV | B412-BR | CSD | CSD DEVICE NOT READY | Alarm | Normal | NL_AL_CSD NR | Transmitted to IEC | [7 empty] | CONTROL1;GGIO2 | ST;Ind2;stVal;SPS |  | 456; | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 14 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 15 | SPE_HLA_Normal_Alarm | SPS | 400kV | B412-BR | CSD | CSD | Alarm | Normal | NL_AL_CSD | Transmitted to IEC | [7 empty] | CONTROL1;GGIO2 | ST;Ind3;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | N | 16 | SPE_HLa_In_Out | SPS | 400kV | B412-BR | CSD | CSD | In | Out | IN_OT_CSD | Transmitted to IEC | [7 empty] | CONTROL1;GGIO2 | ST;Ind1;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 3
|  |  | Digital Inputs Board Slot |  | M
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | M | 1 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 2 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 3 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 4 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 5 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 6 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 7 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 8 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 9 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 10 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 11 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 12 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 13 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 14 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 15 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | M | 16 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL INPUT BOARD DIU2xx
|  |  | Digital Inputs Board Number |  | 4
|  |  | Digital Inputs Board Slot |  | L
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | L | 1 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 2 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 3 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 4 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 5 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 6 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 7 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 8 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 9 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 10 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 11 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 12 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 13 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 14 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 15 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  | L | 16 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 0
|  |  | Digital Outputs Board Slot |  | E
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | E | 1 | DC_SBO_Open_Close | DPC | 400kV | B412-BR | 52 | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI8 | CO;Pos;sboClass;DPC | [5 empty] | 119 |  |  | NO |  | CB | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 2 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 3 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 4 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 5 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 6 | SC_DE_Reset_Set | SPC | 400kV | B412-BR | CSD | CSD BYPASS | Set |  | XX_XX_CSD BYPASS | Transmitted to IEC | [7 empty] | CONTROL1;GGIO2 | CO;SPCSO1;ctlVal;DPC | [6 empty] | 513 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 7 | DC_SBO_Open_Close | DPC | 400kV | B412-BR | 52 | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI8 | CO;Pos;sboClass;DPC | [5 empty] | 119 |  |  | NO |  | CB | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 8 | SC_DE_Reset_Set_1 | SPC | 400kV | B412-BR | PROTECTION | CB CLOSE TO PUA | Set |  | XX_XX_CB CLS PUA | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO4;ctlVal;DPC | [6 empty] | 244 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 9 | SC_DE_Reset_Set_1 | SPC | 400kV | B412-BR | PROTECTION | CB CLOSE TO PUB | Set |  | XX_XX_CB CLS PUB | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO5;ctlVal;DPC | [6 empty] | 243 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | E | 10 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 1
|  |  | Digital Outputs Board Slot |  | F
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | F | 1 | DC_SBO_Open_Close | DPC | 400kV | B412-BR | 89B | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | CO;Pos;sboClass;DPC | [5 empty] | 121 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 2 | DC_SBO_Open_Close | DPC | 400kV | B412-BR | 89B | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | CO;Pos;sboClass;DPC | [5 empty] | 121 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 3 | SC_DE_NotPerm_Perm | SPC | 400kV | B412-BR | IL PERMISSIVE | 89B I/L PERMISSIVE |  |  | XX_XX_89B | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | CO;SPCSO2;ctlVal;DPC | [6 empty] | 509 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 4 | SC_DE_NotPerm_Perm | SPC | 400kV | B412-BR | IL PERMISSIVE | 89BE I/L PERMISSIVE |  |  | XX_XX_89BE | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | CO;SPCSO4;ctlVal;DPC | [6 empty] | 510 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 5 | DC_SBO_Open_Close | DPC | 400kV | B412-BR | 89A | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | CO;Pos;sboClass;DPC | [5 empty] | 120 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 6 | DC_SBO_Open_Close | DPC | 400kV | B412-BR | 89A | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | CO;Pos;sboClass;DPC | [5 empty] | 120 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 7 | SC_DE_NotPerm_Perm | SPC | 400kV | B412-BR | IL PERMISSIVE | 89A I/L PERMISSIVE |  |  | XX_XX_89A | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | CO;SPCSO1;ctlVal;DPC | [6 empty] | 507 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 8 | SC_DE_NotPerm_Perm | SPC | 400kV | B412-BR | IL PERMISSIVE | 89AE I/L PERMISSIVE |  |  | XX_XX_89AE | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | CO;SPCSO7;ctlVal;DPC | [6 empty] | 508 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 9 | SC_DE_NotPerm_Perm | SPC | 400kV | B412-BR | IL PERMISSIVE | 89AE1 I/L PERMISSIVE |  |  | XX_XX_89AE1 | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | CO;SPCSO6;ctlVal;DPC | [8 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | F | 10 | SC_DE_Reset_Set_1 | SPC | 400kV | B412-BR | PROTECTION | TO CB TC-2 CKT | Set |  | XX_XX_TC2 | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO2;ctlVal;DPC | [8 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 2
|  |  | Digital Outputs Board Slot |  | G
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | G | 1 | DC_SBO_Open_Close_2 | DPC | 400kV | B412-BR | 89R | CONTROL |  | Open | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI6 | CO;Pos;sboClass;DPC | [5 empty] | 122 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 2 | DC_SBO_Open_Close_2 | DPC | 400kV | B412-BR | 89R | CONTROL | Close |  | OE_CL_CONTROL | Transmitted to IEC | [7 empty] | CONTROL1;CSWI6 | CO;Pos;sboClass;DPC | [5 empty] | 122 |  |  | NO |  | SG | Switch_DPC |  |  | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 3 | SC_DE_NotPerm_Perm | SPC | 400kV | B412-BR | IL PERMISSIVE | 89BR I/L PERMISSIVE |  |  | XX_XX_89BR | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | CO;SPCSO3;ctlVal;DPC | [6 empty] | 511 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 4 | SC_DE_NotPerm_Perm | SPC | 400kV | B412-BR | IL PERMISSIVE | 89BRE I/L PERMISSIVE |  |  | XX_XX_89BRE | Transmitted to IEC | [7 empty] | CONTROL2;GGIO1 | CO;SPCSO5;ctlVal;DPC | [6 empty] | 512 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 5 | SC_DE_Reset_Set_1 | SPC | 400kV | B412-BR | PROTECTION | 86A TRIP RELAY | Set |  | XX_RS_86A | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO1;ctlVal;DPC | [8 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 6 | SC_DE_Reset_Set_1 | SPC | 400kV | B412-BR | PROTECTION | 86B TRIP RELAY | Set |  | XX_RS_86B | Transmitted to IEC | [7 empty] | CONTROL1;GGIO1 | CO;SPCSO3;ctlVal;DPC | [8 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 7 | SC_DE_Reset_Reset_2 | SPC | 400kV | B412-BR | VT SELECTION | 400KV BUS-2 SELECT | Reset |  | XX_XX_400KV B2 S | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO1;ctlVal;DPC | [6 empty] | 517 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 8 | SC_DE_Reset_Reset_2 | SPC | 400kV | B412-BR | VT SELECTION | 400KV BUS-2 DESELECT | Reset |  | XX_XX_400KV B2 D | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO2;ctlVal;DPC | [6 empty] | 516 |  | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 9 | SC_DE_Reset_Reset_2 | SPC | 400kV | B412-BR | VT SELECTION | 400KV BUS-1 SELECT | Reset |  | XX_XX_400KV B1 S | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO3;ctlVal;DPC | [6 empty] | 515 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | G | 10 | SC_DE_Reset_Reset_2 | SPC | 400kV | B412-BR | VT SELECTION | 400KV BUS-1 DESELECT | Reset |  | XX_XX_400KV B1 D | Transmitted to IEC | [7 empty] | CONTROL2;GGIO2 | CO;SPCSO4;ctlVal;DPC | [6 empty] | 514 |  | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 3
|  |  | Digital Outputs Board Slot |  | H
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | H | 1 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 2 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 3 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 4 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 5 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 6 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 7 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 8 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 9 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | H | 10 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 4
|  |  | Digital Outputs Board Slot |  | I
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | I | 1 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 2 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 3 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 4 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 5 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 6 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 7 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 8 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 9 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | I | 10 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL OUTPUT BOARD DOU20x
|  |  | Digital Outputs Board Number |  | 5
|  |  | Digital Outputs Board Slot |  | J
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | J | 1 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 2 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 3 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 4 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 5 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 6 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 7 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 8 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 9 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  | J | 10 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
ANALOG INPUT BOARD AIU21x
|  |  | Analog Input Board Number |  | 0
|  |  | Analog Input Board Slot |  | D
Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Channel | Transducer Type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 | 4/20 mA | MV_hla_ AuxVoltage_2 | V | 400kV | B412-BR | REACTOR MB | OTI HI ALM | 0.0 | 150.0 | OTI HI ALM | Transmitted to IEC | [7 empty] | CONTROL2;GGIO3 | MX;AnIn1;mag;MV | [14 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 2 | 4/20 mA | MV_hla_ AuxVoltage_2 | V | 400kV | B412-BR | REACTOR MB | OTI HI TRIP | 0.0 | 150.0 | OTI HI TRIP | Transmitted to IEC | [7 empty] | CONTROL2;GGIO3 | MX;AnIn2;mag;MV | [14 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 3 | 4/20 mA | MV_hla_ AuxVoltage_2 | V | 400kV | B412-BR | REACTOR MB | WTI HI ALM | 0.0 | 150.0 | WTI HI ALM | Transmitted to IEC | [7 empty] | CONTROL2;GGIO3 | MX;AnIn3;mag;MV | [14 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 4 | 4/20 mA | MV_HLa_AuxCurrent_2 | A | 400kV | B412-BR | REACTOR MB | WTI HI TRIP | 0.0 | 150.0 | WTI HI TRIP | Transmitted to IEC | [7 empty] | CONTROL2;GGIO3 | MX;AnIn4;mag;MV | [14 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 5 | 4/20 mA | MV_hla_Temp | ˚ Cel | 400kV | B412-BR | REACTOR MB | AC KIOSK TEMP | 0.0 | 100.0 | AC KIOSK TEMP | Transmitted to IEC | [7 empty] | CONTROL2;GGIO3 | MX;AnIn5;mag;MV | [14 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 6 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 7 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 8 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
CT/VT ANALOG INPUT BOARD TMU2x0
|  |  | CT/VT Board Number |  | 0
|  |  | CT/VT Board Slot |  | Q
|  |  | CT/VT Board Model |  | TMU220
CT acquisition
VT acquisition
|  |  | Nominal Current |  | 1 | (1A/5A)
|  |  | Nominal Voltage |  | 110 | [1V … 500V]
Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Input type (U/I) |  | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | DF |  | MV_HLa_Frequency_1 | Hz | 400kV | B412-BR | SYNCH DATA | FREQUENCY DIFFERENCE | 0.0 | 2.0 | FREQUENCY DIFF | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | MX;DifHzClc;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | DV |  | MV_hla_ AuxVoltage_1 | V | 400kV | B412-BR | SYNCH DATA | VOLTAGE DIFFERENCE | 0.0 | 277.13626 | VOLTAGE DIFF | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | MX;DifVClc;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Dj |  | MV_hla_PhaseDiff | ˚ | 400kV | B412-BR | SYNCH DATA | PHASE DIFFERENCE | 0.0 | 360.0 | PHASE ANGLE DIFF | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | MX;DifAngClc;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ia |  | MV_HLa_AuxCurrent | A | 400kV | B412-BR | METERING | I-R PHASE CURRENT | 0.0 | 2400.0 | IR PHASE CURRENT | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;A;phsA;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ib |  | MV_HLa_AuxCurrent | A | 400kV | B412-BR | METERING | I-Y PHASE CURRENT | 0.0 | 2400.0 | IY PHASE CURRENT | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;A;phsB;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ic |  | MV_HLa_AuxCurrent | A | 400kV | B412-BR | METERING | I-B PHASE CURRENT | 0.0 | 2400.0 | IB PHASE CURRENT | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;A;phsC;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Vb |  | MV_hla_ AuxVoltage_1 | V | 400kV | B412-BR | SYNCH DATA | INCOMING SUPPLY | 0.0 | 277.13626 | INCOMING SUPPLY | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU2 | MX;PhV;phsB;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Uab |  | MV_hla_ AuxVoltage | V | 400kV | B412-BR | METERING | R-Y VOLTAGE | 0.0 | 480.0 | R-Y VOLTAGE | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;PPV;phsAB;DELTA | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ubc |  | MV_HLa_Voltage | kV | 400kV | B412-BR | METERING | Y-B VOLTAGE | 0.0 | 480.0 | Y-B VOLTAGE | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;PPV;phsBC;DELTA | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Uca |  | MV_HLa_Voltage | kV | 400kV | B412-BR | METERING | B-R VOLTAGE | 0.0 | 480.0 | B-R VOLTAGE | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;PPV;phsCA;DELTA | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Vbusbar |  | MV_hla_ AuxVoltage_1 | V | 400kV | B412-BR | SYNCH DATA | RUNNING SUPPLY | 0.0 | 277.13626 | RUNNING SPLY-1 | Transmitted to IEC | [7 empty] | MEASUREMENT1;barMMXU1 | MX;PhV;phsA;WYE | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Freq (Line) |  | MV_HLa_Frequency | Hz | 400kV | B412-BR | METERING | FREQUENCY | 45.0 | 55.0 | FREQUENCY | Transmitted to IEC | [7 empty] | MEASUREMENT1;rmsMMXU1 | MX;Hz;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | P total (MW) |  | MV_HLa_ActPower | MW | 400kV | B412-BR | METERING | ACTIVE POWER | -1662.72 | 1662.72 | ACTIVE POWER | Transmitted to IEC | [7 empty] | MEASUREMENT1;powMMXU1 | MX;TotW;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Q total (Mvar) |  | MV_HLa_ActPower | MW | 400kV | B412-BR | METERING | REACTIVE POWER | -1662.72 | 1662.72 | REACTIVE POWER | Transmitted to IEC | [7 empty] | MEASUREMENT1;powMMXU1 | MX;TotVAr;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | cos ft : Power factor |  | MV_HLa_PowerFactor |  | 400kV | B412-BR | METERING | POWER FACTOR | -1.2 | 1.2 | POWER FACTOR | Transmitted to IEC | [7 empty] | MEASUREMENT1;powMMXU1 | MX;TotPF;mag;MV | [14 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  |  |  | SPARE | [32 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  |  |  | SPARE | [32 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B412-BR | 52 ¦ OE_CL_CONTROL | OPEN INTERLOCK | Permissive | Not Permissive | NP_PE_OPEN ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO4 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | CB | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | 52 ¦ OE_CL_CONTROL | OPEN ORDER | Set | Reset | RS_ST_OPN ORD | Transmitted to IEC | [7 empty] | CONTROL1;CSWI8 | ST;OpnOrd;general;general;ACT |  |  | None | [7 empty] | CB | OpenOrderSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B412-BR | 89A ¦ OE_CL_CONTROL | OPEN INTERLOCK | Permissive | Not Permissive | NP_PE_OPN ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO1 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | SG | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B412-BR | 89B ¦ OE_CL_CONTROL | OPEN INTERLOCK | Permissive | Not Permissive | NP_PE_OPN ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO2 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | SG | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B412-BR | 89R ¦ OE_CL_CONTROL | Open/raise interlock result SPS | Permissive | Not Permissive | Open/raise intlk | Transmitted to IEC | [7 empty] | CONTROL2;CILO3 | ST;EnaOpn;stVal;SPS |  |  | None | [7 empty] | SG | OpenIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPS_hla_Set_Reset | SPS | 400kV | B412-BR |  | ORDER RUNNING ON THE BAY | Set | Reset | RS_ST_ORD RUNING | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | ST;OrdRun;stVal;SPS |  |  | None | [8 empty] | OrderInProgress |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B412-BR | 52 ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | NP_PE_CLOSE ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO4 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | CB | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B412-BR | 89A ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | NP_PE_CLS ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO1 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | SG | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B412-BR | 89B ¦ OE_CL_CONTROL | CLOSE INTERLOCK | Permissive | Not Permissive | NP_PE_CLS ILK | Transmitted to IEC | [7 empty] | CONTROL2;CILO2 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | SG | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B412-BR | 89R ¦ OE_CL_CONTROL | Close/lower interlock result SPS | Permissive | Not Permissive | Close/low. intlk | Transmitted to IEC | [7 empty] | CONTROL2;CILO3 | ST;EnaCls;stVal;SPS |  |  | None | [7 empty] | SG | CloseIntlkSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | SYNCH FUNCTION | CLOSE ORDER | Set | Reset | RS_ST_CLS ODR | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;ClsOpSt;stVal;SPS |  |  | None | [7 empty] | IntManualCSFct | CS_CloseOrderState_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPE_HLA_on_off | SPS | 400kV | B412-BR | SYNCH FUNCTION | ON/OFF SECONDARY SPS | Off | On | RS_ST_ON/OFF SEC | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;EnaSec;origin;SPC |  |  | None |  |  | 204 |  |  |  |  | IntManualCSFct | CS_OnOff_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | SYNCH FUNCTION | POSSIBLE CLOSING | Set | Reset | RS_ST_POS CLS | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;Rel;stVal;SPS |  | 458; | None | [7 empty] | IntManualCSFct | CS_AuthoState_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | SYNCH FUNCTION | PRESENCE OF REFERENCE VOLTAGE | Set | Reset | RS_ST_REF U PRES | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;VRefInd;stVal;SPS |  | 458; | None | [7 empty] | IntManualCSFct | CS_VoltageRefPresence_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | SYNCH FUNCTION | ABSENCE OF REFERENCE VOLTAGE | Set | Reset | RS_ST_REF. U ABS | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;VRefAbs;stVal;SPS |  | 458; | None | [7 empty] | IntManualCSFct | CS_VoltageRefAbsence_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | SYNCH FUNCTION | VOLT ABSENCE | Set | Reset | RS_ST_VOLT ABS | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;VAbs;stVal;SPS |  | 458; | None | [7 empty] | IntManualCSFct | CS_VoltageAbsence_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 17 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | SYNCH FUNCTION | VOLT PRESENCE | Set | Reset | RS_ST_VOLT PRES | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | ST;VP;stVal;SPS |  | 458; | None | [7 empty] | IntManualCSFct | CS_VoltagePresence_SPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 18 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B412-BR | 52 ¦ OE_CL_CONTROL | CLOSE ORDER | Permissive | Not Permissive | RS_ST_CLS ORD | Transmitted to IEC | [7 empty] | CONTROL1;CSWI8 | ST;ClsOrd;general;general;ACT |  | 457; | None |  |  |  | 243;244 |  |  |  | CB | CloseOrderSPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 19 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B412-BR | 89A | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | ST;IndSys1;stVal;SPS |  | 443<; | None |  |  |  | 507 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 20 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B412-BR | 89AE | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL1;CSWI5 | ST;IndSys1;stVal;SPS |  | 446<; | None |  |  |  | 508 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 21 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B412-BR | 89B | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | ST;IndSys1;stVal;SPS |  | 447<; | None |  |  |  | 509 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 22 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B412-BR | 89BE | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | ST;IndSys1;stVal;SPS |  | 450<; | None |  |  |  | 510 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 23 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B412-BR | 89R | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL1;CSWI6 | ST;IndSys1;stVal;SPS |  | 451<; | None |  |  |  | 511 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 24 |  | SPE_HLa_Notper_Perm | SPS | 400kV | B412-BR | 89RE | IL PERMISSIVE | Permissive | Not Permissive | NP_PE_I/L PERM | Transmitted to IEC | [7 empty] | CONTROL1;CSWI7 | ST;IndSys1;stVal;SPS |  | 454<; | None |  |  |  | 512 |  |  |  | SG |  |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 25 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | CSD | CSD BYPASS | Set | Reset | RS_ST_CSD BYPASS | Transmitted to IEC | [7 empty] | CONTROL1;GAPC4 | ST;IndSys1;stVal;SPS |  | 456<; | None |  |  |  | 513 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 26 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | PROTECTION | SOTF TO RELAY | Set | Reset | RS_ST_SOTF TO RL | Transmitted to IEC | [7 empty] | CONTROL1;GAPC2 | ST;IndSys1;stVal;SPS |  | 457<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 27 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | SYNCH DATA | CLOSE PERMISSIVE | Set | Reset | RS_ST_CB CLOSE | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | ST;IndSys5;stVal;SPS |  | 458<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 28 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | SYNCH DATA | DEAD INCOMING DEAD RUNNING | Set | Reset | RS_ST_DINC_DRUN | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | ST;IndSys4;stVal;SPS |  | 458<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 29 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | SYNCH DATA | DEAD INCOMING LIVE RUNNING | Set | Reset | RS_ST_DINC_LRUN | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | ST;IndSys3;stVal;SPS |  | 458<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 30 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | SYNCH DATA | LIVE INCOMING DEAD RUNNING | Set | Reset | RS_ST_LINC_DRUN | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | ST;IndSys2;stVal;SPS |  | 458<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 31 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | SYNCH DATA | LIVE INCOMING LIVE RUNNING | Set | Reset | RS_ST_LINC_LRUN | Transmitted to IEC | [7 empty] | CONTROL1;GAPC1 | ST;IndSys1;stVal;SPS |  | 458<; | None | [11 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 32 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | VT SELECTION | 400KV BUS-1 DESELECT | Set | Reset | RS_ST_400KV B1 D | Transmitted to IEC | [7 empty] | CONTROL1;GAPC3 | ST;IndSys3;stVal;SPS |  | 460<; | None |  |  |  | 514 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 33 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | VT SELECTION | 400KV BUS-1 SELECT | Set | Reset | RS_ST_400KV B1 S | Transmitted to IEC | [7 empty] | CONTROL1;GAPC3 | ST;IndSys1;stVal;SPS |  | 460<; | None |  |  |  | 515 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 34 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | VT SELECTION | 400KV BUS-2 DESELECT | Set | Reset | RS_ST_400KV B2 D | Transmitted to IEC | [7 empty] | CONTROL1;GAPC3 | ST;IndSys4;stVal;SPS |  | 460<; | None |  |  |  | 516 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 35 |  | SPE_HLa_Reset_Set | SPS | 400kV | B412-BR | VT SELECTION | 400KV BUS-2 SELECT | Set | Reset | RS_ST_400KV B2 S | Transmitted to IEC | [7 empty] | CONTROL1;GAPC3 | ST;IndSys2;stVal;SPS |  | 460<; | None |  |  |  | 517 | [7 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 36 |  | DP_HLA_CBOpen_Close | DPS | 400kV | B412-BR | 52 | POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI8 | ST;Pos;stVal;DPC |  | 426;441;442;443;444;445;447;448;449;452;453;460; | None |  |  | 119 |  | 455 | Yes |  | CB | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 37 |  | DP_HLA_CBOpen_Close | DPS | 400kV | B412-BR | 52 | POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI8 | ST;Pos;stVal;DPC |  | 426;441;442;443;444;445;447;448;449;452;453;460; | None |  |  | 119 |  | 455 | Yes |  | CB | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 38 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B412-BR | 89A | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 39 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B412-BR | 89A | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI1 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 40 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B412-BR | 89AE | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI5 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 41 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B412-BR | 89AE | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI5 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 42 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B412-BR | 89B | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 43 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B412-BR | 89B | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI2 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 44 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B412-BR | 89BE | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 45 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B412-BR | 89BE | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI3 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 46 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B412-BR | 89R | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI6 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 47 |  | DP_HLA_ ISOOpen_Close | DPS | 400kV | B412-BR | 89R | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI6 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 48 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B412-BR | 89RE | COMP. POSITION |  | Open | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI7 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 49 |  | DP_HLa_ESOpen_Close | DPS | 400kV | B412-BR | 89RE | COMP. POSITION | Closed |  | OE_CL_COMP_POS | Transmitted to IEC | [7 empty] | CONTROL1;CSWI7 | ST;Pos;stVal;DPC |  |  | None | [7 empty] | SG | ComputedSwitchPos_DPS |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 50 |  | DP_HLa_LocRem_Bay | DPS | 400kV | B412-BR |  | BCU MODE |  | Local | LC_RM_BCU MODE | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | ST;Loc;origin;DPC |  |  | None |  |  | 123 | [5 empty] | LocRemBay |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 51 |  | DP_HLa_LocRem_Bay | DPS | 400kV | B412-BR |  | BCU MODE | Remote |  | LC_RM_BCU MODE | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | ST;Loc;origin;DPC |  |  | None |  |  | 123 | [5 empty] | LocRemBay |  |  | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 52 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SC_DE_Off_On | SPC | 400kV | B412-BR | SYNCH FUNCTION | ON/OFF SECONDARY CONTROL SPC | On | Off | OF_ON_ON/OFF SEC | Transmitted to IEC | [7 empty] | CONTROL1;RSYN1 | CO;EnaSec;ctlVal;DPC | [5 empty] | 204 |  |  |  |  | IntManualCSFct | CS_CtrlOnOff_SPC |  |  | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SC_DE_Reset_Set | SPC | 400kV | B412-BR | CSD | CSD OUT FROM HMI | Set |  | XX_ST_CSD OUT H | Transmitted to IEC | [7 empty] | CONTROL1;GAPC4 | CO;SPCSO1;ctlVal;DPC |  | 456; | [12 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | DC_DE_LocRem_BayCtrl | DPC | 400kV | B412-BR |  | BCU MODE |  | Local | LC_RM_BCU MODE | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | CO;Loc;ctlVal;DPC | [5 empty] | 123 | [5 empty] | LocRemBay_DPC |  |  | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | DC_DE_LocRem_BayCtrl | DPC | 400kV | B412-BR |  | BCU MODE | Remote |  | LC_RM_BCU MODE | Transmitted to IEC | [7 empty] | CONTROL1;GBAY1 | CO;Loc;ctlVal;DPC | [5 empty] | 123 | [5 empty] | LocRemBay_DPC |  |  | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | MV_HLa_Unused |  | 400kV | B412-BR | CB_COUNTER | Count_Close | 0.0 | 10000.0 | Count_Close | Transmitted to IEC | [7 empty] | CONTROL2;GAPC1 | MX;AnIn2;mag;MV | [10 empty] | UsrFct | UserFunctionMV |  |  | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | MV_HLa_Unused |  | 400kV | B412-BR | CB_COUNTER | Count_Open | 0.0 | 10000.0 | Count_Open | Transmitted to IEC | [7 empty] | CONTROL2;GAPC1 | MX;AnIn1;mag;MV | [10 empty] | UsrFct | UserFunctionMV |  |  | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on AC226: HMI Display : Specify if the data appears in HMI.
Note on AD226: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE226: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC245: HMI Display : Specify if the data appears in HMI.
Note on AD245: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE245: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC356: HMI Display : Specify if the data appears in HMI.
Note on AD356: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE356: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB376: LCD Display : Specify if the data appears in computer LCD.
Note on AC376: HMI Display : Specify if the data appears in HMI.
Note on AD376: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE376: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## Time Synch
PATH | SIGNAL | IEC ADDRESS
Scs ¦ Ethernet network ¦ System Group ¦ B401_LINE | TIME SYNCHRONISATION ERROR | Scs ¦ Ethernet network ¦ System Group ¦ B401_LINE ¦ C26x IEC Map. ¦ SYSTEM ¦ C26xLDIA1 ¦ ST ¦ SyncSt
Scs ¦ Ethernet network ¦ System Group ¦ B402_TIE | TIME SYNCHRONISATION ERROR | Scs ¦ Ethernet network ¦ System Group ¦ B402_TIE ¦ C26x IEC Map. ¦ SYSTEM ¦ C26xLDIA1 ¦ ST ¦ SyncSt
Scs ¦ Ethernet network ¦ System Group ¦ B403_FUT | TIME SYNCHRONISATION ERROR | Scs ¦ Ethernet network ¦ System Group ¦ B403_FUT ¦ C26x IEC Map. ¦ SYSTEM ¦ C26xLDIA1 ¦ ST ¦ SyncSt
Scs ¦ Ethernet network ¦ System Group ¦ B407_AT | TIME SYNCHRONISATION ERROR | Scs ¦ Ethernet network ¦ System Group ¦ B407_AT ¦ C26x IEC Map. ¦ SYSTEM ¦ C26xLDIA1 ¦ ST ¦ SyncSt
Scs ¦ Ethernet network ¦ System Group ¦ B409_ICT1 | TIME SYNCHRONISATION ERROR | Scs ¦ Ethernet network ¦ System Group ¦ B409_ICT1 ¦ C26x IEC Map. ¦ SYSTEM ¦ C26xLDIA1 ¦ ST ¦ SyncSt
Scs ¦ Ethernet network ¦ System Group ¦ B412_BR | TIME SYNCHRONISATION ERROR | Scs ¦ Ethernet network ¦ System Group ¦ B412_BR¦ C26x IEC Map. ¦ SYSTEM ¦ C26xLDIA1 ¦ ST ¦ SyncSt

## Goose
PATH | PROFILE | SIGNAL | IEC ADDRESS
B401-LINE¦ PROTECTION ¦NL_AL_GOOSE RECP | 46 : SPE_HLA_Normal_Alarm | GOOSE RECEIPT FAIL/TROUBLE | CONTROL2; | GAPC2 ST; IndSys2
B402-TIE ¦ PROTECTION ¦NL_AL_GOOSE RECP | 46 : SPE_HLA_Normal_Alarm | GOOSE RECEIPT FAIL/TROUBLE | CONTROL2; | GAPC2 ST; IndSys2
B407-AT ¦ PROTECTION ¦NL_AL_GOOSE RECP | 46 : SPE_HLA_Normal_Alarm | GOOSE RECEIPT FAIL/TROUBLE | CONTROL2; | GAPC2 ST; IndSys2
B409-ICT-1 ¦ PROTECTION ¦NL_AL_GOOSE RECP | 46 : SPE_HLA_Normal_Alarm | GOOSE RECEIPT FAIL/TROUBLE | CONTROL2; | GAPC2 ST; IndSys2
B412-BR ¦ PROTECTION ¦NL_AL_GOOSE RECP | 46 : SPE_HLA_Normal_Alarm | GOOSE RECEIPT FAIL/TROUBLE | CONTROL2; | GAPC2 ST; IndSys2

## IEC R407_P442_67 HV
Designation : |  |  | Project Name | [30 empty] | Symbol : |  | SAM-DTL-DS Agile-4.3.3.0 |  |  |  | ACAC
Issue : |  |  | A | [30 empty] | Ref : |  | PROJECTNAME-Xnn-DTL
Date : |  |  | 0 | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | BHADLA
IEC Description
Keys :
|  |  | Computer Name |  | R707_P442_21R |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 765KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R707_P442_21R
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 765kV | R407_P442_21/67 | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  | System;GosGGIO2 | ST;Ind1;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 765kV | R707_P442_21R | GOOSE | 86A TRIP RELAY | Alarm | Reset | RS_OP_86A | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind1;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind2;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 765kV | R707_P442_21R | GOOSE | 86B TRIP RELAY | Alarm | Reset | RS_OP_86B | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind2;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind3;stVal;SPS | SPE_HLa_Reset_Set | SPS | 765kV | R707_P442_21R | GOOSE | BB | Alarm | Reset | RS_ST_BB | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind3;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 765kV | R407_P442_21/67 | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | Protection;PTRC1 | ST;Tr;general;ACT | SPE_HLA_Reset_Optd | SPS | 765kV | R407_P442_21/67 | PROTECTION | GENERAL TRIP | Operated | Reset | RS_OP_GEN TRIP | Transmitted to IEC | [7 empty] | Protection;PTRC1 | ST;Tr;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;OcpEI1PTOC1 | ST;Op;phsA;general;ACT | SPE_HLA_Reset_Optd | SPS | 765kV | R407_P442_21/67 | PROTECTION | HV OVER CURRENT R-PH TRIP | Operated | Reset | RS_OP_HV O/C R | Transmitted to IEC | [7 empty] | Protection;OcpPTOC1 | ST;Op;phsA;general;ACT |  |  | None | [11 empty] | 1 | 0
A |  |  | Protection;OcpEI1PTOC1 | ST;Op;phsB;general;ACT | SPE_HLA_Reset_Optd | SPS | 765kV | R407_P442_21/67 | PROTECTION | HV OVER CURRENT Y-PH TRIP | Operated | Reset | RS_OP_HV O/C Y | Transmitted to IEC | [7 empty] | Protection;OcpPTOC1 | ST;Op;phsB;general;ACT |  |  | None | [11 empty] | 1 | 0
A |  |  | Protection;OcpEI1PTOC1 | ST;Op;phsC;general;ACT | SPE_HLA_Reset_Optd | SPS | 765kV | R407_P442_21/67 | PROTECTION | HV OVER CURRENT B-PH TRIP | Operated | Reset | RS_OP_HV O/C B | Transmitted to IEC | [7 empty] | Protection;OcpPTOC1 | ST;Op;phsC;general;ACT |  |  | None | [11 empty] | 1 | 0
A |  |  | Protection;OcpEI1PTOC1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 765kV | R407_P442_21/67 | PROTECTION | HV OVER CURRENT TRIP | Operated | Reset | RS_OP_HV O/C | Transmitted to IEC | [7 empty] | Protection;OcpPTOC1 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | 0
A |  |  | Protection;OcpEI1PTOC1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 765kV | R407_P442_21/67 | PROTECTION | HV OVER CURRENT START | Set | Reset | RS_OP_HV O/C S | Transmitted to IEC | [7 empty] | Protection;OcpPTOC1 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | 0
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | #REF!
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | R707_P442_21R
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS | 765kV | R407_P442_21/67 | PROTECTION | DIRECTIONAL EARTH FAULT START | Set | Reset | RS_ST_E/F_S | [8 empty] | Protection;EfdPTOC1 | ST;Op;phsC;general;ACD | [14 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPS | 765kV | R407_P442_21/67 | PROTECTION | DIRECTIONAL EARTH FAULT TRIP | Operated | Reset | RS_ST_E/F | [8 empty] | Protection;EfdPTOC1 | ST;Op;phsC;general;ACT | [14 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | R707_P442_21R
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R707_P442_21R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R707_P442_21R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R707_P442_21R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R707_P442_21R
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | R707_P442_21R
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R707_P442_21R
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | R707_P442_21R
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R707_P442_21R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R707_P442_21R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R707_P442_21R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R707_P442_21R
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on X24: Arnab Ghosh {अर्नब घोष}: Why is Ind4 used instead of Ind1
Note on D35: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E35: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D49: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E49: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC49: HMI Display : Specify if the data appears in HMI.
Note on AD49: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE49: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D57: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E57: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D63: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E63: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB63: LCD Display : Specify if the data appears in computer LCD.
Note on AC63: HMI Display : Specify if the data appears in HMI.
Note on AD63: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE63: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC126: HMI Display : Specify if the data appears in HMI.
Note on AD126: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE126: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB146: LCD Display : Specify if the data appears in computer LCD.
Note on AC146: HMI Display : Specify if the data appears in HMI.
Note on AD146: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE146: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## IEC R407_P442_67 LV
Designation : |  |  | Project Name | [30 empty] | Symbol : |  | SAM-DTL-DS Agile-4.3.3.0 |  |  |  | ACAC
Issue : |  |  | A | [30 empty] | Ref : |  | PROJECTNAME-Xnn-DTL
Date : |  |  | 0 | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | BHADLA
IEC Description
Keys :
|  |  | Computer Name |  | R707_P442_21R |  |  |  |  | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) |  | IEC |  |  |  |  | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
|  |  | SCADA 1 | 765KV SERVER M | 1
SCADA 2
SCADA 3
SCADA 4
|  |  | IED NAME : |  | R707_P442_21R
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | System;LLN0 | ST;SyncSt;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 765kV | R712_P442_21/67 | PROTECTION | TIME SYNCHRONISATION ERROR | Alarm | Normal | NL_AL_TIME SYNC | Transmitted to IEC | [7 empty] | System;LLN0 | ST;SyncSt;stVal;SPS |  |  | None | [11 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  | System;GosGGIO2 | ST;Ind1;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 765kV | R707_P442_21R | GOOSE | 86A TRIP RELAY | Alarm | Reset | RS_OP_86A | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind1;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind2;stVal;SPS | SPE_HLA_Reset_Optd | SPS | 765kV | R707_P442_21R | GOOSE | 86B TRIP RELAY | Alarm | Reset | RS_OP_86B | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind2;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind3;stVal;SPS | SPE_HLa_Reset_Set | SPS | 765kV | R707_P442_21R | GOOSE | BB | Alarm | Reset | RS_ST_BB | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind3;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | System;GosGGIO2 | ST;Ind4;stVal;SPS | SPE_HLA_Normal_Alarm | SPS | 765kV | R712_P442_21/67 | PROTECTION | GOOSE RECEIPT FAIL/TROUBLE | Alarm | Normal | NL_AL_GOOSE RECP | Transmitted to IEC | [7 empty] | System;GosGGIO2 | ST;Ind4;stVal;SPS |  |  | None | [5 empty] | Yes | [5 empty] | 1 | #REF!
A |  |  | Protection;PTRC1 | ST;Tr;general;ACT | SPE_HLA_Reset_Optd | SPS | 765kV | R712_P442_21/67 | PROTECTION | GENERAL TRIP | Operated | Reset | RS_OP_GEN TRIP | Transmitted to IEC | [7 empty] | Protection;PTRC1 | ST;Tr;general;ACT |  |  | None | [11 empty] | 1 | #REF!
A |  |  | Protection;OcpEI1PTOC1 | ST;Op;phsA;general;ACT | SPE_HLA_Reset_Optd | SPS | 765kV | R712_P442_21/67 | PROTECTION | LV OVER CURRENT R-PH TRIP | Operated | Reset | RS_OP_HV O/C R | Transmitted to IEC | [7 empty] | Protection;OcpPTOC1 | ST;Op;phsA;general;ACT |  |  | None | [11 empty] | 1 | 0
A |  |  | Protection;OcpEI1PTOC1 | ST;Op;phsB;general;ACT | SPE_HLA_Reset_Optd | SPS | 765kV | R712_P442_21/67 | PROTECTION | LV OVER CURRENT Y-PH TRIP | Operated | Reset | RS_OP_HV O/C Y | Transmitted to IEC | [7 empty] | Protection;OcpPTOC1 | ST;Op;phsB;general;ACT |  |  | None | [11 empty] | 1 | 0
A |  |  | Protection;OcpEI1PTOC1 | ST;Op;phsC;general;ACT | SPE_HLA_Reset_Optd | SPS | 765kV | R712_P442_21/67 | PROTECTION | LV OVER CURRENT B-PH TRIP | Operated | Reset | RS_OP_HV O/C B | Transmitted to IEC | [7 empty] | Protection;OcpPTOC1 | ST;Op;phsC;general;ACT |  |  | None | [11 empty] | 1 | 0
A |  |  | Protection;OcpEI1PTOC1 | ST;Op;general;general;ACT | SPE_HLA_Reset_Optd | SPS | 765kV | R712_P442_21/67 | PROTECTION | LV OVER CURRENT TRIP | Operated | Reset | RS_OP_HV O/C | Transmitted to IEC | [7 empty] | Protection;OcpPTOC1 | ST;Op;general;general;ACT |  |  | None | [11 empty] | 1 | 0
A |  |  | Protection;OcpEI1PTOC1 | ST;Str;general;general;ACD | SPE_HLA_Reset_Optd | SPS | 765kV | R712_P442_21/67 | PROTECTION | LV OVER CURRENT START | Set | Reset | RS_OP_HV O/C S | Transmitted to IEC | [7 empty] | Protection;OcpPTOC1 | ST;Str;general;general;ACD |  |  | None | [11 empty] | 1 | 0
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | #REF!
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name | R707_P442_21R
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS | 765kV | R407_P442_21/67 | PROTECTION | DIRECTIONAL EARTH FAULT START | Set | Reset | RS_ST_E/F_S | [8 empty] | Protection;EfdPTOC1 | ST;Op;phsC;general;ACD | [14 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPS | 765kV | R407_P442_21/67 | PROTECTION | DIRECTIONAL EARTH FAULT TRIP | Operated | Reset | RS_ST_E/F | [8 empty] | Protection;EfdPTOC1 | ST;Op;phsC;general;ACT | [14 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name R707_P442_21R
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name | R707_P442_21R
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R707_P442_21R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R707_P442_21R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R707_P442_21R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name R707_P442_21R
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name | R707_P442_21R
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R707_P442_21R
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name R707_P442_21R
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name | R707_P442_21R
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R707_P442_21R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R707_P442_21R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R707_P442_21R
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name R707_P442_21R
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on X24: Arnab Ghosh {अर्नब घोष}: Why is Ind4 used instead of Ind1
Note on D35: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E35: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D49: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E49: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC49: HMI Display : Specify if the data appears in HMI.
Note on AD49: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE49: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D57: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E57: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D63: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E63: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB63: LCD Display : Specify if the data appears in computer LCD.
Note on AC63: HMI Display : Specify if the data appears in HMI.
Note on AD63: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE63: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC126: HMI Display : Specify if the data appears in HMI.
Note on AD126: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE126: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB146: LCD Display : Specify if the data appears in computer LCD.
Note on AC146: HMI Display : Specify if the data appears in HMI.
Note on AD146: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE146: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## SystemInformation_Template (hidden)
Designation : |  | #REF! | [22 empty] | Symbol : |  | #REF!
Issue : |  | #REF! | [22 empty] | Ref : |  | #REF!
Date : |  | #REF! | [5 empty] | Substation Automation | [16 empty] | Data Of : |  | #REF!
SYSTEM INFORMATION DATA DESCRIPTION
|  |  |  | Gateway | Port used (on gateway) |  | Keys :
|  |  | SCADA 1 |  |  |  | GE Reserved
|  |  | SCADA 2 |  |  |  | Auto generated
|  |  | SCADA 3 |  |  |  | Read Only
|  |  | SCADA 4 |  |  |  | ERROR
SYSTEM INFORMATION SERVER OI
SERVER OI Name :
Iss. | Electrical Data |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special | Automation |  | Template | Conf. Mng.
Issue | Equipment Link | Function | Type | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used | Datapoint Name (in SCE Template) | Process | Comments
|  | Sp0000 | SPS | AGENCY STATUS | HEALTHY | FAULTY | Agency status | [21 empty] | 40 | SYSTEM INFORMATION SERVER OI | AgencyStatus
|  | Sp0000 | SPS | AUTOMATIC ARCHIVING STATUS | HEALTHY | FAULTY | Auto archiving | [21 empty] | 40 | SYSTEM INFORMATION SERVER OI | AutomaticArchiving
|  | Mp0000OIHist | MPS | HISTORIAN DATABASE STATUS |  |  | Central archive | [21 empty] | 40 | SYSTEM INFORMATION SERVER OI | CentralArchiving
|  | Sp0000 | SPS | OI SBUS LINK | HEALTHY | FAULTY | Device link | [21 empty] | 40 | SYSTEM INFORMATION SERVER OI | CommDevice
|  | Sp0H00 | SPS | SBUS ACQUISITION STATUS | HEALTHY | FAULTY | IEC Coupling | [21 empty] | 40 | SYSTEM INFORMATION SERVER OI | CouplingStatus
|  | Sp0H00 | SPS | LOGGING QUEUE STATUS | HEALTHY | FAULTY | Log Queue | [21 empty] | 40 | SYSTEM INFORMATION SERVER OI | LogQueue
|  | Mp0HLAOpMod | MPS | OPERATING MODE |  |  | Operating mode | [21 empty] | 40 | SYSTEM INFORMATION SERVER OI | OperatingMode
|  | Sp0H00 | SPS | REDUNDANCY MODE | ACTIVE | STANDBY | Redundancy mode | [21 empty] | 40 | SYSTEM INFORMATION SERVER OI | RedDevice
|  | Mp0HLAOpMod | MPS | REDUNDANCY STATUS |  |  | Redundancy status | [19 empty] | No |  | 40 | SYSTEM INFORMATION SERVER OI | RedundancyStatus
|  | Sp0H00 | SPS | SYNCHRONIZATION STATUS | HEALTHY | FAULTY | Synchronisation | [21 empty] | 40 | SYSTEM INFORMATION SERVER OI | SyncDevice
| OI printer | Mp0HLAOIPrt | MPS | PRINTER STATUS |  |  | Printer status | [21 empty] | 40 | SYSTEM INFORMATION SERVER OI | Printing
| OI printer | Mp0HLAOIPrt | MPS | BACKUP PRINTER STATUS |  |  | BackupPrint stat | [19 empty] | No |  | 40 | SYSTEM INFORMATION SERVER OI | BackupPrinting
SYSTEM INFORMATION CLIENT OI
CLIENT OI Name :
Iss. | Electrical Data |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special | Automation |  | Template | Conf. Mng.
Issue | Equipment Link | Function | Type | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used | Datapoint Name (in SCE Template) | Process | Comments
|  | Sp0HLARev | SPS | CONNECTION STATUS | HEALTHY | FAULTY | OI client link | [21 empty] | 41 | SYSTEM INFORMATION CLIENT OI | CommS2K_C
SYSTEM INFORMATION MiCOM C264
MiCOM C264 Name :
Iss. | Electrical Data |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special | Automation |  | Template | Conf. Mng.
Issue | Equipment Link | Function | Type | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used | Datapoint Name (in SCE Template) | Process | Comments
|  | Sp0000 | SPS | DATABASE INCONSISTENCY | YES | NO | DB incoh. SPS | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | DBIncoherency
|  | ScD000Pul | SPC | C264 DATABASE SWITCHING | EXECUTE | - | DB switch ctrl | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | DBSwitch_SPC
|  | Sp0000 | SPS | C264 SBUS LINK | HEALTHY | FAULTY | Device link | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | CommDevice
|  | Sp0000 | SPS | DIGITAL INPUT ACQUISITION | FAULTY | HEALTHY | DI acq stopped | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | DIAcquisitionStopped
|  | DcD000Pul | DPC | C264 BAYS CONTROL MODE CHANGE | REMOTE | LOCAL | Loc/rem ctrl DPC | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | LocRemDevice_DPC
|  | Dp0000 | DPS | C264 MANAGED BAYS IN CONTROL MODE | REMOTE | LOCAL | Local/remote DPS | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | LocRemDevice
|  | Sp0HL0 | SPS | C264 BAYS IN CONTROL MODE | REMOTE | LOCAL | Local/remote SPS | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | LocRemDeviceForIEC
|  | Mv0000Mst | MV | C264 FAULT LEVEL FOR REDUNDANCY |  |  | Main status MV | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | MainInternalStatus
|  | DcD000Pul | DPC | C264 FORCE OPERATION MODE TO | OPERATIONNAL | MAINTENANCE | Mode control DPC | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | ModeDevice_DPC
|  | Mp0HLAOpMod | MPS | C264 OPERATING MODE |  |  | Operating mode | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | OperatingMode
|  | ScD000Pul | SPC | C264 BIU REDUNDANCY RELAY CO 2 | ACTIVATE | DEACTIVATE | Red mode ctrl | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | RedChangeMode_SPC
|  | ScD000Pul | SPC | C264 BIU REDUNDANCY RELAY CO 1 | ACTIVATE | DEACTIVATE | Red Status ctrl | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | RedChangeStatus_SPC
|  | Sp0HL0 | SPS | REDUNDANT C264 CHANGE MODE | ACTIVE | STANDBY | Red. change mode | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | RedChangeMode
|  | Sp0HL0 | SPS | REDUNDANT C264 STATUS | ACTIVE | STANDBY | Red. change stat | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | RedChangeStatus
|  | Sp0000 | SPS | SOFTWARE ERROR DETECTED | YES | NO | Soft. error SPS | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | SoftError
|  | Sp0H00 | SPS | C264 SYNCHRONIZATION STATUS | HEALTHY | FAULTY | Synchronisation | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | SyncDevice
|  | DcD000Pul | DPC | C264 CHANGE EXPLOITATION MODE | NORMAL | TEST | Test control DPC | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | TestDevice_DPC
|  | Sp0000 | SPS | C264 WATCHDOG RELAY STATUS | HEALTHY | FAULTY | Watchdog SPS | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | WatchdogError
|  | Dp0000OpM | DPS | C264 OPERATING MODE | RUNNING | MAINTENANCE | Device mode | [19 empty] | No |  | 42 | SYSTEM INFORMATION MiCOM C264 | ModeDevice
|  | Sp0H00 | SPS | DISTURBANCE FILE ON C264 | READY | NOT READY | DREC ready | [19 empty] | No |  | 42 | SYSTEM INFORMATION MiCOM C264 | DisturbUCA2
|  | Sp0000 | SPS | C264 COUNTERS ACQUISITION TOP | YES | NO | Counter Top | [19 empty] | No |  | 42 | SYSTEM INFORMATION MiCOM C264 | CounterTop
|  | Sp0HLARev | SPS | GPS SYNCHRONISATION SOURCE | HEALTHY | FAULTY | Ext clock status | [19 empty] | No |  | 42 | SYSTEM INFORMATION MiCOM C264 | ExtClockStatus
|  | Sp0HL0 | SPS | C264 REDUNDANCY MODE | ACTIVE | STANDBY | Redundancy mode | [19 empty] | No |  | 42 | SYSTEM INFORMATION MiCOM C264 | RedDevice
|  | Sp0HL0 | SPS | REPORT BUFFER OVERFLOW GTW 1 | YES | NO | Buff Ov Gtw 1 | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264
|  | Sp0HL0 | SPS | REPORT BUFFER OVERFLOW GTW 2 | YES | NO | Buff Ov Gtw 2
|  | Sp0HL0 | SPS | REPORT BUFFER OVERFLOW OI | YES | NO | Buff Ov OI
|  | Sp0HL0 | SPS | REPORT BUFFER OVERFLOW OI BACKUP | YES | NO | Buff Ov OI Bck
|  | Sp0HL0 | SPS | ALL AIU STATUS | FAULTY | HEALTHY | All AIU status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | GlobalAIUStatus
|  | Sp0HL0 | SPS | ALL AOU STATUS | FAULTY | HEALTHY | All AOU status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | GlobalAOUStatus
|  | Sp0HL0 | SPS | ALL CCU STATUS | FAULTY | HEALTHY | All CCU status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | GlobalCCUStatus
|  | Sp0HL0 | SPS | ALL DIU STATUS | FAULTY | HEALTHY | All DIU status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | GlobalDIUStatus
|  | Sp0HL0 | SPS | ALL DOU STATUS | FAULTY | HEALTHY | All DOU status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | GlobalDOUStatus
|  | Sp0HL0 | SPS | ALL TMU STATUS | FAULTY | HEALTHY | All TMU status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | GlobalTMUStatus
|  | Sp0HL0 | SPS | ALL HBU STATUS | FAULTY | HEALTHY | All HBU status
|  | Sp0HL0 | SPS | ALL IED STATUS | FAULTY | HEALTHY | All IED status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | GlobalIEDStatus
|  | Sp0HL0 | SPS | ALL Printer STATUS | FAULTY | HEALTHY | All Printer stat | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | GlobalPrinterStatus
|  | Sp0HL0 | SPS | ALL RACK STATUS | FAULTY | HEALTHY | All rack status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | GlobalRackLinkStatus
|  | Sp0HL0 | SPS | LOCAL ALARM ACKNOWLEDGEMENT | YES | NO | Local alarm ack | [19 empty] | No |  | 42 | SYSTEM INFORMATION MiCOM C264 | LocalAlarmAck_SPS
|  | Sp0HL0 | SPS | SETTING DONE | YES | NO | Setting done | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | SettingDone
|  | Sp0HL0 | SPS | SETTING FILE DISCORDANCE | YES | NO | Setting disc. | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | SettingFileDiscordance
|  | Sp0HL0 | SPS | SETTING IN PROGRESS | YES | NO | Setting in prog. | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | SettingInProgress
|  | Sp0HL0 | SPS | SETTING INCOHERENCY | YES | NO | Setting incoher. | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | SettingIncoherency
| BoardBIU | Mp0HLABoard | MPS | BIU BOARD STATUS |  |  | BIU status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | BIUStatus
| BoardGHU | Mp0HLABoard | MPS | GHU BOARD STATUS |  |  | GHU status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | GHUStatus
| BoardAIU201 | Mp0HLABoard | MPS | AIU20x BOARD STATUS |  |  | AIU status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | AIUStatus
| BoardAIU210 | Mp0HLABoard | MPS | AIU20x BOARD STATUS |  |  | AIU status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | AIUStatus
| BoardAOU200 | Mp0HLABoard | MPS | AOU200 BOARD STATUS |  |  | AOU status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | AOUStatus
| BoardDIU | Mp0HLABoard | MPS | DIU BOARD STATUS |  |  | DIU status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | DIUStatus
| BoardDOU | Mp0HLABoard | MPS | DOU BOARD STATUS |  |  | DOU status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | DOUStatus
| BoardCCU | Mp0HLABoard | MPS | CCU BOARD STATUS |  |  | CCU status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | CCUStatus
| BoardTMU | Mp0HLABoard | MPS | TMU BOARD STATUS |  |  | TMU status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | TIUStatus
| BoardHBU | Mp0HLABoard | MPS | HBU BOARD STATUS |  |  | HBU status
| IED | Sp0HLARev | SPS | IED CONNECTION STATUS TO C264 | HEALTHY | FAULTY | IED SPS com. | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | CommIED
| IED | Sp0H00 | SPS | IED SYNCHRONISATION STATUS | HEALTHY | FAULTY | IED SPS Synchro. | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | SyncIED
| IED | Sp0000 | SPS | IED DISTURBANCE FILE | READY | NOT READY | IED DREC ready | [19 empty] | No |  | 42 | SYSTEM INFORMATION MiCOM C264 | DisturbIED
| RackLink | Dp0000OpM | DPS | RACK LINK STATUS | HEALTHY | FAULTY | Rack link status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | RackLinkStatus
| PLC Isagraph | Mp0HLAIsag | MPS | ISAGRAF STATUS |  |  | ISAGRAF status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | ISAGRAFStatus
| BoardPrinter | Dp0000OpM | DPS | PRINTER STATUS DPS |  |  | Printer st. DPS | [19 empty] | No |  | 42 | SYSTEM INFORMATION MiCOM C264 | PrinterStatus
| BoardPrinter | Mp0HLAOIPrt | MPS | LOCAL PRINTER STATUS |  |  | Printer Status | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | Printing
| SCADA | Sp0H00 | SPS | C264 SCADA PORT COMMUNICATION | ACTIVE | STANDBY | Redundancy SPS | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | RedSCADA
| SCADA | Sp0HLARev | SPS | SCADA CONNECTION STATUS TO C264 | HEALTHY | FAULTY | SCADA SPS com. | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | CommSCADA
SYSTEM INFORMATION MiCOM C364
MiCOM C364 Name :
Iss. | Electrical Data |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special | Automation |  | Template | Conf. Mng.
Issue | Equipment Link | Function | Type | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used | Datapoint Name (in SCE Template) | Process | Comments
|  | Sp0000 | SPS | DATABASE INCONSISTENCY | YES | NO | DB incoh. SPS | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | DBIncoherency
|  | ScD000Pul | SPC | C364 DATABASE SWITCHING | EXECUTE | - | DB switch ctrl | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | DBSwitch_SPC
|  | Sp0000 | SPS | C364 SBUS LINK | HEALTHY | FAULTY | Device link | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | CommDevice
|  | DcD000Pul | DPC | C364 BAYS CONTROL MODE CHANGE | REMOTE | LOCAL | Loc/rem ctrl DPC | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | LocRemDevice_DPC
|  | Dp0000 | DPS | C364 MANAGED BAYS IN CONTROL MODE | REMOTE | LOCAL | Local/remote DPS | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | LocRemDevice
|  | Sp0HL0 | SPS | C364 BAYS IN CONTROL MODE | REMOTE | LOCAL | Local/remote SPS | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | LocRemDeviceForIEC
|  | Sp0H00 | SPS | LOGGING QUEUE STATUS | HEALTHY | FAULTY | Log Queue | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | LogQueue
|  | DcD000Pul | DPC | C364 FORCE OPERATION MODE TO | OPERATIONNAL | MAINTENANCE | Mode control DPC | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | ModeDevice_DPC
|  | Mp0HLAOpMod | MPS | C364 OPERATING MODE |  |  | Operating mode | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | OperatingMode
|  | Sp0000 | SPS | SOFTWARE ERROR DETECTED | YES | NO | Soft. error SPS | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | SoftError
|  | Sp0H00 | SPS | C364 SYNCHRONIZATION STATUS | HEALTHY | FAULTY | Synchronisation | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | SyncDevice
|  | DcD000Pul | DPC | C364 CHANGE EXPLOITATION MODE | NORMAL | TEST | Test control DPC | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | TestDevice_DPC
|  | Sp0000 | SPS | C364 WATCHDOG RELAY STATUS | HEALTHY | FAULTY | Watchdog SPS | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | WatchdogError
|  | Dp0000OpM | DPS | C364 OPERATING MODE | RUNNING | MAINTENANCE | Device mode | [19 empty] | No |  | 43 | SYSTEM INFORMATION MiCOM C364 | ModeDevice
|  | Sp0HLARev | SPS | GPS SYNCHRONISATION SOURCE | HEALTHY | FAULTY | Ext clock status | [19 empty] | No |  | 43 | SYSTEM INFORMATION MiCOM C364 | ExtClockStatus
|  | Sp0HL0 | SPS | C364 REDUNDANCY MODE | ACTIVE | STANDBY | Redundancy mode | [19 empty] | No |  | 43 | SYSTEM INFORMATION MiCOM C364 | RedDevice
| IED | Sp0HLARev | SPS | IED CONNECTION STATUS TO C364 | HEALTHY | FAULTY | IED SPS com. | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | CommIED
| IED | Sp0H00 | SPS | IED SYNCHRONISATION STATUS | HEALTHY | FAULTY | IED SPS Synchro. | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | SyncIED
| IED | Sp0000 | SPS | IED DISTURBANCE FILE | READY | NOT READY | IED DREC ready | [19 empty] | No |  | 43 | SYSTEM INFORMATION MiCOM C364 | DisturbIED
| PLC Isagraph | Mp0HLAIsag | MPS | ISAGRAF STATUS |  |  | ISAGRAF status | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | ISAGRAFStatus
| SCADA | Sp0H00 | SPS | C364 SCADA PORT COMMUNICATION | ACTIVE | STANDBY | Redundancy SPS | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | RedSCADA
| SCADA | Sp0HLARev | SPS | SCADA CONNECTION STATUS TO C364 | HEALTHY | FAULTY | SCADA SPS com. | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | CommSCADA
SYSTEM INFORMATION UCA2 IED
UCA2 IED Name :
Iss. | Electrical Data |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special | Automation |  | Template | Conf. Mng.
Issue | Equipment Link | Function | Type | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used | Datapoint Name (in SCE Template) | Process | Comments
|  | Sp0HLARev | SPS | IED SBUS LINK | HEALTHY | FAULTY | Device link | [21 empty] | 44 | SYSTEM INFORMATION UCA2 IED | CommDevice
SYSTEM INFORMATION GATEWAY
GATEWAY Name :
Iss. | Electrical Data |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special | Automation |  | Template | Conf. Mng.
Issue | Equipment Link | Function | Type | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used | Datapoint Name (in SCE Template) | Process | Comments
|  | ScD000Pul | SPC | GTW DATABASE SWITCHING | EXECUTE | - | DB switch ctrl | [21 empty] | 45 | SYSTEM INFORMATION GATEWAY | DBSwitch_SPC
|  | Sp0000 | SPS | GTW SBUS LINK | HEALTHY | FAULTY | Device link | [21 empty] | 45 | SYSTEM INFORMATION GATEWAY | CommDevice
|  | DcD000Pul | DPC | GTW FORCE OPERATION MODE TO | OPERATIONNAL | MAINTENANCE | Mode control DPC | [21 empty] | 45 | SYSTEM INFORMATION GATEWAY | ModeDevice_DPC
|  | Mp0HLAOpMod | MPS | GTW OPERATING MODE |  |  | Operating mode | [21 empty] | 45 | SYSTEM INFORMATION GATEWAY | OperatingMode
|  | Sp0H00 | SPS | GTW SYNCHRONISATION STATUS | HEALTHY | FAULTY | Synchronisation | [21 empty] | 45 | SYSTEM INFORMATION GATEWAY | SyncDevice
| SCADA | Sp0H00 | SPS | GTW SCADA PORT COMMUNICATION | ACTIVE | STANDBY | Redundancy SPS | [21 empty] | 45 | SYSTEM INFORMATION GATEWAY | RedSCADA
| SCADA | Sp0HLARev | SPS | SCADA CONNECTION STATUS TO GTW | HEALTHY | FAULTY | SCADA SPS com. | [21 empty] | 45 | SYSTEM INFORMATION GATEWAY | CommSCADA
| IED | Sp0HLARev | SPS | IED CONNECTION STATUS TO GTW | HEALTHY | FAULTY | IED SPS com. | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | CommIED
| IED | Sp0H00 | SPS | IED SYNCHRONISATION STATUS | HEALTHY | FAULTY | IED SPS Synchro. | [21 empty] | 42 | SYSTEM INFORMATION MiCOM C264 | SyncIED
| PLC Isagraph | Mp0HLAIsag | MPS | ISAGRAF STATUS |  |  | ISAGRAF status | [21 empty] | 43 | SYSTEM INFORMATION MiCOM C364 | ISAGRAFStatus_GTW
SYSTEM INFORMATION IEC 61850
IEC 61850 Name :
Iss. | Electrical Data |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special | Automation |  | Template | Conf. Mng.
Issue | Equipment Link | Function | Type | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used | Datapoint Name (in SCE Template) | Process | Comments
|  | Sp0HLARev | SPS | IED SBUS LINK | HEALTHY | FAULTY | Device link | [21 empty] | 46 | SYSTEM INFORMATION IEC 61850 | CommDevice
|  | Mp0HLAOpMod | MPS | IED OPERATING MODE |  |  | Operating mode | [19 empty] | No |  | 46 | SYSTEM INFORMATION IEC 61850 | OperatingMode
|  | DcD000Pul | DPC | IED FORCE OPERATION MODE TO | OPERATIONNAL | MAINTENANCE | Mode control DPC | [19 empty] | No |  | 46 | SYSTEM INFORMATION IEC 61850 | ModeDevice_DPC
|  | Sp0H00 | SPS | REDUNDANCY MODE | ACTIVE | STANDBY | Redundancy mode | [19 empty] | No |  | 46 | SYSTEM INFORMATION IEC 61850 | RedDevice
|  | Sp0H00 | SPS | DISTURBANCE FILE ON IED | READY | NOT READY | DREC ready | [19 empty] | No |  | 46 | SYSTEM INFORMATION IEC 61850 | DisturbUCA2
|  | Sp0H00 | SPS | LOGICAL DEVICE DISTURBANCE FILE | READY | NOT READY | LD DREC ready | [19 empty] | No |  | 46 | SYSTEM INFORMATION IEC 61850 | DisturbLD
|  | Sp0000 | SPS | IEC61850 GENERIC SPS | HEALTHY | FAULTY | IEC61850 gen SPS | [19 empty] | No |  | 46 | SYSTEM INFORMATION IEC 61850 | UCA2GenSPS
|  | Dp0000 | DPS | IEC61850 GENERIC DPS | HEALTHY | FAULTY | IEC61850 gen DPS | [19 empty] | No |  | 46 | SYSTEM INFORMATION IEC 61850 | UCA2GenDPS
|  | Mp0000OIHist | MPS | IEC61850 GENERIC MPS |  |  | IEC61850 gen MPS | [19 empty] | No |  | 46 | SYSTEM INFORMATION IEC 61850 | UCA2GenMPS
|  | ScD000Pul | SPC | IEC61850 GENERIC SPC | HEALTHY | FAULTY | IEC61850 gen SPC | [19 empty] | No |  | 46 | SYSTEM INFORMATION IEC 61850 | UCA2GenSPC
|  | DcD000Pul | DPC | IEC61850 GENERIC DPC | HEALTHY | FAULTY | IEC61850 gen DPC | [19 empty] | No |  | 46 | SYSTEM INFORMATION IEC 61850 | UCA2GenDPC
|  | Mv0000Mst | MV | IEC61850 GENERIC MV |  |  | IEC61850 gen MV | [19 empty] | No |  | 46 | SYSTEM INFORMATION IEC 61850 | UCA2GenMV
SYSTEM INFORMATION BAY OI
BAY OI Name :
Iss. | Electrical Data |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special | Automation |  | Template | Conf. Mng.
Issue | Equipment Link | Function | Type | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used | Datapoint Name (in SCE Template) | Process | Comments
|  | Sp0000 | SPS | AGENCY STATUS | HEALTHY | FAULTY | Agency status | [21 empty] | 47 | SYSTEM INFORMATION BAY OI | AgencyStatus
|  | Sp0000 | SPS | AUTOMATIC ARCHIVING STATUS | HEALTHY | FAULTY | Auto archiving | [21 empty] | 47 | SYSTEM INFORMATION BAY OI | AutomaticArchiving
|  | Mp0000OIHist | MPS | HISTORIAN DATABASE STATUS |  |  | Central archive | [21 empty] | 47 | SYSTEM INFORMATION BAY OI | CentralArchiving
|  | Sp0000 | SPS | OI SBUS LINK | HEALTHY | FAULTY | Device link | [21 empty] | 47 | SYSTEM INFORMATION BAY OI | CommDevice
|  | Sp0H00 | SPS | SBUS ACQUISITION STATUS | HEALTHY | FAULTY | IEC Coupling | [21 empty] | 47 | SYSTEM INFORMATION BAY OI | CouplingStatus
|  | Sp0H00 | SPS | LOGGING QUEUE STATUS | HEALTHY | FAULTY | Log Queue | [21 empty] | 47 | SYSTEM INFORMATION BAY OI | LogQueue
|  | Sp0HLARev | SPS | CONNECTION STATUS | HEALTHY | FAULTY | OI client link | [21 empty] | 47 | SYSTEM INFORMATION BAY OI | CommS2K_C
|  | Mp0HLAOpMod | MPS | OPERATING MODE |  |  | Operating mode | [21 empty] | 47 | SYSTEM INFORMATION BAY OI | OperatingMode
|  | Sp0H00 | SPS | REDUNDANCY MODE | ACTIVE | STANDBY | Redundancy mode | [21 empty] | 47 | SYSTEM INFORMATION BAY OI | RedDevice
|  | Sp0H00 | SPS | SYNCHRONIZATION STATUS | HEALTHY | FAULTY | Synchronisation | [21 empty] | 47 | SYSTEM INFORMATION BAY OI | SyncDevice
END OF DATA
| Français |  |  | English |  |  | Spanish |  |  | Português Brasil |  |  | Russian |  |  | German
First column to begin translation is column 5
SYSTEM INFORMATION SERVER OI |  |  |  | SYSTEM INFORMATION SERVER OI |  |  | SYSTEM INFORMATION SERVER OI |  |  | SYSTEM INFORMATION SERVER OI |  |  | SYSTEM INFORMATION SERVER OI |  |  | SYSTEM INFORMATION SERVER OI
| 1 ¦ AgencyStatus |  |  | 1 ¦ AgencyStatus |  |  | 1 ¦ AgencyStatus |  |  | 1 ¦ AgencyStatus |  |  | 1 ¦ AgencyStatus |  |  | 1 ¦ AgencyStatus
| ETAT DE L'AGENCE |  |  | AGENCY STATUS |  |  | ESTADO AGENCY |  |  | ESTADO DA AGENCY IEC |  |  | СТАТУС ДРАЙВЕРА |  |  | AGENCY STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Etat de l'agence |  |  | Agency status |  |  | Estado Agency |  |  | Estado Agency |  |  | Статус драйвера |  |  | Agency status
| 1 ¦ AutomaticArchiving |  |  | 1 ¦ AutomaticArchiving |  |  | 1 ¦ AutomaticArchiving |  |  | 1 ¦ AutomaticArchiving |  |  | 1 ¦ AutomaticArchiving |  |  | 1 ¦ AutomaticArchiving
| ETAT DE L'ARCHIVAGE AUTOMATIQUE |  |  | AUTOMATIC ARCHIVING STATUS |  |  | ESTADO ARCHIVO AUTOMATICO |  |  | ESTADO DO ARQUIVO AUTOMATICO |  |  | СТАТУС АВТОМАТИЧЕСКОЙ АРХИВАЦИИ |  |  | AUTOMATIC ARCHIVING STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Archivage Auto |  |  | Auto archiving |  |  | Archivo Auto |  |  | Arquivo Auto |  |  | Авто архивация |  |  | Auto archiving
| 1 ¦ CentralArchiving |  |  | 1 ¦ CentralArchiving |  |  | 1 ¦ CentralArchiving |  |  | 1 ¦ CentralArchiving |  |  | 1 ¦ CentralArchiving |  |  | 1 ¦ CentralArchiving
| ETAT DE LA BD HISTORIAN |  |  | HISTORIAN DATABASE STATUS |  |  | ESTADO BASE DE DATOS HISTORIAN |  |  | ESTADO BASE DE DADOS HISTORIAN |  |  | Статус БД Историк |  |  | HISTORIAN DATABASE STATUS
| Archive Centrale |  |  | Central archive |  |  | Archivo Central |  |  | Archivo Central |  |  | Центр. архив |  |  | Central archive
| 1 ¦ CommDevice |  |  | 1 ¦ CommDevice |  |  | 1 ¦ CommDevice |  |  | 1 ¦ CommDevice |  |  | 1 ¦ CommDevice |  |  | 1 ¦ CommDevice
| ETAT DU LIEN SBUS |  |  | OI SBUS LINK |  |  | ENLACE OI SBUS |  |  | ESTADO DA CONEXAO SBUS |  |  | СОЕДИНЕНИЕ OI и SBUS |  |  | OI SBUS LINK
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Lien SBUS |  |  | Device link |  |  | Enlace SBUS |  |  | Conexao SBUS |  |  | Связь устройств. |  |  | Device link
| 1 ¦ LogQueue |  |  | 1 ¦ LogQueue |  |  | 1 ¦ LogQueue |  |  | 1 ¦ LogQueue |  |  | 1 ¦ LogQueue |  |  | 1 ¦ LogQueue
| ETAT DE LA FILE D'IMPRESSION |  |  | LOGGING QUEUE STATUS |  |  | ESTADO COLA DE EVENTOS |  |  | ESTADO DA FILA DE EVENTOS |  |  | СНЯТИЕ ПОКАЗАНИЯ СТАТУСА ОЧЕРЕДИ |  |  | LOGGING QUEUE STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| File impression |  |  | Log Queue |  |  | Cola de Eventos |  |  | Fila de Eventos |  |  | Лог очереди |  |  | Log Queue
| 1 ¦ OperatingMode |  |  | 1 ¦ OperatingMode |  |  | 1 ¦ OperatingMode |  |  | 1 ¦ OperatingMode |  |  | 1 ¦ OperatingMode |  |  | 1 ¦ OperatingMode
| MODE OPERATIONNEL |  |  | OPERATING MODE |  |  | MODO OPERACIONAL |  |  | MODO DE OPERACAO |  |  | РЕЖИМ РАБОТЫ |  |  | OPERATING MODE
| Mode d'Operation |  |  | Operating mode |  |  | Modo Operacional |  |  | Modo do operacao |  |  | Режим работы |  |  | Operating mode
| 1 ¦ RedDevice |  |  | 1 ¦ RedDevice |  |  | 1 ¦ RedDevice |  |  | 1 ¦ RedDevice |  |  | 1 ¦ RedDevice |  |  | 1 ¦ RedDevice
| MODE DE REDONDANCE |  |  | REDUNDANCY MODE |  |  | MODO REDUNDANCIA |  |  | MODO REDUNDANCIA |  |  | РЕЖИМ РЕЗЕРВА |  |  | REDUNDANCY MODE
| ACTIF |  |  | ACTIVE |  |  | ACTIVO |  |  | ATIVO |  |  | ОСНОВНОЙ |  |  | AKTIV
| RESERVE |  |  | STANDBY |  |  | EN ESPERA |  |  | RESERVA |  |  | РЕЗЕРВНЫЙ |  |  | RESERVE
| Mode Redondance |  |  | Redundancy mode |  |  | Modo Redundancia |  |  | Modo Redundancia |  |  | Режим резерва |  |  | Redundanzmodus
| 1 ¦ RedundancyStatus |  |  | 1 ¦ RedundancyStatus |  |  | 1 ¦ RedundancyStatus |  |  | 1 ¦ RedundancyStatus |  |  | 1 ¦ RedundancyStatus |  |  | 1 ¦ RedundancyStatus
| ETAT DE REDONDANCE |  |  | REDUNDANCY STATUS |  |  | ESTADO REDUNDANCIA |  |  | ESTADO REDUNDANCIA |  |  | СТАТУС РЕЗЕРВА |  |  | REDUNDANCY STATUS
| Etat Redondance |  |  | Redundancy status |  |  | Estado Redundancia |  |  | Estado Redundancia |  |  | СТАТУС резерва |  |  | Redundanzstatus
| 1 ¦ SyncDevice |  |  | 1 ¦ SyncDevice |  |  | 1 ¦ SyncDevice |  |  | 1 ¦ SyncDevice |  |  | 1 ¦ SyncDevice |  |  | 1 ¦ SyncDevice
| ETAT DE SYNCHRONISATION |  |  | SYNCHRONIZATION STATUS |  |  | ESTADO SINCRONIZACION |  |  | ESTADO DA SINCRONIZACAO |  |  | СТАТУС СИНХРОНИЗАЦИИ |  |  | SYNCHRONISIERUNG STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Synchronisation |  |  | Synchronisation |  |  | Sincronización |  |  | Sincronizacao |  |  | Синхронизация |  |  | Synchronisation
| 1 ¦ CouplingStatus |  |  | 1 ¦ CouplingStatus |  |  | 1 ¦ CouplingStatus |  |  | 1 ¦ CouplingStatus |  |  | 1 ¦ CouplingStatus |  |  | 1 ¦ CouplingStatus
| ETAT DU COUPLAGE AGENCE |  |  | SBUS ACQUISITION STATUS |  |  | ESTADO ADQUISICION SBUS |  |  | ESTADO AQUISICAO SBUS |  |  | SBUS СТАТУС СБОРА ДАННЫХ |  |  | SBUS ACQUISITION STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Couplage IEC |  |  | IEC Coupling |  |  | Acople IEC |  |  | Aquisicao IEC |  |  | Связь с IEC |  |  | IEC Coupling
| 1 ¦ Printing |  |  | 1 ¦ Printing |  |  | 1 ¦ Printing |  |  | 1 ¦ Printing |  |  | 1 ¦ Printing |  |  | 1 ¦ Printing
| ETAT DE L'IMPRIMANTE |  |  | PRINTER STATUS |  |  | ESTADO IMPRESORA |  |  | ESTADO IMPRESSORA |  |  | СТАТУС ПРИНТЕРА |  |  | DRUCKER STATUS
| Etat Imprimante |  |  | Printer status |  |  | Estado Impresora |  |  | Estado Impresora |  |  | СТАТУС ПРИНТЕРА |  |  | Drucker Status
| 1 ¦ BackupPrinting |  |  | 1 ¦ BackupPrinting |  |  | 1 ¦ BackupPrinting |  |  | 1 ¦ BackupPrinting |  |  | 1 ¦ BackupPrinting |  |  | 1 ¦ BackupPrinting
| ETAT DE L'IMPRIMANTE DE RESERVE |  |  | BACKUP PRINTER STATUS |  |  | ESTADO IMPRESORA DE RESPALDO |  |  | ESTADO IMPRESSORA RESERVA |  |  | СТАТУС РЕЗЕРВНОГО ПРИНТЕРА |  |  | RESERVE DRUCKER STATUS
| Etat Imp Reserve |  |  | BackupPrint stat |  |  | Estado Impr.Res. |  |  | Estado Impr.Res. |  |  | Ст.резе.принтера |  |  | Res.Druck stat
SYSTEM INFORMATION CLIENT OI |  |  |  | SYSTEM INFORMATION CLIENT OI |  |  | SYSTEM INFORMATION CLIENT OI |  |  | SYSTEM INFORMATION CLIENT OI |  |  | SYSTEM INFORMATION CLIENT OI |  |  | SYSTEM INFORMATION CLIENT OI
| 2 ¦ CommS2K_C |  |  | 2 ¦ CommS2K_C |  |  | 2 ¦ CommS2K_C |  |  | 2 ¦ CommS2K_C |  |  | 2 ¦ CommS2K_C |  |  | 2 ¦ CommS2K_C
| ETAT DE LA CONNECTION |  |  | CONNECTION STATUS |  |  | ESTADO CONEXIÓN |  |  | ESTADO DA CONEXAO |  |  | СТАТУС СОЕДИНЕНИЯ |  |  | VERBINDUNG STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Lien OI CLIENT |  |  | OI client link |  |  | Enlace CLIENTE |  |  | Conexao CLIENTE |  |  | Связь клиента |  |  | OI client link
SYSTEM INFORMATION MiCOM C264 |  |  |  | SYSTEM INFORMATION MiCOM C264 |  |  | SYSTEM INFORMATION MiCOM C264 |  |  | SYSTEM INFORMATION MiCOM C264 |  |  | SYSTEM INFORMATION MiCOM C264 |  |  | SYSTEM INFORMATION MiCOM C264
| 3 ¦ DBIncoherency |  |  | 3 ¦ DBIncoherency |  |  | 3 ¦ DBIncoherency |  |  | 3 ¦ DBIncoherency |  |  | 3 ¦ DBIncoherency |  |  | 3 ¦ DBIncoherency
| BD INCOHERENTE |  |  | DATABASE INCONSISTENCY |  |  | INCONSISTENCIA BASE DE DATOS |  |  | BD INCOERENTE |  |  | НЕСОВМЕСТИМОСТЬ БД |  |  | DATABASE INKONSISTENZ
| OUI |  |  | YES |  |  | SI |  |  | SIM |  |  | ДА |  |  | JA
| NON |  |  | NO |  |  | NO |  |  | NAO |  |  | НЕТ |  |  | NEIN
| DB incoh. SPS |  |  | DB incoh. SPS |  |  | DB incoh. SPS |  |  | DB incoh. SPS |  |  | БД несовм. SPS |  |  | DB incoh. SPS
| 3 ¦ DBSwitch_SPC |  |  | 3 ¦ DBSwitch_SPC |  |  | 3 ¦ DBSwitch_SPC |  |  | 3 ¦ DBSwitch_SPC |  |  | 3 ¦ DBSwitch_SPC |  |  | 3 ¦ DBSwitch_SPC
| PERMUTATION DE BD |  |  | C264 DATABASE SWITCHING |  |  | CAMBIANDO BASE DE DATOS C264 |  |  | CHAVEAMENTO DE BD |  |  | ПЕРЕКЛЮЧЕНИЕ БД НА С264 |  |  | C264 DATABASE UMSCHALTUNG
| EXECUTER |  |  | EXECUTE |  |  | EJECUTAR |  |  | EXECUTAR |  |  | ВЫПОЛНЕНИЕ |  |  | AUSFÜHREN
| - |  |  | - |  |  | - |  |  | - |  |  | - |  |  | -
| Permutation BD |  |  | DB switch ctrl |  |  | Ctrl Cambio BD |  |  | Chaveamento BD |  |  | БД Ком переключ. |  |  | DB switch ctrl
| 3 ¦ CommDevice |  |  | 3 ¦ CommDevice |  |  | 3 ¦ CommDevice |  |  | 3 ¦ CommDevice |  |  | 3 ¦ CommDevice |  |  | 3 ¦ CommDevice
| ETAT DU LIEN SBUS |  |  | C264 SBUS LINK |  |  | ENLACE C264 SBUS |  |  | ESTADO DA CONEXAO SBUS |  |  | СВЯЗЬ с сетью SBUS |  |  | C264 SBUS LINK
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Lien Equipement |  |  | Device link |  |  | Enlace Dispo. |  |  | Enlace Dispo. |  |  | Связь устройств. |  |  | Gerät Link
| 3 ¦ DIAcquisitionStopped |  |  | 3 ¦ DIAcquisitionStopped |  |  | 3 ¦ DIAcquisitionStopped |  |  | 3 ¦ DIAcquisitionStopped |  |  | 3 ¦ DIAcquisitionStopped |  |  | 3 ¦ DIAcquisitionStopped
| ACQUISITION CARTES ENTREES |  |  | DIGITAL INPUT ACQUISITION |  |  | ADQUISICION ENTRADAS DIGITALES |  |  | AQUISICAO ENTRADAS DIGITAIS |  |  | ОПРОС DI |  |  | DIGITAL EINGANGSERFASSUNG
| ARRETEE |  |  | FAULTY |  |  | PARADO |  |  | PARADA |  |  | ИСПРАВНЫЙ |  |  | FEHLER
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | НЕИСПРАВНЫЙ |  |  | BETRIEB
| DI acq arrêtée |  |  | DI acq stopped |  |  | Adq. ED detenida |  |  | Adq. ED detenida |  |  | Остано.опроса DI |  |  | DI acq stopped
| 3 ¦ LocRemDevice_DPC |  |  | 3 ¦ LocRemDevice_DPC |  |  | 3 ¦ LocRemDevice_DPC |  |  | 3 ¦ LocRemDevice_DPC |  |  | 3 ¦ LocRemDevice_DPC |  |  | 3 ¦ LocRemDevice_DPC
| CHANGEMENT MODE DE CONTRÔLE C264 |  |  | C264 BAYS CONTROL MODE CHANGE |  |  | CAMBIO MODO CONTROL BAHIAS C264 |  |  | CHAVEAR MODO DE CONTROLE DA C264 |  |  | ИЗМЕНЕНИЕ РЕЖИМА УПРАВЛЕНИЯ ЯЧЕЙКАМИ С264 |  |  | C264 BAYS CONTROL MODE CHANGE
| DISTANT |  |  | REMOTE |  |  | REMOTO |  |  | REMOTO |  |  | ДИСТАНЦИОННЫЙ |  |  | FERN
| LOCAL |  |  | LOCAL |  |  | LOCAL |  |  | LOCAL |  |  | МЕСТНЫЙ |  |  | LOKAL
| Loc/Dst ctrl DPC |  |  | Loc/rem ctrl DPC |  |  | Loc/rem ctrl DPC |  |  | Loc/rem ctrl DPC |  |  | Мес/Дист ком DPC |  |  | Loc/rem ctrl DPC
| 3 ¦ LocRemDevice |  |  | 3 ¦ LocRemDevice |  |  | 3 ¦ LocRemDevice |  |  | 3 ¦ LocRemDevice |  |  | 3 ¦ LocRemDevice |  |  | 3 ¦ LocRemDevice
| ETAT DU MODE DE CONTRÔLE C264 |  |  | C264 MANAGED BAYS IN CONTROL MODE |  |  | BAHIAS DEL C264 EN MODO CONTROL |  |  | MODO DE CONTROLE DA C264 |  |  | С264 ОБСЛУЖИВАЕТ ЯЧЕЙКИ В РЕЖИМЕ УПРАВЛЕНИЯ |  |  | C264 MANAGED BAYS IN CONTROL MODE
| DISTANT |  |  | REMOTE |  |  | REMOTO |  |  | REMOTO |  |  | ДИСТАНЦИОННЫЙ |  |  | FERN
| LOCAL |  |  | LOCAL |  |  | LOCAL |  |  | LOCAL |  |  | МЕСТНЫЙ |  |  | LOKAL
| Local/Dist DPS |  |  | Local/remote DPS |  |  | Local/remoto DPS |  |  | Local/remoto DPS |  |  | Мес/Дист ком DPS |  |  | Fern/Lokal Sps
| 3 ¦ LocRemDeviceForIEC |  |  | 3 ¦ LocRemDeviceForIEC |  |  | 3 ¦ LocRemDeviceForIEC |  |  | 3 ¦ LocRemDeviceForIEC |  |  | 3 ¦ LocRemDeviceForIEC |  |  | 3 ¦ LocRemDeviceForIEC
| ETAT DU MODE DE CONTRÔLE C264 |  |  | C264 BAYS IN CONTROL MODE |  |  | BAHIAS C264 EN MODO CONTROL |  |  | MODO DE CONTROLE DA C264 |  |  | РЕЖИМ УПРАВЛЕНИЯ ЯЧЕЙКАМИ С264 |  |  | C264 FELDSTEUERMODUS
| DISTANT |  |  | REMOTE |  |  | REMOTO |  |  | REMOTO |  |  | ДИСТАНЦИОННЫЙ |  |  | FERN
| LOCAL |  |  | LOCAL |  |  | LOCAL |  |  | LOCAL |  |  | МЕСТНЫЙ |  |  | LOKAL
| Local/Dist SPS |  |  | Local/remote SPS |  |  | Local/remoto SPS |  |  | Local/remoto SPS |  |  | Мес/Дист ком SPS |  |  | Fern/Lokal SPS
| 3 ¦ MainInternalStatus |  |  | 3 ¦ MainInternalStatus |  |  | 3 ¦ MainInternalStatus |  |  | 3 ¦ MainInternalStatus |  |  | 3 ¦ MainInternalStatus |  |  | 3 ¦ MainInternalStatus
| NIVEAU DU DEFAUT C264 POUR REDONDANCE |  |  | C264 FAULT LEVEL FOR REDUNDANCY |  |  | C264 NIVEL DE FALLA PARA REDUNDANCIA |  |  | NIVEL DE DEFEITO DA C264 P/ REDUNDANCIA |  |  | C264 Вины уровня избыточности |  |  | C264 FEHLERLEVEL REDUNDANZ
| Etat Princial MV |  |  | Main status MV |  |  | Estado Princ MV |  |  | Estado Princ MV |  |  | Основной статус |  |  | Main status MV
| 3 ¦ ModeDevice_DPC |  |  | 3 ¦ ModeDevice_DPC |  |  | 3 ¦ ModeDevice_DPC |  |  | 3 ¦ ModeDevice_DPC |  |  | 3 ¦ ModeDevice_DPC |  |  | 3 ¦ ModeDevice_DPC
| CHANGER LE MODE D'EXPLOITATION |  |  | C264 FORCE OPERATION MODE TO |  |  | FORZAR C264 MODO DE OPERACIÓN A |  |  | CHAVEAR MODO DE OPERACAO |  |  | C264 Силу режиме для |  |  | C264 SETZE GERÄTEMODUS IN
| OPERATIONNEL |  |  | OPERATIONNAL |  |  | OPERACIONAL |  |  | OPERACIONAL |  |  | В РАБОТЕ |  |  | BERTIEBSMODUS
| MAINTENANCE |  |  | MAINTENANCE |  |  | MANTENIMIENTO |  |  | MANUTENCAO |  |  | ОБСЛУЖИВАНИЕ |  |  | WARTUNG
| Mode ctrl DPC |  |  | Mode control DPC |  |  | Modo control DPC |  |  | Modo control DPC |  |  | Команда режима |  |  | MODUS UMSCHALT
| 3 ¦ OperatingMode |  |  | 3 ¦ OperatingMode |  |  | 3 ¦ OperatingMode |  |  | 3 ¦ OperatingMode |  |  | 3 ¦ OperatingMode |  |  | 3 ¦ OperatingMode
| MODE OPERATIONNEL |  |  | C264 OPERATING MODE |  |  | C264 MODO OPERACIÓN |  |  | MODO DE OPERACAO |  |  | Режим работы C264 |  |  | C264 BETRIEBSMODUS
| Mode d'Operation |  |  | Operating mode |  |  | Modo Operacional |  |  | Modo do operacao |  |  | Режим работы |  |  | Operating mode
| 3 ¦ RedChangeMode_SPC |  |  | 3 ¦ RedChangeMode_SPC |  |  | 3 ¦ RedChangeMode_SPC |  |  | 3 ¦ RedChangeMode_SPC |  |  | 3 ¦ RedChangeMode_SPC |  |  | 3 ¦ RedChangeMode_SPC
| RELAIS DE REDONDANCE BIU CO2 |  |  | C264 BIU REDUNDANCY RELAY CO 2 |  |  | C264 BIU RELE REDUNDANCIA CO 2 |  |  | C264 BIU RELE REDUNDANCIA CO 2 |  |  | C264 BIU Pезервирования Pелейной CO 2 |  |  | C264 BIU REDUNDANZ RELAIS CO 2
| ACTIVER |  |  | ACTIVATE |  |  | ACTIVAR |  |  | ATIVAR |  |  | АКТИВНО |  |  | AKTIVIERE
| DESACTIVER |  |  | DEACTIVATE |  |  | DESACTIVAR |  |  | DESATIVAR |  |  | НЕАКТИВНО |  |  | DEAKTIVIERE
| Mode Ctrl Red |  |  | Red mode ctrl |  |  | Ctrl Modo Red. |  |  | Ctrl Modo Red. |  |  | управ.режи.резер |  |  | Red Mod Befehl
| 3 ¦ RedChangeStatus_SPC |  |  | 3 ¦ RedChangeStatus_SPC |  |  | 3 ¦ RedChangeStatus_SPC |  |  | 3 ¦ RedChangeStatus_SPC |  |  | 3 ¦ RedChangeStatus_SPC |  |  | 3 ¦ RedChangeStatus_SPC
| RELAIS DE REDONDANCE BIU CO1 |  |  | C264 BIU REDUNDANCY RELAY CO 1 |  |  | C264 BIU RELE REDUNDANCIA CO 1 |  |  | C264 BIU RELE REDUNDANCIA CO 1 |  |  | C264 BIU Pезервирования Pелейной CO 1 |  |  | C264 BIU REDUNDANZ RELAIS CO 1
| ACTIVER |  |  | ACTIVATE |  |  | ACTIVAR |  |  | ATIVAR |  |  | АКТИВНО |  |  | AKTIVIERE
| DESACTIVER |  |  | DEACTIVATE |  |  | DESACTIVAR |  |  | DESATIVAR |  |  | НЕАКТИВНО |  |  | DEAKTIVIERE
| Etat Ctrl Red |  |  | Red Status ctrl |  |  | Ctrl Estado Red. |  |  | Ctrl Estado Red. |  |  | Управ.стат.резер |  |  | Red Mod Befehl
| 3 ¦ RedChangeMode |  |  | 3 ¦ RedChangeMode |  |  | 3 ¦ RedChangeMode |  |  | 3 ¦ RedChangeMode |  |  | 3 ¦ RedChangeMode |  |  | 3 ¦ RedChangeMode
| MODE DE REDONDANCE |  |  | REDUNDANT C264 CHANGE MODE |  |  | MODO REDUNDANCIA C264 |  |  | MODO DA REDUNDANCIA |  |  | Режим РЕЗЕРВНОГО C264 |  |  | RESERVE C264 MODE
| ACTIF |  |  | ACTIVE |  |  | ACTIVA |  |  | ATIVO |  |  | ОСНОВНОЙ |  |  | ACTIV
| RESERVE |  |  | STANDBY |  |  | EN ESPERA |  |  | RESERVA |  |  | РЕЗЕРВНЫЙ |  |  | RESERVE
| Mode Chgt Red |  |  | Red. change mode |  |  | Mod. Cambio Red. |  |  | Mod. Cambio Red. |  |  | Реж.перек.резер |  |  | Red. Änderung Md
| 3 ¦ RedChangeStatus |  |  | 3 ¦ RedChangeStatus |  |  | 3 ¦ RedChangeStatus |  |  | 3 ¦ RedChangeStatus |  |  | 3 ¦ RedChangeStatus |  |  | 3 ¦ RedChangeStatus
| ETAT DE REDONDANCE |  |  | REDUNDANT C264 STATUS |  |  | ESTADO REDUNDANCIA C264 |  |  | ESTADO DA REDUNDANCIA |  |  | СТАТУС РЕЗЕРВНОГО C264 |  |  | RESERVE C264 STATUS
| ACTIF |  |  | ACTIVE |  |  | ACTIVA |  |  | ATIVO |  |  | ОСНОВНОЙ |  |  | ACTIV
| RESERVE |  |  | STANDBY |  |  | EN ESPERA |  |  | RESERVA |  |  | РЕЗЕРВНЫЙ |  |  | RESERVE
| Etat Chgt Red |  |  | Red. change stat |  |  | Est. Cambio Red. |  |  | Est. Cambio Red. |  |  | Стат.перек.резер |  |  | Red. Änderung St
| 3 ¦ SoftError |  |  | 3 ¦ SoftError |  |  | 3 ¦ SoftError |  |  | 3 ¦ SoftError |  |  | 3 ¦ SoftError |  |  | 3 ¦ SoftError
| ERREUR LOGICIELLE DETECTEE |  |  | SOFTWARE ERROR DETECTED |  |  | ERROR DETECTADO SOFTWARE |  |  | ERRO DE SOFTWARE DETECTADO |  |  | ОБНАРУЖЕНА ОШИБКА ПО |  |  | SOFTWAREFEHLER
| OUI |  |  | YES |  |  | SI |  |  | SIM |  |  | ДА |  |  | JA
| NON |  |  | NO |  |  | NO |  |  | NAO |  |  | НЕТ |  |  | NEIN
| Err. Logicielle |  |  | Soft. error SPS |  |  | Error Soft. SPS |  |  | Soft. error SPS |  |  | Ошибка по SPS |  |  | Softwarefehler
| 3 ¦ SyncDevice |  |  | 3 ¦ SyncDevice |  |  | 3 ¦ SyncDevice |  |  | 3 ¦ SyncDevice |  |  | 3 ¦ SyncDevice |  |  | 3 ¦ SyncDevice
| ETAT DE SYNCHRONISATION |  |  | C264 SYNCHRONIZATION STATUS |  |  | ESATDO SINCRONIZACION C264 |  |  | ESTADO DA SINCRONIZACAO |  |  | СТАТУС СИНХРОНИЗАЦИИ C264 |  |  | C264 SYNCHRONISIERUNG STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Synchronisation |  |  | Synchronisation |  |  | Sincronización |  |  | Sincronizacao |  |  | Синхронизация |  |  | Synchronisation
| 3 ¦ TestDevice_DPC |  |  | 3 ¦ TestDevice_DPC |  |  | 3 ¦ TestDevice_DPC |  |  | 3 ¦ TestDevice_DPC |  |  | 3 ¦ TestDevice_DPC |  |  | 3 ¦ TestDevice_DPC
| CHANGEMENT MODE EXPLOITATION |  |  | C264 CHANGE EXPLOITATION MODE |  |  | CAMBIO MODO EXPLOTACION C264 |  |  | CHAVEAR MODO DE OPERACAO |  |  | Смена режима работы C264 |  |  | C264 TESTMODUS UMSCHALT
| OPERATIONNEL |  |  | NORMAL |  |  | NORMAL |  |  | OPERACIONAM |  |  | НОРМАЛЬНЫЙ |  |  | NORMAL
| TEST |  |  | TEST |  |  | PRUEBA |  |  | TESTE |  |  | ТЕСТОВОЙ |  |  | TEST
| Ctrl Test DPC |  |  | Test control DPC |  |  | Ctrl Prueba DPC |  |  | Ctrl Prueba DPC |  |  | ком Тестов. DPC |  |  | Testmodus DPC
| 3 ¦ WatchdogError |  |  | 3 ¦ WatchdogError |  |  | 3 ¦ WatchdogError |  |  | 3 ¦ WatchdogError |  |  | 3 ¦ WatchdogError |  |  | 3 ¦ WatchdogError
| ETAT DU CHIEN DE GARDE C264 |  |  | C264 WATCHDOG RELAY STATUS |  |  | ESTADO RELE WATCHDOG C264 |  |  | ESTADO RELE WATCHDOG C264 |  |  | СТАТУС WATCHDOG C264 |  |  | C264 WATCHDOG RELAIS STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | ATIVO |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Watchdog SPS |  |  | Watchdog SPS |  |  | Watchdog SPS |  |  | Watchdog SPS |  |  | Watchdog SPS |  |  | Watchdog SPS
| 3 ¦ ModeDevice |  |  | 3 ¦ ModeDevice |  |  | 3 ¦ ModeDevice |  |  | 3 ¦ ModeDevice |  |  | 3 ¦ ModeDevice |  |  | 3 ¦ ModeDevice
| V3 MODE OPERATIONNEL |  |  | C264 OPERATING MODE |  |  | C264 MODO OPERACIÓN DISPOSITIVO |  |  | V3 MODO DE OPERACAO |  |  | РЕЖИМ РАБОТЫ C264 |  |  | C264 BETRIEBSMODUS
| OPERATIONNEL |  |  | RUNNING |  |  | EN SERVICIO |  |  | EM SERVICO |  |  | Рабочее |  |  | BETRIEB
| MAINTENANCE |  |  | MAINTENANCE |  |  | MANTENIMIENTO |  |  | MANUTENCAO |  |  | ОБСЛУЖИВАНИЕ |  |  | WARTUNG
| Mode Eqpt |  |  | Device mode |  |  | Modo Dispositivo |  |  | Modo Dispositivo |  |  | Режим устройства |  |  | Gerätemodus
| 3 ¦ DisturbUCA2 |  |  | 3 ¦ DisturbUCA2 |  |  | 3 ¦ DisturbUCA2 |  |  | 3 ¦ DisturbUCA2 |  |  | 3 ¦ DisturbUCA2 |  |  | 3 ¦ DisturbUCA2
| FICHIER DE PERTURBOGRAPHIE C264 |  |  | DISTURBANCE FILE ON C264 |  |  | ARCHIVO DE DISTURBIO EN C264 |  |  | ARQUIVO DE OSCILOGRAFIA C264 |  |  | ФАЙЛ ОСЦИЛОГРАМ НА C264 |  |  | STÖRFALLDATEI AUF C264
| PRÊT |  |  | READY |  |  | LISTO |  |  | PRONTO |  |  | ГОТОВ |  |  | BEREIT
| ABSENT |  |  | NOT READY |  |  | NO LISTO |  |  | AUSENTE |  |  | НЕ ГОТОВ |  |  | NICHT BEREIT
| DREC prêt |  |  | DREC ready |  |  | DREC Listo |  |  | DREC Pronto |  |  | DREC готов |  |  | DREC ready
| 3 ¦ CounterTop |  |  | 3 ¦ CounterTop |  |  | 3 ¦ CounterTop |  |  | 3 ¦ CounterTop |  |  | 3 ¦ CounterTop |  |  | 3 ¦ CounterTop
| DEMARRAGE DU COMPTAGE |  |  | C264 COUNTERS ACQUISITION TOP |  |  | ADQ MAX CONTADORES C264 |  |  | CONTAGEM PARTIDA |  |  | Счетчик C264 макс |  |  | C264 ZÄHLERSTAND MAX
| OUI |  |  | YES |  |  | SI |  |  | SIM |  |  | ДА |  |  | JA
| NON |  |  | NO |  |  | NO |  |  | NAO |  |  | НЕТ |  |  | NEIN
| Max Compteur |  |  | Counter Top |  |  | Max Contadores |  |  | Max Contagem |  |  | Счетчик макс |  |  | Zähler max
| 3 ¦ ExtClockStatus |  |  | 3 ¦ ExtClockStatus |  |  | 3 ¦ ExtClockStatus |  |  | 3 ¦ ExtClockStatus |  |  | 3 ¦ ExtClockStatus |  |  | 3 ¦ ExtClockStatus
| ETAT DE LA SOURCE DE SYNCHRONISATION |  |  | GPS SYNCHRONISATION SOURCE |  |  | FUENTE SINCRONIZACION GPS |  |  | FONTE SINCRONIZACAO GPS |  |  | GPS ИСТОЧНИК СИНХРОНИЗАЦИИ |  |  | GPS SYNCHRONISIERUNG QUELLE
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Etat Horloge |  |  | Ext clock status |  |  | Estado Reloj GPS |  |  | Estado Reloj GPS |  |  | Статус IRIG-B |  |  | Ext Uhr Status
| 3 ¦ RedDevice |  |  | 3 ¦ RedDevice |  |  | 3 ¦ RedDevice |  |  | 3 ¦ RedDevice |  |  | 3 ¦ RedDevice |  |  | 3 ¦ RedDevice
| MODE DE REDONDANCE |  |  | C264 REDUNDANCY MODE |  |  | MODO REDUNDANCIA C264 |  |  | MODO REDUNDANCIA C264 |  |  | C264 Режим резервирования |  |  | C264 REDUNDANZ MODUS
| ACTIF |  |  | ACTIVE |  |  | ACTIVO |  |  | ATIVO |  |  | ОСНОВНОЙ |  |  | AKTIV
| RESERVE |  |  | STANDBY |  |  | EN ESPERA |  |  | RESERVA |  |  | РЕЗЕРВНЫЙ |  |  | RESERVE
| Mode Redondance |  |  | Redundancy mode |  |  | Modo Redundancia |  |  | Modo Redundancia |  |  | Режим резерва |  |  | Redundanzmodus
| 3 ¦ BuffOvGtw1 |  |  | 3 ¦ BuffOvGtw1 |  |  | 3 ¦ BuffOvGtw1 |  |  | 3 ¦ BuffOvGtw1 |  |  | 3 ¦ BuffOvGtw1 |  |  | 3 ¦ BuffOvGtw1
| DEBORDEMENT DE TAMPON GTW 1 |  |  | REPORT BUFFER OVERFLOW GTW 1 |  |  | DESBORDAMIENTO DE BUFER GTW 1 |  |  | DESBORDAMIENTO DE BUFER GTW 1 |  |  | Переполнение буфера GTW 1 |  |  | Pufferüberlauf GTW 1
| OUI |  |  | YES |  |  | SI |  |  | SIM |  |  | ДА |  |  | JA
| NON |  |  | NO |  |  | NO |  |  | NAO |  |  | НЕТ |  |  | NEIN
| Débord. Tampon Gtw 1 |  |  | Buff Ov Gtw 1 |  |  | Desbord. Búfer Gtw 1 |  |  | Desbord. Búfer Gtw 1 |  |  | Переп. Буфера Gtw 1 |  |  | Pufferüberlauf Gtw 1
| 3 ¦ BuffOvGtw2 |  |  | 3 ¦ BuffOvGtw2 |  |  | 3 ¦ BuffOvGtw2 |  |  | 3 ¦ BuffOvGtw2 |  |  | 3 ¦ BuffOvGtw2 |  |  | 3 ¦ BuffOvGtw2
| DEBORDEMENT DE TAMPON GTW 2 |  |  | REPORT BUFFER OVERFLOW GTW 2 |  |  | DESBORDAMIENTO DE BUFER GTW 2 |  |  | DESBORDAMIENTO DE BUFER GTW 2 |  |  | Переполнение буфера GTW 2 |  |  | Pufferüberlauf GTW 2
| OUI |  |  | YES |  |  | SI |  |  | SIM |  |  | ДА |  |  | JA
| NON |  |  | NO |  |  | NO |  |  | NAO |  |  | НЕТ |  |  | NEIN
| Débord. Tampon OI |  |  | Buff Ov Gtw 2 |  |  | Desbord. Búfer Gtw 2 |  |  | Desbord. Búfer Gtw 2 |  |  | Переп. Буфера Gtw 2 |  |  | Pufferüberlauf Gtw 2
| 3 ¦ BuffOvOI |  |  | 3 ¦ BuffOvOI |  |  | 3 ¦ BuffOvOI |  |  | 3 ¦ BuffOvOI |  |  | 3 ¦ BuffOvOI |  |  | 3 ¦ BuffOvOI
| DEBORDEMENT DE TAMPON OI |  |  | REPORT BUFFER OVERFLOW OI |  |  | DESBORDAMIENTO DE BUFER OI |  |  | DESBORDAMIENTO DE BUFER OI |  |  | Переполнение буфера OI |  |  | Pufferüberlauf OI
| OUI |  |  | YES |  |  | SI |  |  | SIM |  |  | ДА |  |  | JA
| NON |  |  | NO |  |  | NO |  |  | NAO |  |  | НЕТ |  |  | NEIN
| Débord. Tampon Oi |  |  | Buff Ov Oi |  |  | Desbord. Búfer Oi |  |  | Desbord. Búfer Oi |  |  | Переп. Буфера Oi |  |  | Pufferüberlauf Oi
| 3 ¦ BuffOvOIBck |  |  | 3 ¦ BuffOvOIBck |  |  | 3 ¦ BuffOvOI Bck |  |  | 3 ¦ BuffOvOIBck |  |  | 3 ¦ BuffOvOIBck |  |  | 3 ¦ BuffOvOIBck
| DEBORDEMENT DE TAMPON OI BACKUP |  |  | REPORT BUFFER OVERFLOW OI BACKUP |  |  | DESBORDAMIENTO DE BUFER OI BACKUP |  |  | DESBORDAMIENTO DE BUFER OI BACKUP |  |  | Переполнение буфера OI BACKUP |  |  | Pufferüberlauf OI BACKUP
| OUI |  |  | YES |  |  | SI |  |  | SIM |  |  | ДА |  |  | JA
| NON |  |  | NO |  |  | NO |  |  | NAO |  |  | НЕТ |  |  | NEIN
| Débord. Tampon Oi Bck |  |  | Buff Ov Oi Bck |  |  | Desbord. Búfer Oi Bck |  |  | Desbord. Búfer Oi Bck |  |  | Переп. Буфера Oi Bck |  |  | Pufferüberlauf Oi Bck
| 3 ¦ BIUStatus |  |  | 3 ¦ BIUStatus |  |  | 3 ¦ BIUStatus |  |  | 3 ¦ BIUStatus |  |  | 3 ¦ BIUStatus |  |  | 3 ¦ BIUStatus
| ETAT DE LA CARTE BIU |  |  | BIU BOARD STATUS |  |  | ESTADO TARJETA BIU |  |  | ESTADO DO CARTAO BIU |  |  | СТАТУС ПЛАТЫ BIU |  |  | BIU KARTEN STATUS
| Etat BIU |  |  | BIU status |  |  | Estado BIU |  |  | Estado BIU |  |  | BIU статус |  |  | BIU status
| 3 ¦ GHUStatus |  |  | 3 ¦ GHUStatus |  |  | 3 ¦ GHUStatus |  |  | 3 ¦ GHUStatus |  |  | 3 ¦ GHUStatus |  |  | 3 ¦ GHUStatus
| ETAT DE LA CARTE GHU |  |  | GHU BOARD STATUS |  |  | ESTADO TARJETA GHU |  |  | ESTADO DO CARTAO GHU |  |  | GHU СТАТУС ПЛАТЫ |  |  | GHU KARTEN STATUS
| Etat GHU |  |  | GHU status |  |  | Estado GHU |  |  | Estado GHU |  |  | GHU статус |  |  | GHU status
| 3 ¦ AIUStatus |  |  | 3 ¦ AIUStatus |  |  | 3 ¦ AIUStatus |  |  | 3 ¦ AIUStatus |  |  | 3 ¦ AIUStatus |  |  | 3 ¦ AIUStatus
| ETAT DE LA CARTE AIU20x |  |  | AIU20x BOARD STATUS |  |  | ESTADO TARJETA AIU20x |  |  | ESTADO DO CARTAO AIU20x |  |  | AIU20x СТАТУС ПЛАТЫ |  |  | AIU20x KARTEN STATUS
| Etat AIU |  |  | AIU status |  |  | Estado AIU |  |  | Estado AIU |  |  | AIU статус |  |  | AIU status
| 3 ¦ AIUStatus |  |  | 3 ¦ AIUStatus |  |  | 3 ¦ AIUStatus |  |  | 3 ¦ AIUStatus |  |  | 3 ¦ AIUStatus |  |  | 3 ¦ AIUStatus
| ETAT DE LA CARTE AIU21x |  |  | AIU21x BOARD STATUS |  |  | ESTADO TARJETA AIU21x |  |  | ESTADO DO CARTAO AIU21x |  |  | AIU21x СТАТУС ПЛАТЫ |  |  | AIU21x KARTEN STATUS
| Etat AIU |  |  | AIU status |  |  | Estado AIU |  |  | Estado AIU |  |  | AIU статус |  |  | AIU status
| 3 ¦ AOUStatus |  |  | 3 ¦ AOUStatus |  |  | 3 ¦ AOUStatus |  |  | 3 ¦ AOUStatus |  |  | 3 ¦ AOUStatus |  |  | 3 ¦ AOUStatus
| ETAT DE LA CARTE AOU200 |  |  | AOU200 BOARD STATUS |  |  | ESTADO TARJETA AOU200 |  |  | ESTADO DO CARTAO AOU200 |  |  | AOU200 СТАТУС ПЛАТЫ |  |  | AOU200 KARTEN STATUS
| Etat AOU |  |  | AOU status |  |  | Estado AOU |  |  | Estado AOU |  |  | AOU статус |  |  | AOU status
| 3 ¦ DIUStatus |  |  | 3 ¦ DIUStatus |  |  | 3 ¦ DIUStatus |  |  | 3 ¦ DIUStatus |  |  | 3 ¦ DIUStatus |  |  | 3 ¦ DIUStatus
| ETAT DE LA CARTE DIU |  |  | DIU BOARD STATUS |  |  | ESTADO TARJETA DIU |  |  | ESTADO DO CARTAO DIU |  |  | DIU СТАТУС ПЛАТЫ |  |  | DIU KARTEN STATUS
| Etat DIU |  |  | DIU status |  |  | Estado DIU |  |  | Estado DIU |  |  | DIU статус |  |  | DIU status
| 3 ¦ DOUStatus |  |  | 3 ¦ DOUStatus |  |  | 3 ¦ DOUStatus |  |  | 3 ¦ DOUStatus |  |  | 3 ¦ DOUStatus |  |  | 3 ¦ DOUStatus
| ETAT DE LA CARTE DOU |  |  | DOU BOARD STATUS |  |  | ESTADO TARJETA DOU |  |  | ESTADO DO CARTAO DOU |  |  | DOU СТАТУС ПЛАТЫ |  |  | DOU KARTEN STATUS
| Etat DOU |  |  | DOU status |  |  | Estado DOU |  |  | Estado DOU |  |  | DOU статус |  |  | DOU status
| 3 ¦ CCUStatus |  |  | 3 ¦ CCUStatus |  |  | 3 ¦ CCUStatus |  |  | 3 ¦ CCUStatus |  |  | 3 ¦ CCUStatus |  |  | 3 ¦ CCUStatus
| ETAT DE LA CARTE CCU |  |  | CCU BOARD STATUS |  |  | ESTADO TARJETA CCU |  |  | ESTADO DO CARTAO CCU |  |  | CCU СТАТУС ПЛАТЫ |  |  | CCU KARTEN STATUS
| Etat CCU |  |  | CCU status |  |  | Estado CCU |  |  | Estado CCU |  |  | CCU статус |  |  | CCU status
| 3 ¦ TIUStatus |  |  | 3 ¦ TIUStatus |  |  | 3 ¦ TIUStatus |  |  | 3 ¦ TIUStatus |  |  | 3 ¦ TIUStatus |  |  | 3 ¦ TIUStatus
| ETAT DE LA CARTE TMU |  |  | TMU BOARD STATUS |  |  | ESTADO TARJETA TMU |  |  | ESTADO DO CARTAO TMU |  |  | TMU СТАТУС ПЛАТЫ |  |  | TMU KARTEN STATUS
| Etat TMU |  |  | TMU status |  |  | Estado TMU |  |  | Estado TMU |  |  | TMU статус |  |  | TMU status
| 3 ¦ HBUStatus |  |  | 3 ¦ HBUStatus |  |  | 3 HBUStatus |  |  | 3 ¦ HBUStatus |  |  | 3 ¦HBUStatus |  |  | 3 ¦HBUStatus
| ETAT DE LA CARTE HBU |  |  | HBU BOARD STATUS |  |  | ESTADO TARJETA HBU |  |  | ESTADO DO CARTAO HBU |  |  | HBU СТАТУС ПЛАТЫ |  |  | HBU KARTEN STATUS
| Etat HBU |  |  | HBU status |  |  | Estado HBU |  |  | Estado HBU |  |  | HBU статус |  |  | HBU status
| 3 ¦ CommIED |  |  | 3 ¦ CommIED |  |  | 3 ¦ CommIED |  |  | 3 ¦ CommIED |  |  | 3 ¦ CommIED |  |  | 3 ¦ CommIED
| ETAT DE LA CONNECTION AU C264 |  |  | IED CONNECTION STATUS TO C264 |  |  | ESTADO COMUNICACIÓN IED AL C264 |  |  | ESTADO DA CONEXAO COM A C264 |  |  | СТАТУС СВЯЗИ IED С С264 |  |  | IED VERBINDUNGSSTATUS C264
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Com. IED SPS |  |  | IED SPS com. |  |  | IED SPS com. |  |  | IED SPS com. |  |  | IED SPS связь. |  |  | IED SPS com.
| 3 ¦ SyncIED |  |  | 3 ¦ SyncIED |  |  | 3 ¦ SyncIED |  |  | 3 ¦ SyncIED |  |  | 3 ¦ SyncIED |  |  | 3 ¦ SyncIED
| ETAT DE LA SYNCHRONISATION DE L'IED |  |  | IED SYNCHRONISATION STATUS |  |  | ESTADO SINCRONIZACION IED |  |  | ESTADO DA SINCRONIZACAO DO RELE |  |  | IED СТАТУС СИНХРОНИЗАЦИИ |  |  | IED SYNCHRONISIERUNGSSTATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Synchro. IED SPS |  |  | IED SPS Synchro. |  |  | IED SPS Sincro. |  |  | IED SPS Sincro. |  |  | IED SPS синхр. |  |  | IED SPS Synchro.
| 3 ¦ DisturbIED |  |  | 3 ¦ DisturbIED |  |  | 3 ¦ DisturbIED |  |  | 3 ¦ DisturbIED |  |  | 3 ¦ DisturbIED |  |  | 3 ¦ DisturbIED
| FICHIER DE PERTURBOGRAPHIE IED |  |  | IED DISTURBANCE FILE |  |  | ARCHIVO DE DISTURBIO EN IED |  |  | ARQUIVO DE OSCILOGRAFIA IED |  |  | IED ФАЙЛ ОСЦИЛОГРАМ |  |  | IED DISTURBANCE FILE
| PRÊT |  |  | READY |  |  | LISTO |  |  | PRONTO |  |  | ГОТОВ |  |  | BEREIT
| ABSENT |  |  | NOT READY |  |  | NO LISTO |  |  | AUSENTE |  |  | НЕ ГОТОВ |  |  | NICHT BEREIT
| IED DREC Prêt |  |  | IED DREC ready |  |  | IED DREC Listo |  |  | IED DREC Pronto |  |  | IED DRECготов |  |  | IED DREC ready
| 3 ¦ ISAGRAFStatus |  |  | 3 ¦ ISAGRAFStatus |  |  | 3 ¦ ISAGRAFStatus |  |  | 3 ¦ ISAGRAFStatus |  |  | 3 ¦ ISAGRAFStatus |  |  | 3 ¦ ISAGRAFStatus
| ETAT ISAGRAF |  |  | ISAGRAF STATUS |  |  | ESTADO ISAGRAF |  |  | ESTADO ISAGRAF |  |  | ISAGRAF статус |  |  | ISAGRAF STATUS
| Etat ISAGRAF |  |  | ISAGRAF status |  |  | Estado ISAGRAF |  |  | Estado ISAGRAF |  |  | ISAGRAF статус |  |  | ISAGRAF status
| 3 ¦ PrinterStatus |  |  | 3 ¦ PrinterStatus |  |  | 3 ¦ PrinterStatus |  |  | 3 ¦ PrinterStatus |  |  | 3 ¦ PrinterStatus |  |  | 3 ¦ PrinterStatus
| PRINTER STATUS DPS |  |  | PRINTER STATUS DPS |  |  | DPS ESTADO IMPRESORA |  |  | DPS ESTADO IMPRESSORA |  |  | СТАТУС ПРИНТЕРА DPS |  |  | DRUCKER STATUS DPS
| Etat Impr. DPS |  |  | Printer st. DPS |  |  | Edo. Impr. DPS |  |  | Edo. Impr. DPS |  |  | стат принт DPS |  |  | Druckerstat. DPS
| 3 ¦ Printing |  |  | 3 ¦ Printing |  |  | 3 ¦ Printing |  |  | 3 ¦ Printing |  |  | 3 ¦ Printing |  |  | 3 ¦ Printing
| ETAT DE L'IMPRIMANTE LOCAL |  |  | LOCAL PRINTER STATUS |  |  | ESTADO IMPRESORA LOCAL |  |  | ESTADO IMPRESSORA LOCAL |  |  | СТАТУС ПРИНТЕРА |  |  | LOKAL DRUCKER STATUS
| Etat Imprimante |  |  | Printer Status |  |  | Edo. Impresora |  |  | Edo. Impressora |  |  | статус принтера |  |  | Drucker Status
| 3 ¦ RedSCADA |  |  | 3 ¦ RedSCADA |  |  | 3 ¦ RedSCADA |  |  | 3 ¦ RedSCADA |  |  | 3 ¦ RedSCADA |  |  | 3 ¦ RedSCADA
| PORT DE COMMUNICATION AVEC LE SCADA |  |  | C264 SCADA PORT COMMUNICATION |  |  | PTO. COM C264 SCADA |  |  | CANAL DE COMUNICACAO C/ SCADA |  |  | СТАТУС ПОРТА СВЯЗЬ C264 с SCADA |  |  | C264 FWL PORT KOMMUNIKATION
| ACTIF |  |  | ACTIVE |  |  | ACTIVO |  |  | ATIVO |  |  | ОСНОВНОЙ |  |  | AKTIV
| RESERVE |  |  | STANDBY |  |  | EN ESPERA |  |  | RESERVA |  |  | РЕЗЕРВНЫЙ |  |  | RESERVE
| SPS Redondance |  |  | Redundancy SPS |  |  | Redundancia SPS |  |  | Redundancia SPS |  |  | резервирование |  |  | Redundancy SPS
| 3 ¦ CommSCADA |  |  | 3 ¦ CommSCADA |  |  | 3 ¦ CommSCADA |  |  | 3 ¦ CommSCADA |  |  | 3 ¦ CommSCADA |  |  | 3 ¦ CommSCADA
| ETAT DE LA COMMUNICATION SCADA |  |  | SCADA CONNECTION STATUS TO C264 |  |  | EDO. CONEXIÓN SCADA AL C264 |  |  | ESTADO DA CONEXAO C/ SCADA |  |  | СТАТУС СОЕДИНЕНИЯ SCADA С C264 |  |  | FWL VERBINDUNGSSTATUS C264
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Com. SCADA SPS |  |  | SCADA SPS com. |  |  | SCADA SPS com. |  |  | SCADA SPS com. |  |  | SCADA SPS связь |  |  | FWL SPS KOMMU
| 3 ¦ GlobalAIUStatus |  |  | 3 ¦ GlobalAIUStatus |  |  | 3 ¦ GlobalAIUStatus |  |  | 3 ¦ GlobalAIUStatus |  |  | 3 ¦ GlobalAIUStatus |  |  | 3 ¦ GlobalAIUStatus
| TOUS LES ETATS AIU |  |  | ALL AIU STATUS |  |  | TODOS LOS AIU ESTADO |  |  | AIU TODO ESTADO |  |  | ВСЕ AIU СТАТУС |  |  | ALLE AIU STATUS
| ARRETEE |  |  | FAULTY |  |  | PARADO |  |  | PARADA |  |  | ИСПРАВНЫЙ |  |  | FEHLER
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | НЕИСПРАВНЫЙ |  |  | BETRIEB
| Tous états AIU |  |  | All AIU status |  |  | Todos AIU estado |  |  | AIU todo estado |  |  | Все AIU статус |  |  | Alle AIU Status
| 3 ¦ GlobalAOUStatus |  |  | 3 ¦ GlobalAOUStatus |  |  | 3 ¦ GlobalAOUStatus |  |  | 3 ¦ GlobalAOUStatus |  |  | 3 ¦ GlobalAOUStatus |  |  | 3 ¦ GlobalAOUStatus
| TOUS LES ETATS AOU |  |  | ALL AOU STATUS |  |  | TODOS LOS AOU ESTADO |  |  | AOU TODO ESTADO |  |  | ВСЕ АOU СТАТУС |  |  | ALLE AOU STATUS
| ARRETEE |  |  | FAULTY |  |  | PARADO |  |  | PARADA |  |  | ИСПРАВНЫЙ |  |  | FEHLER
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | НЕИСПРАВНЫЙ |  |  | BETRIEB
| Tous états AOU |  |  | All AOU status |  |  | Todos AOU estado |  |  | AOU todo estado |  |  | Все AOU статус |  |  | Alle AOU Status
| 3 ¦ GlobalCCUStatus |  |  | 3 ¦ GlobalCCUStatus |  |  | 3 ¦ GlobalCCUStatus |  |  | 3 ¦ GlobalCCUStatus |  |  | 3 ¦ GlobalCCUStatus |  |  | 3 ¦ GlobalCCUStatus
| TOUS LES ETATS CCU |  |  | ALL CCU STATUS |  |  | TODOS LOS CCU ESTADO |  |  | CCU TODO ESTADO |  |  | ВСЕ CCU СТАТУС |  |  | ALLE CCU STATUS
| ARRETEE |  |  | FAULTY |  |  | PARADO |  |  | PARADA |  |  | ИСПРАВНЫЙ |  |  | FEHLER
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | НЕИСПРАВНЫЙ |  |  | BETRIEB
| Tous états CCU |  |  | All CCU status |  |  | Todos CCU estado |  |  | CCU todo estado |  |  | Все CCU статус |  |  | Alle CCU Status
| 3 ¦ GlobalDIUStatus |  |  | 3 ¦ GlobalDIUStatus |  |  | 3 ¦ GlobalDIUStatus |  |  | 3 ¦ GlobalDIUStatus |  |  | 3 ¦ GlobalDIUStatus |  |  | 3 ¦ GlobalDIUStatus
| TOUS LES ETATS DIU |  |  | ALL DIU STATUS |  |  | TODOS LOS DIU ESTADO |  |  | DIU TODO ESTADO |  |  | ВСЕ DIU СТАТУС |  |  | ALLE DIU STATUS
| ARRETEE |  |  | FAULTY |  |  | PARADO |  |  | PARADA |  |  | ИСПРАВНЫЙ |  |  | FEHLER
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | НЕИСПРАВНЫЙ |  |  | BETRIEB
| Tous états DIU |  |  | All DIU status |  |  | Todos DIU estado |  |  | DIU todo estado |  |  | Все DIU статус |  |  | Alle DIU Status
| 3 ¦ GlobalDOUStatus |  |  | 3 ¦ GlobalDOUStatus |  |  | 3 ¦ GlobalDOUStatus |  |  | 3 ¦ GlobalDOUStatus |  |  | 3 ¦ GlobalDOUStatus |  |  | 3 ¦ GlobalDOUStatus
| TOUS LES ETATS DOU |  |  | ALL DOU STATUS |  |  | TODOS LOS DOU ESTADO |  |  | DOU TODO ESTADO |  |  | ВСЕ DOU СТАТУС |  |  | ALLE DOU STATUS
| ARRETEE |  |  | FAULTY |  |  | PARADO |  |  | PARADA |  |  | ИСПРАВНЫЙ |  |  | FEHLER
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | НЕИСПРАВНЫЙ |  |  | BETRIEB
| Tous états DOU |  |  | All DOU status |  |  | Todos DOU estado |  |  | DOU todo estado |  |  | Все DOU статус |  |  | Alle DOU Status
| 3 ¦ GlobalTMUStatus |  |  | 3 ¦ GlobalTMUStatus |  |  | 3 ¦ GlobalTMUStatus |  |  | 3 ¦ GlobalTMUStatus |  |  | 3 ¦ GlobalTMUStatus |  |  | 3 ¦ GlobalTMUStatus
| TOUS LES ETATS TMU |  |  | ALL TMU STATUS |  |  | TODOS LOS TMU ESTADO |  |  | TMU TODO ESTADO |  |  | ВСЕ TMU СТАТУС |  |  | ALLE TMU STATUS
| ARRETEE |  |  | FAULTY |  |  | PARADO |  |  | PARADA |  |  | ИСПРАВНЫЙ |  |  | FEHLER
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | НЕИСПРАВНЫЙ |  |  | BETRIEB
| Tous états TMU |  |  | All TMU status |  |  | Todos TMU estado |  |  | TMU todo estado |  |  | Все TMU статус |  |  | Alle TMU Status
| 3 ¦ GlobalHBUStatus |  |  | 3 ¦ GlobaHBMUStatus |  |  | 3 ¦ GlobalHBUStatus |  |  | 3 ¦ GlobalHBUStatus |  |  | 3 ¦ GlobalHBUStatus |  |  | 3 ¦ GlobalHBUStatus
| TOUS LES ETATS HBU |  |  | ALL HBU STATUS |  |  | TODOS LOS HBU ESTADO |  |  | HBU TODO ESTADO |  |  | ВСЕ HBU СТАТУС |  |  | ALLE HBU STATUS
| ARRETEE |  |  | FAULTY |  |  | PARADO |  |  | PARADA |  |  | ИСПРАВНЫЙ |  |  | FEHLER
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | НЕИСПРАВНЫЙ |  |  | BETRIEB
| Tous états HBU |  |  | All HBU status |  |  | Todos HBU estado |  |  | HBU todo estado |  |  | Все HBU статус |  |  | Alle HBU Status
| 3 ¦ GlobalIEDStatus |  |  | 3 ¦ GlobalIEDStatus |  |  | 3 ¦ GlobalIEDStatus |  |  | 3 ¦ GlobalIEDStatus |  |  | 3 ¦ GlobalIEDStatus |  |  | 3 ¦ GlobalIEDStatus
| TOUS LES ETATS IED |  |  | ALL IED STATUS |  |  | TODOS LOS IED ESTADO |  |  | IED TODO ESTADO |  |  | ВСЕ IED СТАТУС |  |  | ALLE IED STATUS
| ARRETEE |  |  | FAULTY |  |  | PARADO |  |  | PARADA |  |  | ИСПРАВНЫЙ |  |  | FEHLER
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | НЕИСПРАВНЫЙ |  |  | BETRIEB
| Tous états IED |  |  | All IED status |  |  | Todos IED estado |  |  | IED todo estado |  |  | Все IED статус |  |  | Alle IED Status
| 3 ¦ GlobalPrinterStatus |  |  | 3 ¦ GlobalPrinterStatus |  |  | 3 ¦ GlobalPrinterStatus |  |  | 3 ¦ GlobalPrinterStatus |  |  | 3 ¦ GlobalPrinterStatus |  |  | 3 ¦ GlobalPrinterStatus
| TOUS LES ETATS D'IMPRIMANTES |  |  | ALL Printer STATUS |  |  | TODOS LOS IMPRESSORA ESTADO |  |  | IMPRESSORA TODO ESTADO |  |  | ВСЕ ПРИНТЕР СТАТУС |  |  | ALLE DRUCKER-STATUS
| ARRETEE |  |  | FAULTY |  |  | PARADO |  |  | PARADA |  |  | ИСПРАВНЫЙ |  |  | FEHLER
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | НЕИСПРАВНЫЙ |  |  | BETRIEB
| Tous états Impr. |  |  | All Printer stat |  |  | Todos Imp.estado |  |  | Todos Imp.estado |  |  | Все Принтер стат |  |  | Alle Druck.Status
| 3 ¦ GlobalRackLinkStatus |  |  | 3 ¦ GlobalRackLinkStatus |  |  | 3 ¦ GlobalRackLinkStatus |  |  | 3 ¦ GlobalRackLinkStatus |  |  | 3 ¦ GlobalRackLinkStatus |  |  | 3 ¦ GlobalRackLinkStatus
| TOUS LES ETATS RACK |  |  | ALL RACK STATUS |  |  | TODOS LOS RACK ESTADO |  |  | RACK TODO ESTADO |  |  | ВСЕ RACK СТАТУС |  |  | ALLE RACK STATUS
| ARRETEE |  |  | FAULTY |  |  | PARADO |  |  | PARADA |  |  | ИСПРАВНЫЙ |  |  | FEHLER
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | НЕИСПРАВНЫЙ |  |  | BETRIEB
| Tous états rack |  |  | All rack status |  |  | Todos rack estado |  |  | rack todo estado |  |  | Все rack статус |  |  | Alle rack status
| 3 ¦ RackLinkStatus |  |  | 3 ¦ RackLinkStatus |  |  | 3 ¦ RackLinkStatus |  |  | 3 ¦ RackLinkStatus |  |  | 3 ¦ RackLinkStatus |  |  | 3 ¦ RackLinkStatus
| ETAT DU LIEN RACK |  |  | RACK LINK STATUS |  |  | RACK DE ENLACE DE ESTADO |  |  | RACK LINK ESTADO |  |  | RACK СТАТУС |  |  | RACK LINK STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Etat lien Rack |  |  | Rack link status |  |  | Rack estado |  |  | Rack estado |  |  | Rack статус |  |  | Rack link status
| 3 ¦ LocalAlarmAck_SPS |  |  | 3 ¦ LocalAlarmAck_SPS |  |  | 3 ¦ LocalAlarmAck_SPS |  |  | 3 ¦ LocalAlarmAck_SPS |  |  | 3 ¦ LocalAlarmAck_SPS |  |  | 3 ¦ LocalAlarmAck_SPS
| ACQUITTEMENT ALARME LOCALE |  |  | LOCAL ALARM ACKNOWLEDGEMENT |  |  | RECONOCIMIENTO DE ALARMA LOCAL |  |  | LOCAIS ALARME AVISO |  |  | МЕСТНЫЕ СИГНАЛА ПОДТВЕРЖДЕНИЯ |  |  | LOKALEN ALARM ANERKENNUNG
| OUI |  |  | YES |  |  | SI |  |  | SIM |  |  | ДА |  |  | JA
| NON |  |  | NO |  |  | NO |  |  | NAO |  |  | НЕТ |  |  | NEIN
| Acq. Alarm loc |  |  | Local alarm ack |  |  | Recon Alarma loc |  |  | Loc Alarme aviso |  |  | Mес Сигнала подт |  |  | Zähler max
| 3 ¦ SettingDone |  |  | 3 ¦ SettingDone |  |  | 3 ¦ SettingDone |  |  | 3 ¦ SettingDone |  |  | 3 ¦ SettingDone |  |  | 3 ¦ SettingDone
| PARAMETRAGE EFFECTUE |  |  | SETTING DONE |  |  | AJUSTE DE HECHO |  |  | DEFINIR FEITO |  |  | НАСТРОЙКА ДЕЛАЕТСЯ |  |  | EINSTELLUNG ERFOLGT
| OUI |  |  | YES |  |  | SI |  |  | SIM |  |  | ДА |  |  | JA
| NON |  |  | NO |  |  | NO |  |  | NAO |  |  | НЕТ |  |  | NEIN
| Parametrage fait |  |  | Setting done |  |  | Ajuste de hecho |  |  | Definir feito |  |  | Настр делается |  |  | Einst. Erfolgt
| 3 ¦ SettingFileDiscordance |  |  | 3 ¦ SettingFileDiscordance |  |  | 3 ¦ SettingFileDiscordance |  |  | 3 ¦ SettingFileDiscordance |  |  | 3 ¦ SettingFileDiscordance |  |  | 3 ¦ SettingFileDiscordance
| DISCORDANCE FICHIER PARAMETRAGE |  |  | SETTING FILE DISCORDANCE |  |  | ARCHIVO DE CONFIGURACION DISCORDANCIA |  |  | DEFINIÇÃO ARQUIVO DISCORDANCIA |  |  | НАСТРОЙКА ФАЙЛОВ РАЗНОГОЛОСИЦА |  |  | EINSTELLUNG DATEI DISSONANZ
| OUI |  |  | YES |  |  | SI |  |  | SIM |  |  | ДА |  |  | JA
| NON |  |  | NO |  |  | NO |  |  | NAO |  |  | НЕТ |  |  | NEIN
| Disc.fich.param |  |  | Setting disc. |  |  | Arch.Conf.Disc. |  |  | Def.Arquivo Disc |  |  | Настр файлов раз |  |  | Einst.Dat.Diss.
| 3 ¦ SettingInProgress |  |  | 3 ¦ SettingInProgress |  |  | 3 ¦ SettingInProgress |  |  | 3 ¦ SettingInProgress |  |  | 3 ¦ SettingInProgress |  |  | 3 ¦ SettingInProgress
| PARAMETRAGE EN COURS |  |  | SETTING IN PROGRESS |  |  | AJUSTE EN MARCHA |  |  | DEFINIR EM ANDAMENTO |  |  | УСТАНОВЛЕНИЕ В ХОДЕ |  |  | EINSTELLUNG IN PROGRESS
| OUI |  |  | YES |  |  | SI |  |  | SIM |  |  | ДА |  |  | JA
| NON |  |  | NO |  |  | NO |  |  | NAO |  |  | НЕТ |  |  | NEIN
| Param en cours |  |  | Setting in prog. |  |  | Ajuste en marcha |  |  | Definir em Andam |  |  | Устан В Ходе |  |  | Einst. In prog.
| 3 ¦ SettingIncoherency |  |  | 3 ¦ SettingIncoherency |  |  | 3 ¦ SettingIncoherency |  |  | 3 ¦ SettingIncoherency |  |  | 3 ¦ SettingIncoherency |  |  | 3 ¦ SettingIncoherency
| PARAMETRAGE INCOHERENT |  |  | SETTING INCOHERENCY |  |  | AJUSTE INCOHERENCY |  |  | DEFINIR INCOHERENCY |  |  | УСТАНОВЛЕНИЕ НЕПОСЛЕДОВАТЕЛЬНОСТЬ |  |  | EINSTELLUNG INCOHERENCY
| OUI |  |  | YES |  |  | SI |  |  | SIM |  |  | ДА |  |  | JA
| NON |  |  | NO |  |  | NO |  |  | NAO |  |  | НЕТ |  |  | NEIN
| Param Invalide |  |  | Setting incoher. |  |  | Ajuste incoher. |  |  | Definir incoher. |  |  | Устан Непосл |  |  | Einst. Incoher.
SYSTEM INFORMATION MiCOM C364 |  |  |  | SYSTEM INFORMATION MiCOM C364 |  |  | SYSTEM INFORMATION MiCOM C364 |  |  | SYSTEM INFORMATION MiCOM C364 |  |  | SYSTEM INFORMATION MiCOM C364 |  |  | SYSTEM INFORMATION MiCOM C364
| 4 ¦ DBIncoherency |  |  | 4 ¦ DBIncoherency |  |  | 4 ¦ DBIncoherency |  |  | 4 ¦ DBIncoherency |  |  | 4 ¦ DBIncoherency |  |  | 4 ¦ DBIncoherency
| BD INCOHERENTE |  |  | DATABASE INCONSISTENCY |  |  | INCONSISTENCIA BASE DE DATOS |  |  | BD INCOERENTE |  |  | НЕСОВМЕСТИМОСТЬ БД |  |  | DATENBANK INKONSISTENZ
| OUI |  |  | YES |  |  | SI |  |  | SIM |  |  | ДА |  |  | JA
| NON |  |  | NO |  |  | NO |  |  | NAO |  |  | НЕТ |  |  | NEIN
| DB incoh. SPS |  |  | DB incoh. SPS |  |  | DB incoh. SPS |  |  | DB incoh. SPS |  |  | БД несовм. SPS |  |  | DB Inkonsistenz
| 4 ¦ DBSwitch_SPC |  |  | 4 ¦ DBSwitch_SPC |  |  | 4 ¦ DBSwitch_SPC |  |  | 4 ¦ DBSwitch_SPC |  |  | 4 ¦ DBSwitch_SPC |  |  | 4 ¦ DBSwitch_SPC
| PERMUTATION DE BD C364 |  |  | C364 DATABASE SWITCHING |  |  | CAMBIANDO BASE DE DATOS C364 |  |  | CHAVEAMENTO DE BD C364 |  |  | ПЕРЕКЛЮЧЕНИЕ БД НА С364 |  |  | C364 DATABASE UMSCHALTUNG
| EXECUTER |  |  | EXECUTE |  |  | EJECUTAR |  |  | EXECUTAR |  |  | ВЫПОЛНЕНИЕ |  |  | AUSFÜHREN
| - |  |  | - |  |  | - |  |  | - |  |  | - |  |  | -
| Permutation BD |  |  | DB switch ctrl |  |  | Ctrl Cambio BD |  |  | Chaveamento BD |  |  | БД Ком переключ. |  |  | DB switch ctrl
| 4 ¦ CommDevice |  |  | 4 ¦ CommDevice |  |  | 4 ¦ CommDevice |  |  | 4 ¦ CommDevice |  |  | 4 ¦ CommDevice |  |  | 4 ¦ CommDevice
| ETAT DU LIEN SBUS |  |  | C364 SBUS LINK |  |  | ENLACE C364 SBUS |  |  | ESTADO DA CONEXAO SBUS |  |  | СВЯЗЬ с сетью SBUS |  |  | C364 SBUS LINK
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Lien Equipement |  |  | Device link |  |  | Enlace Dispo. |  |  | Enlace Dispo. |  |  | Связь устройств. |  |  | Gerät Link
| 4 ¦ LocRemDevice_DPC |  |  | 4 ¦ LocRemDevice_DPC |  |  | 4 ¦ LocRemDevice_DPC |  |  | 4 ¦ LocRemDevice_DPC |  |  | 4 ¦ LocRemDevice_DPC |  |  | 4 ¦ LocRemDevice_DPC
| CHANGEMENT MODE DE CONTRÔLE C364 |  |  | C364 BAYS CONTROL MODE CHANGE |  |  | CAMBIO MODO CONTROL BAHIAS C364 |  |  | CHAVEAR MODO DE CONTROLE DA C364 |  |  | ИЗМЕНЕНИЕ РЕЖИМА УПРАВЛЕНИЯ ЯЧЕЙКАМИ С264 |  |  | C364 BAYS CONTROL MODE CHANGE
| DISTANT |  |  | REMOTE |  |  | REMOTO |  |  | REMOTO |  |  | ДИСТАНЦИОННЫЙ |  |  | FERN
| LOCAL |  |  | LOCAL |  |  | LOCAL |  |  | LOCAL |  |  | МЕСТНЫЙ |  |  | LOKAL
| Loc/Dst ctrl DPC |  |  | Loc/rem ctrl DPC |  |  | Loc/rem ctrl DPC |  |  | Loc/rem ctrl DPC |  |  | Мес/Дист ком DPC |  |  | Loc/rem ctrl DPC
| 4 ¦ LocRemDevice |  |  | 4 ¦ LocRemDevice |  |  | 4 ¦ LocRemDevice |  |  | 4 ¦ LocRemDevice |  |  | 4 ¦ LocRemDevice |  |  | 4 ¦ LocRemDevice
| ETAT DU MODE DE CONTRÔLE C364 |  |  | C364 MANAGED BAYS IN CONTROL MODE |  |  | BAHIAS DEL C364 EN MODO CONTROL |  |  | MODO DE CONTROLE DA C364 |  |  | С264 ОБСЛУЖИВАЕТ ЯЧЕЙКИ В РЕЖИМЕ УПРАВЛЕНИЯ |  |  | C364 MANAGED BAYS IN CONTROL MODE
| DISTANT |  |  | REMOTE |  |  | REMOTO |  |  | REMOTO |  |  | ДИСТАНЦИОННЫЙ |  |  | FERN
| LOCAL |  |  | LOCAL |  |  | LOCAL |  |  | LOCAL |  |  | МЕСТНЫЙ |  |  | LOKAL
| Local/Dist DPS |  |  | Local/remote DPS |  |  | Local/remoto DPS |  |  | Local/remoto DPS |  |  | Мес/Дист ком DPS |  |  | Fern/Lokal Sps
| 4 ¦ LocRemDeviceForIEC |  |  | 4 ¦ LocRemDeviceForIEC |  |  | 4 ¦ LocRemDeviceForIEC |  |  | 4 ¦ LocRemDeviceForIEC |  |  | 4 ¦ LocRemDeviceForIEC |  |  | 4 ¦ LocRemDeviceForIEC
| ETAT DU MODE DE CONTRÔLE C364 |  |  | C364 BAYS IN CONTROL MODE |  |  | BAHIAS C364 EN MODO CONTROL |  |  | MODO DE CONTROLE DA C364 |  |  | РЕЖИМ УПРАВЛЕНИЯ ЯЧЕЙКАМИ С264 |  |  | C364 FELDSTEUERMODUS
| DISTANT |  |  | REMOTE |  |  | REMOTO |  |  | REMOTO |  |  | ДИСТАНЦИОННЫЙ |  |  | FERN
| LOCAL |  |  | LOCAL |  |  | LOCAL |  |  | LOCAL |  |  | МЕСТНЫЙ |  |  | LOKAL
| Local/Dist SPS |  |  | Local/remote SPS |  |  | Local/remoto SPS |  |  | Local/remoto SPS |  |  | Мес/Дист ком SPS |  |  | Fern/Lokal SPS
| 4 ¦ LogQueue |  |  | 4 ¦ LogQueue |  |  | 4 ¦ LogQueue |  |  | 4 ¦ LogQueue |  |  | 4 ¦ LogQueue |  |  | 4 ¦ LogQueue
| ETAT DE LA FILE D'IMPRESSION |  |  | LOGGING QUEUE STATUS |  |  | ESTADO COLA DE EVENTOS |  |  | ESTADO DA FILA DE EVENTOS |  |  | СНЯТИЕ ПОКАЗАНИЯ СТАТУСА ОЧЕРЕДИ |  |  | LOGGING QUEUE STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| File impression |  |  | Log Queue |  |  | Cola de Eventos |  |  | Fila de Eventos |  |  | Лог очереди |  |  | Log Queue
| 4 ¦ ModeDevice_DPC |  |  | 4 ¦ ModeDevice_DPC |  |  | 4 ¦ ModeDevice_DPC |  |  | 4 ¦ ModeDevice_DPC |  |  | 4 ¦ ModeDevice_DPC |  |  | 4 ¦ ModeDevice_DPC
| CHANGER LE MODE D'EXPLOITATION C364 |  |  | C364 FORCE OPERATION MODE TO |  |  | FORZAR C364 MODO DE OPERACIÓN A |  |  | CHAVEAR C364 MODO DE OPERACAO |  |  | C364 Силу режиме для |  |  | C364 SETZE GERÄTEMODUS IN
| OPERATIONNEL |  |  | OPERATIONNAL |  |  | OPERACIONAL |  |  | OPERACIONAL |  |  | В РАБОТЕ |  |  | BERTIEBSMODUS
| MAINTENANCE |  |  | MAINTENANCE |  |  | MANTENIMIENTO |  |  | MANUTENCAO |  |  | ОБСЛУЖИВАНИЕ |  |  | WARTUNG
| Mode ctrl DPC |  |  | Mode control DPC |  |  | Modo control DPC |  |  | Modo control DPC |  |  | Команда режима |  |  | MODUS UMSCHALT
| 4 ¦ OperatingMode |  |  | 4 ¦ OperatingMode |  |  | 4 ¦ OperatingMode |  |  | 4 ¦ OperatingMode |  |  | 4 ¦ OperatingMode |  |  | 4 ¦ OperatingMode
| MODE OPERATIONNEL C364 |  |  | C364 OPERATING MODE |  |  | C364 MODO OPERACIÓN |  |  | C364 MODO DE OPERACAO |  |  | Режим работы C364 |  |  | C364 BETRIEBSMODUS
| Mode d'Operation |  |  | Operating mode |  |  | Modo Operacional |  |  | Modo do operacao |  |  | Режим работы |  |  | Operating mode
| 4 ¦ SoftError |  |  | 4 ¦ SoftError |  |  | 4 ¦ SoftError |  |  | 4 ¦ SoftError |  |  | 4 ¦ SoftError |  |  | 4 ¦ SoftError
| ERREUR LOGICIELLE DETECTEE |  |  | SOFTWARE ERROR DETECTED |  |  | ERROR DETECTADO SOFTWARE |  |  | ERRO DE SOFTWARE DETECTADO |  |  | ОБНАРУЖЕНА ОШИБКА ПО |  |  | SOFTWAREFEHLER
| OUI |  |  | YES |  |  | SI |  |  | SIM |  |  | ДА |  |  | JA
| NON |  |  | NO |  |  | NO |  |  | NAO |  |  | НЕТ |  |  | NEIN
| Err. Logicielle |  |  | Soft. error SPS |  |  | Error Soft. SPS |  |  | Soft. error SPS |  |  | Ошибка по SPS |  |  | Softwarefehler
| 4 ¦ SyncDevice |  |  | 4 ¦ SyncDevice |  |  | 4 ¦ SyncDevice |  |  | 4 ¦ SyncDevice |  |  | 4 ¦ SyncDevice |  |  | 4 ¦ SyncDevice
| ETAT DE SYNCHRONISATION C364 |  |  | C364 SYNCHRONIZATION STATUS |  |  | ESATDO SINCRONIZACION C364 |  |  | ESTADO DA SINCRONIZACAO C364 |  |  | СТАТУС СИНХРОНИЗАЦИИ C364 |  |  | C364 SYNCHRONISIERUNG STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Synchronisation |  |  | Synchronisation |  |  | Sincronización |  |  | Sincronizacao |  |  | Синхронизация |  |  | Synchronisation
| 4 ¦ TestDevice_DPC |  |  | 4 ¦ TestDevice_DPC |  |  | 4 ¦ TestDevice_DPC |  |  | 4 ¦ TestDevice_DPC |  |  | 4 ¦ TestDevice_DPC |  |  | 4 ¦ TestDevice_DPC
| CHANGEMENT MODE EXPLOITATION C364 |  |  | C364 CHANGE EXPLOITATION MODE |  |  | CAMBIO MODO EXPLOTACION C364 |  |  | CHAVEAR MODO DE OPERACAO C364 |  |  | Смена режима работы C364 |  |  | C364 TESTMODUS UMSCHALT
| OPERATIONNEL |  |  | NORMAL |  |  | NORMAL |  |  | OPERACIONAM |  |  | НОРМАЛЬНЫЙ |  |  | NORMAL
| TEST |  |  | TEST |  |  | PRUEBA |  |  | TESTE |  |  | ТЕСТОВОЙ |  |  | TEST
| Ctrl Test DPC |  |  | Test control DPC |  |  | Ctrl Prueba DPC |  |  | Ctrl Prueba DPC |  |  | ком Тестов. DPC |  |  | Testmodus DPC
| 4 ¦ WatchdogError |  |  | 4 ¦ WatchdogError |  |  | 4 ¦ WatchdogError |  |  | 4 ¦ WatchdogError |  |  | 4 ¦ WatchdogError |  |  | 4 ¦ WatchdogError
| ETAT DU CHIEN DE GARDE C364 |  |  | C364 WATCHDOG RELAY STATUS |  |  | ESTADO RELE WATCHDOG C364 |  |  | ESTADO RELE WATCHDOG C364 |  |  | СТАТУС WATCHDOG C364 |  |  | C364 WATCHDOG RELAIS STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | ATIVO |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Watchdog SPS |  |  | Watchdog SPS |  |  | Watchdog SPS |  |  | Watchdog SPS |  |  | Watchdog SPS |  |  | Watchdog SPS
| 4 ¦ ModeDevice |  |  | 4 ¦ ModeDevice |  |  | 4 ¦ ModeDevice |  |  | 4 ¦ ModeDevice |  |  | 4 ¦ ModeDevice |  |  | 4 ¦ ModeDevice
| V3 MODE OPERATIONNEL |  |  | C364 OPERATING MODE |  |  | C364 MODO OPERACIÓN DISPOSITIVO |  |  | V3 MODO DE OPERACAO |  |  | РЕЖИМ РАБОТЫ C364 |  |  | C364 BETRIEBSMODUS
| OPERATIONNEL |  |  | RUNNING |  |  | EN SERVICIO |  |  | EM SERVICO |  |  | Рабочее |  |  | BETRIEB
| MAINTENANCE |  |  | MAINTENANCE |  |  | MANTENIMIENTO |  |  | MANUTENCAO |  |  | ОБСЛУЖИВАНИЕ |  |  | WARTUNG
| Mode Eqpt |  |  | Device mode |  |  | Modo Dispositivo |  |  | Modo Dispositivo |  |  | Режим устройства |  |  | Gerätemodus
| 4 ¦ ExtClockStatus |  |  | 4 ¦ ExtClockStatus |  |  | 4 ¦ ExtClockStatus |  |  | 4 ¦ ExtClockStatus |  |  | 4 ¦ ExtClockStatus |  |  | 4 ¦ ExtClockStatus
| ETAT DE LA SOURCE DE SYNCHRONISATION |  |  | GPS SYNCHRONISATION SOURCE |  |  | FUENTE SINCRONIZACION GPS |  |  | FONTE SINCRONIZACAO GPS |  |  | GPS ИСТОЧНИК СИНХРОНИЗАЦИИ |  |  | GPS SYNCHRONISIERUNG QUELLE
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Etat Horloge |  |  | Ext clock status |  |  | Estado Reloj GPS |  |  | Estado Reloj GPS |  |  | Статус IRIG-B |  |  | Ext Uhr Status
| 4 ¦ RedDevice |  |  | 4 ¦ RedDevice |  |  | 4 ¦ RedDevice |  |  | 4 ¦ RedDevice |  |  | 4 ¦ RedDevice |  |  | 4 ¦ RedDevice
| MODE DE REDONDANCE C364 |  |  | C364 REDUNDANCY MODE |  |  | MODO REDUNDANCIA C364 |  |  | MODO REDUNDANCIA C364 |  |  | C364 Режим резервирования |  |  | C364 REDUNDANZ MODUS
| ACTIF |  |  | ACTIVE |  |  | ACTIVO |  |  | ATIVO |  |  | ОСНОВНОЙ |  |  | AKTIV
| RESERVE |  |  | STANDBY |  |  | EN ESPERA |  |  | RESERVA |  |  | РЕЗЕРВНЫЙ |  |  | RESERVE
| Mode Redondance |  |  | Redundancy mode |  |  | Modo Redundancia |  |  | Modo Redundancia |  |  | Режим резерва |  |  | Redundanzmodus
| 4 ¦ CommIED |  |  | 4 ¦ CommIED |  |  | 4 ¦ CommIED |  |  | 4 ¦ CommIED |  |  | 4 ¦ CommIED |  |  | 4 ¦ CommIED
| ETAT DE LA CONNECTION AU C364 |  |  | IED CONNECTION STATUS TO C364 |  |  | ESTADO COMUNICACIÓN IED AL C364 |  |  | ESTADO DA CONEXAO COM A C364 |  |  | СТАТУС СВЯЗИ IED С С264 |  |  | IED VERBINDUNGSSTATUS C364
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Com. IED SPS |  |  | IED SPS com. |  |  | IED SPS com. |  |  | IED SPS com. |  |  | IED SPS связь. |  |  | IED SPS com.
| 4 ¦ SyncIED |  |  | 4 ¦ SyncIED |  |  | 4 ¦ SyncIED |  |  | 4 ¦ SyncIED |  |  | 4 ¦ SyncIED |  |  | 4 ¦ SyncIED
| ETAT DE LA SYNCHRONISATION DE L'IED |  |  | IED SYNCHRONISATION STATUS |  |  | ESTADO SINCRONIZACION IED |  |  | ESTADO DA SINCRONIZACAO DO RELE |  |  | IED СТАТУС СИНХРОНИЗАЦИИ |  |  | IED SYNCHRONISIERUNGSSTATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Synchro. IED SPS |  |  | IED SPS Synchro. |  |  | IED SPS Sincro. |  |  | IED SPS Sincro. |  |  | IED SPS синхр. |  |  | IED SPS Synchro.
| 4 ¦ DisturbIED |  |  | 4 ¦ DisturbIED |  |  | 4 ¦ DisturbIED |  |  | 4 ¦ DisturbIED |  |  | 4 ¦ DisturbIED |  |  | 4 ¦ DisturbIED
| FICHIER DE PERTURBOGRAPHIE IED |  |  | IED DISTURBANCE FILE |  |  | ARCHIVO DE DISTURBIO EN IED |  |  | ARQUIVO DE OSCILOGRAFIA IED |  |  | IED ФАЙЛ ОСЦИЛОГРАМ |  |  | IED DISTURBANCE FILE
| PRÊT |  |  | READY |  |  | LISTO |  |  | PRONTO |  |  | ГОТОВ |  |  | BEREIT
| ABSENT |  |  | NOT READY |  |  | NO LISTO |  |  | AUSENTE |  |  | НЕ ГОТОВ |  |  | NICHT BEREIT
| IED DREC Prêt |  |  | IED DREC ready |  |  | IED DREC Listo |  |  | IED DREC Pronto |  |  | IED DRECготов |  |  | IED DREC ready
| 4 ¦ ISAGRAFStatus |  |  | 4 ¦ ISAGRAFStatus |  |  | 4 ¦ ISAGRAFStatus |  |  | 4 ¦ ISAGRAFStatus |  |  | 4 ¦ ISAGRAFStatus |  |  | 4 ¦ ISAGRAFStatus
| ETAT ISAGRAF |  |  | ISAGRAF STATUS |  |  | ESTADO ISAGRAF |  |  | ESTADO ISAGRAF |  |  | ISAGRAF статус |  |  | ISAGRAF STATUS
| Etat ISAGRAF |  |  | ISAGRAF status |  |  | Estado ISAGRAF |  |  | Estado ISAGRAF |  |  | ISAGRAF статус |  |  | ISAGRAF status
| 4 ¦ RedSCADA |  |  | 4 ¦ RedSCADA |  |  | 4 ¦ RedSCADA |  |  | 4 ¦ RedSCADA |  |  | 4 ¦ RedSCADA |  |  | 4 ¦ RedSCADA
| PORT DE COMMUNICATION C364 AVEC LE SCADA |  |  | C364 SCADA PORT COMMUNICATION |  |  | PTO. COM C364 SCADA |  |  | CANAL DE COMUNICACAO C364 C/ SCADA |  |  | СТАТУС ПОРТА СВЯЗЬ C364 с SCADA |  |  | C364 FWL PORT KOMMUNIKATION
| ACTIF |  |  | ACTIVE |  |  | ACTIVO |  |  | ATIVO |  |  | ОСНОВНОЙ |  |  | AKTIV
| RESERVE |  |  | STANDBY |  |  | EN ESPERA |  |  | RESERVA |  |  | РЕЗЕРВНЫЙ |  |  | RESERVE
| SPS Redondance |  |  | Redundancy SPS |  |  | Redundancia SPS |  |  | Redundancia SPS |  |  | резервирование |  |  | Redundancy SPS
| 4 ¦ CommSCADA |  |  | 4 ¦ CommSCADA |  |  | 4 ¦ CommSCADA |  |  | 4 ¦ CommSCADA |  |  | 4 ¦ CommSCADA |  |  | 4 ¦ CommSCADA
| ETAT DE LA COMMUNICATION SCADA C364 |  |  | SCADA CONNECTION STATUS TO C364 |  |  | EDO. CONEXIÓN SCADA AL C364 |  |  | ESTADO DA CONEXAO C364 C/ SCADA |  |  | СТАТУС СОЕДИНЕНИЯ SCADA С C364 |  |  | FWL VERBINDUNGSSTATUS C364
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Com. SCADA SPS |  |  | SCADA SPS com. |  |  | SCADA SPS com. |  |  | SCADA SPS com. |  |  | SCADA SPS связь |  |  | FWL SPS KOMMU
SYSTEM INFORMATION UCA2 IED |  |  |  | SYSTEM INFORMATION UCA2 IED |  |  | SYSTEM INFORMATION UCA2 IED |  |  | SYSTEM INFORMATION UCA2 IED |  |  | SYSTEM INFORMATION UCA2 IED |  |  | SYSTEM INFORMATION UCA2 IED
| 5 ¦ CommDevice |  |  | 5 ¦ CommDevice |  |  | 5 ¦ CommDevice |  |  | 5 ¦ CommDevice |  |  | 5 ¦ CommDevice |  |  | 5 ¦ CommDevice
| ETAT DU LIEN IED SBUS |  |  | IED SBUS LINK |  |  | ENLACE IED SBUS |  |  | ESTADO DA CONEXAO IED SBUS |  |  | IED SBUS связь |  |  | IED SBUS LINK
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Lien Equipement |  |  | Device link |  |  | Enlace Dispo. |  |  | Enlace Dispo. |  |  | Связь устройств. |  |  | Gerät Link
SYSTEM INFORMATION GATEWAY |  |  |  | SYSTEM INFORMATION GATEWAY |  |  | SYSTEM INFORMATION GATEWAY |  |  | SYSTEM INFORMATION GATEWAY |  |  | SYSTEM INFORMATION GATEWAY |  |  | SYSTEM INFORMATION GATEWAY
| 6 ¦ DBSwitch_SPC |  |  | 6 ¦ DBSwitch_SPC |  |  | 6 ¦ DBSwitch_SPC |  |  | 6 ¦ DBSwitch_SPC |  |  | 6 ¦ DBSwitch_SPC |  |  | 6 ¦ DBSwitch_SPC
| PERMUTATION DE BD GTW |  |  | GTW DATABASE SWITCHING |  |  | CAMBIANDO BASE DE DATOS GTW |  |  | CHAVEAMENTO DE BD GTW |  |  | ПЕРЕКЛЮЧЕНИЕ БД GTW |  |  | GTW DATENBANKUMSCHALTUNG
| EXECUTER |  |  | EXECUTE |  |  | EJECUTAR |  |  | EXECUTAR |  |  | ВЫПОЛНЕНИЕ |  |  | AUSFÜHREN
| - |  |  | - |  |  | - |  |  | - |  |  | - |  |  | -
| Permutation BD |  |  | DB switch ctrl |  |  | Ctrl Cambio BD |  |  | Chaveamento BD |  |  | БД Ком переключ. |  |  | DB switch ctrl
| 6 ¦ CommDevice |  |  | 6 ¦ CommDevice |  |  | 6 ¦ CommDevice |  |  | 6 ¦ CommDevice |  |  | 6 ¦ CommDevice |  |  | 6 ¦ CommDevice
| ETAT DU LIEN GTW SBUS |  |  | GTW SBUS LINK |  |  | ENLACE GTW SBUS |  |  | ESTADO DA CONEXAO GTW SBUS |  |  | GTW SBUS СВЯЗЬ |  |  | GTW SBUS LINK
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Lien Equipement |  |  | Device link |  |  | Enlace Dispo. |  |  | Enlace Dispo. |  |  | Связь устройств. |  |  | Device link
| 6 ¦ ModeDevice_DPC |  |  | 6 ¦ ModeDevice_DPC |  |  | 6 ¦ ModeDevice_DPC |  |  | 6 ¦ ModeDevice_DPC |  |  | 6 ¦ ModeDevice_DPC |  |  | 6 ¦ ModeDevice_DPC
| CHANGER LE MODE D'EXPLOITATION GTW |  |  | GTW FORCE OPERATION MODE TO |  |  | FORZAR GTW MODO DE OPERACIÓN A |  |  | CHAVEAR GTW MODO DE OPERACAO |  |  | GTW ПЕРЕЙТИ В РЕЖИМ |  |  | GTW UMSCHALTUNG BETRIEBSMODUS
| OPERATIONNEL |  |  | OPERATIONNAL |  |  | OPERACIONAL |  |  | OPERACIONAL |  |  | В РАБОТЕ |  |  | BERTIEBSMODUS
| MAINTENANCE |  |  | MAINTENANCE |  |  | MANTENIMIENTO |  |  | MANUTENCAO |  |  | ОБСЛУЖИВАНИЕ |  |  | WARTUNG
| Mode ctrl DPC |  |  | Mode control DPC |  |  | Modo control DPC |  |  | Modo control DPC |  |  | Команда режима |  |  | MODUS UMSCHALT
| 6 ¦ OperatingMode |  |  | 6 ¦ OperatingMode |  |  | 6 ¦ OperatingMode |  |  | 6 ¦ OperatingMode |  |  | 6 ¦ OperatingMode |  |  | 6 ¦ OperatingMode
| MODE OPERATIONNEL GTW |  |  | GTW OPERATING MODE |  |  | MODO OPERACIONAL GTW |  |  | GTW MODO DE OPERACAO |  |  | GTW Режим работы |  |  | GTW BETRIEBSMODUS
| Mode d'Operation |  |  | Operating mode |  |  | Modo Operacional |  |  | Modo do operacao |  |  | Режим работы |  |  | Operating mode
| 6 ¦ SyncDevice |  |  | 6 ¦ SyncDevice |  |  | 6 ¦ SyncDevice |  |  | 6 ¦ SyncDevice |  |  | 6 ¦ SyncDevice |  |  | 6 ¦ SyncDevice
| ETAT DE SYNCHRONISATION GTW |  |  | GTW SYNCHRONISATION STATUS |  |  | ESTADO SINCRONIZACION GTW |  |  | ESTADO DA SINCRONIZACAO GTW |  |  | GTW СТАТУС СИНХРОНИЗАЦИИ |  |  | GTW SYNCHRONISATION STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Synchronisation |  |  | Synchronisation |  |  | Sincronización |  |  | Sincronizacao |  |  | Синхронизация |  |  | Synchronisation
| 6 ¦ RedSCADA |  |  | 6 ¦ RedSCADA |  |  | 6 ¦ RedSCADA |  |  | 6 ¦ RedSCADA |  |  | 6 ¦ RedSCADA |  |  | 6 ¦ RedSCADA
| PORT DE COMMUNICATION GTW AVEC LE SCADA |  |  | GTW SCADA PORT COMMUNICATION |  |  | PTO. COM GTW SCADA |  |  | CANAL DE COMUNICACAO GTW C/ SCADA |  |  | СТАТУС ПОРТА СВЯЗЬ GTW c SCADA |  |  | GTW FWL PORT KOMMUNIKATION
| ACTIF |  |  | ACTIVE |  |  | ACTIVO |  |  | ATIVO |  |  | ОСНОВНОЙ |  |  | AKTIV
| RESERVE |  |  | STANDBY |  |  | EN ESPERA |  |  | RESERVA |  |  | РЕЗЕРВНЫЙ |  |  | RESERVE
| SPS Redondance |  |  | Redundancy SPS |  |  | Redundancia SPS |  |  | Redundancia SPS |  |  | резервирование |  |  | Redundancy SPS
| 6 ¦ CommSCADA |  |  | 6 ¦ CommSCADA |  |  | 6 ¦ CommSCADA |  |  | 6 ¦ CommSCADA |  |  | 6 ¦ CommSCADA |  |  | 6 ¦ CommSCADA
| ETAT DE LA COMMUNICATION GTW SCADA |  |  | SCADA CONNECTION STATUS TO GTW |  |  | EDO. CONEXIÓN SCADA AL GTW |  |  | ESTADO DA CONEXAO GTW C/ SCADA |  |  | СТАТУС СОЕДИНЕНИЯ SCADA С GTW |  |  | FWL VERBINDUNGSSTATUS GTW
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Com. SCADA SPS |  |  | SCADA SPS com. |  |  | SCADA SPS com. |  |  | SCADA SPS com. |  |  | SCADA SPS связь |  |  | FWL SPS KOMMU
| 6 ¦ CommIED |  |  | 6 ¦ CommIED |  |  | 6 ¦ CommIED |  |  | 6 ¦ CommIED |  |  | 6 ¦ CommIED |  |  | 6 ¦ CommIED
| ETAT DE LA CONNECTION GTW |  |  | IED CONNECTION STATUS TO GTW |  |  | ESTADO COMUNICACIÓN IED AL GTW |  |  | ESTADO DA CONEXAO COM A GTW |  |  | СТАТУС СВЯЗИ IED С GTW |  |  | IED VERBINDUNGSSTATUS GTW
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Com. IED SPS |  |  | IED SPS com. |  |  | IED SPS com. |  |  | IED SPS com. |  |  | IED SPS связь. |  |  | IED SPS com.
| 6 ¦ SyncIED |  |  | 6¦ SyncIED |  |  | 6 ¦ SyncIED |  |  | 6 ¦ SyncIED |  |  | 6 ¦ SyncIED |  |  | 6 ¦ SyncIED
| ETAT DE LA SYNCHRONISATION DE L'IED |  |  | IED SYNCHRONISATION STATUS |  |  | ESTADO SINCRONIZACION IED |  |  | ESTADO DA SINCRONIZACAO DO RELE |  |  | IED СТАТУС СИНХРОНИЗАЦИИ |  |  | IED SYNCHRONISIERUNGSSTATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Synchro. IED SPS |  |  | IED SPS Synchro. |  |  | IED SPS Sincro. |  |  | IED SPS Sincro. |  |  | IED SPS синхр. |  |  | IED SPS Synchro.
| 6 ¦ ISAGRAFStatus |  |  | 6 ¦ ISAGRAFStatus |  |  | 6 ¦ ISAGRAFStatus |  |  | 6 ¦ ISAGRAFStatus |  |  | 6 ¦ ISAGRAFStatus |  |  | 6 ¦ ISAGRAFStatus
| ETAT ISAGRAF |  |  | ISAGRAF STATUS |  |  | ESTADO ISAGRAF |  |  | ESTADO ISAGRAF |  |  | ISAGRAF статус |  |  | ISAGRAF STATUS
| Etat ISAGRAF |  |  | ISAGRAF status |  |  | Estado ISAGRAF |  |  | Estado ISAGRAF |  |  | ISAGRAF статус |  |  | ISAGRAF status
SYSTEM INFORMATION IEC 61850 |  |  |  | SYSTEM INFORMATION IEC 61850 |  |  | SYSTEM INFORMATION IEC 61850 |  |  | SYSTEM INFORMATION IEC 61850 |  |  | SYSTEM INFORMATION IEC 61850 |  |  | SYSTEM INFORMATION IEC 61850
| 7 ¦ CommDevice |  |  | 7 ¦ CommDevice |  |  | 7 ¦ CommDevice |  |  | 7 ¦ CommDevice |  |  | 7 ¦ CommDevice |  |  | 7 ¦ CommDevice
| ETAT DU LIEN IED SBUS |  |  | IED SBUS LINK |  |  | ENLACE IED SBUS |  |  | ESTADO DA CONEXAO IED SBUS |  |  | IED SBUS связь |  |  | IED SBUS LINK
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Lien Equipement |  |  | Device link |  |  | Enlace Dispo. |  |  | Enlace Dispo. |  |  | Связь устройств. |  |  | Gerät Link
| 7 ¦ OperatingMode |  |  | 7 ¦ OperatingMode |  |  | 7 ¦ OperatingMode |  |  | 7 ¦ OperatingMode |  |  | 7 ¦ OperatingMode |  |  | 7 ¦ OperatingMode
| MODE OPERATIONNEL |  |  | IED OPERATING MODE |  |  | IED MODO OPERACIÓN |  |  | MODO DE OPERACAO |  |  | Режим работы IED |  |  | IED BETRIEBSMODUS
| Mode d'Operation |  |  | Operating mode |  |  | Modo Operacional |  |  | Modo do operacao |  |  | Режим работы |  |  | Operating mode
| 7 ¦ ModeDevice_DPC |  |  | 7 ¦ ModeDevice_DPC |  |  | 7 ¦ ModeDevice_DPC |  |  | 7 ¦ ModeDevice_DPC |  |  | 7 ¦ ModeDevice_DPC |  |  | 7 ¦ ModeDevice_DPC
| CHANGER LE MODE D'EXPLOITATION |  |  | IED FORCE OPERATION MODE TO |  |  | FORZAR IED MODO DE OPERACIÓN A |  |  | CHAVEAR MODO DE OPERACAO |  |  | IED Силу режиме для |  |  | IED SETZE GERÄTEMODUS IN
| OPERATIONNEL |  |  | OPERATIONNAL |  |  | OPERACIONAL |  |  | OPERACIONAL |  |  | В РАБОТЕ |  |  | BERTIEBSMODUS
| MAINTENANCE |  |  | MAINTENANCE |  |  | MANTENIMIENTO |  |  | MANUTENCAO |  |  | ОБСЛУЖИВАНИЕ |  |  | WARTUNG
| Mode ctrl DPC |  |  | Mode control DPC |  |  | Modo control DPC |  |  | Modo control DPC |  |  | Команда режима |  |  | MODUS UMSCHALT
| 7 ¦ RedDevice |  |  | 7 ¦ RedDevice |  |  | 7 ¦ RedDevice |  |  | 7 ¦ RedDevice |  |  | 7 ¦ RedDevice |  |  | 7 ¦ RedDevice
| MODE DE REDONDANCE |  |  | REDUNDANCY MODE |  |  | MODO REDUNDANCIA |  |  | MODO REDUNDANCIA |  |  | РЕЖИМ РЕЗЕРВА |  |  | REDUNDANCY MODE
| ACTIF |  |  | ACTIVE |  |  | ACTIVO |  |  | ATIVO |  |  | ОСНОВНОЙ |  |  | AKTIV
| RESERVE |  |  | STANDBY |  |  | EN ESPERA |  |  | RESERVA |  |  | РЕЗЕРВНЫЙ |  |  | RESERVE
| Mode Redondance |  |  | Redundancy mode |  |  | Modo Redundancia |  |  | Modo Redundancia |  |  | Режим резерва |  |  | Redundanzmodus
| 7 ¦ DisturbUCA2 |  |  | 7 ¦ DisturbUCA2 |  |  | 7 ¦ DisturbUCA2 |  |  | 7 ¦ DisturbUCA2 |  |  | 7 ¦ DisturbUCA2 |  |  | 7 ¦ DisturbUCA2
| FICHIER DE PERTURBOGRAPHIE IED |  |  | DISTURBANCE FILE ON IED |  |  | ARCHIVO DE DISTURBIO EN IED |  |  | ARQUIVO DE OSCILOGRAFIA IED |  |  | ФАЙЛ ОСЦИЛОГРАМ НА IED |  |  | STÖRFALLDATEI AUF IED
| PRÊT |  |  | READY |  |  | LISTO |  |  | PRONTO |  |  | ГОТОВ |  |  | BEREIT
| ABSENT |  |  | NOT READY |  |  | NO LISTO |  |  | AUSENTE |  |  | НЕ ГОТОВ |  |  | NICHT BEREIT
| DREC prêt |  |  | DREC ready |  |  | DREC Listo |  |  | DREC Pronto |  |  | DREC готов |  |  | DREC ready
| 7 ¦ DisturbLD |  |  | 7 ¦ DisturbLD |  |  | 7 ¦ DisturbLD |  |  | 7 ¦ DisturbLD |  |  | 7 ¦ DisturbLD |  |  | 7 ¦ DisturbLD
| FICHIER DE PERTURBOGRAPHIE LD |  |  | LOGICAL DEVICE DISTURBANCE FILE |  |  | ARCHIVO DE DISTURBIO LD |  |  | ARQUIVO DE OSCILOGRAFIA LD |  |  | ФАЙЛ ОСЦИЛОГРАМ LD |  |  | STÖRFALLDATEI LD
| PRÊT |  |  | READY |  |  | LISTO |  |  | PRONTO |  |  | ГОТОВ |  |  | BEREIT
| ABSENT |  |  | NOT READY |  |  | NO LISTO |  |  | AUSENTE |  |  | НЕ ГОТОВ |  |  | NICHT BEREIT
| LD DREC prêt |  |  | LD DREC ready |  |  | LD DREC Listo |  |  | LD DREC Pronto |  |  | LD DREC готов |  |  | LD DREC ready
| 7 ¦ UCA2GenSPS |  |  | 7 ¦ UCA2GenSPS |  |  | 7 ¦ UCA2GenSPS |  |  | 7 ¦ UCA2GenSPS |  |  | 7 ¦ UCA2GenSPS |  |  | 7 ¦ UCA2GenSPS
| IEC61850 GENERIC SPS |  |  | IEC61850 GENERIC SPS |  |  | IEC61850 GENERIC SPS |  |  | IEC61850 GENERIC SPS |  |  | IEC61850 GENERIC SPS |  |  | IEC61850 GENERIC SPS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| IEC61850 gen SPS |  |  | IEC61850 gen SPS |  |  | IEC61850 gen SPS |  |  | IEC61850 gen SPS |  |  | IEC61850 gen SPS |  |  | IEC61850 gen SPS
| 7 ¦ UCA2GenDPS |  |  | 7 ¦ UCA2GenDPS |  |  | 7 ¦ UCA2GenDPS |  |  | 7 ¦ UCA2GenDPS |  |  | 7 ¦ UCA2GenDPS |  |  | 7 ¦ UCA2GenDPS
| IEC61850 GENERIC DPS |  |  | IEC61850 GENERIC DPS |  |  | IEC61850 GENERIC DPS |  |  | IEC61850 GENERIC DPS |  |  | IEC61850 GENERIC DPS |  |  | IEC61850 GENERIC DPS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| IEC61850 gen DPS |  |  | IEC61850 gen DPS |  |  | IEC61850 gen DPS |  |  | IEC61850 gen DPS |  |  | IEC61850 gen DPS |  |  | IEC61850 gen DPS
| 7 ¦ UCA2GenMPS |  |  | 7 ¦ UCA2GenMPS |  |  | 7 ¦ UCA2GenMPS |  |  | 7 ¦ UCA2GenMPS |  |  | 7 ¦ UCA2GenMPS |  |  | 7 ¦ UCA2GenMPS
| IEC61850 GENERIC MPS |  |  | IEC61850 GENERIC MPS |  |  | IEC61850 GENERIC MPS |  |  | IEC61850 GENERIC MPS |  |  | IEC61850 GENERIC MPS |  |  | IEC61850 GENERIC MPS
| IEC61850 gen MPS |  |  | IEC61850 gen MPS |  |  | IEC61850 gen MPS |  |  | IEC61850 gen MPS |  |  | IEC61850 gen MPS |  |  | IEC61850 gen MPS
| 7 ¦ UCA2GenSPC |  |  | 7 ¦ UCA2GenSPC |  |  | 7 ¦ UCA2GenSPC |  |  | 7 ¦ UCA2GenSPC |  |  | 7 ¦ UCA2GenSPC |  |  | 7 ¦ UCA2GenSPC
| IEC61850 GENERIC SPC |  |  | IEC61850 GENERIC SPC |  |  | IEC61850 GENERIC SPC |  |  | IEC61850 GENERIC SPC |  |  | IEC61850 GENERIC SPC |  |  | IEC61850 GENERIC SPC
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| IEC61850 gen SPC |  |  | IEC61850 gen SPC |  |  | IEC61850 gen SPC |  |  | IEC61850 gen SPC |  |  | IEC61850 gen SPC |  |  | IEC61850 gen SPC
| 7 ¦ UCA2GenDPC |  |  | 7 ¦ UCA2GenDPC |  |  | 7 ¦ UCA2GenDPC |  |  | 7 ¦ UCA2GenDPC |  |  | 7 ¦ UCA2GenDPC |  |  | 7 ¦ UCA2GenDPC
| IEC61850 GENERIC DPC |  |  | IEC61850 GENERIC DPC |  |  | IEC61850 GENERIC DPC |  |  | IEC61850 GENERIC DPC |  |  | IEC61850 GENERIC DPC |  |  | IEC61850 GENERIC DPC
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| IEC61850 gen DPC |  |  | IEC61850 gen DPC |  |  | IEC61850 gen DPC |  |  | IEC61850 gen DPC |  |  | IEC61850 gen DPC |  |  | IEC61850 gen DPC
| 7 ¦ UCA2GenMV |  |  | 7 ¦ UCA2GenMV |  |  | 7 ¦ UCA2GenMV |  |  | 7 ¦ UCA2GenMV |  |  | 7 ¦ UCA2GenMV |  |  | 7 ¦ UCA2GenMV
| IEC61850 GENERIC MV |  |  | IEC61850 GENERIC MV |  |  | IEC61850 GENERIC MV |  |  | IEC61850 GENERIC MV |  |  | IEC61850 GENERIC MV |  |  | IEC61850 GENERIC MV
| IEC61850 gen MV |  |  | IEC61850 gen MV |  |  | IEC61850 gen MV |  |  | IEC61850 gen MV |  |  | IEC61850 gen MV |  |  | IEC61850 gen MV
SYSTEM INFORMATION BAY OI |  |  |  | SYSTEM INFORMATION BAY OI |  |  | SYSTEM INFORMATION BAY OI |  |  | SYSTEM INFORMATION BAY OI |  |  | SYSTEM INFORMATION BAY OI |  |  | SYSTEM INFORMATION BAY OI
| 8 ¦ AgencyStatus |  |  | 8 ¦ AgencyStatus |  |  | 8 ¦ AgencyStatus |  |  | 8 ¦ AgencyStatus |  |  | 8 ¦ AgencyStatus |  |  | 8 ¦ AgencyStatus
| ETAT DE L'AGENCE |  |  | AGENCY STATUS |  |  | ESTADO AGENCY |  |  | ESTADO DA AGENCY IEC |  |  | СТАТУС ДРАЙВЕРА |  |  | AGENCY STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Etat de l'agence |  |  | Agency status |  |  | Estado Agency |  |  | Estado Agency |  |  | Статус драйвера |  |  | Agency status
| 8 ¦ AutomaticArchiving |  |  | 8 ¦ AutomaticArchiving |  |  | 8 ¦ AutomaticArchiving |  |  | 8 ¦ AutomaticArchiving |  |  | 8 ¦ AutomaticArchiving |  |  | 8 ¦ AutomaticArchiving
| ETAT DE L'ARCHIVAGE AUTOMATIQUE |  |  | AUTOMATIC ARCHIVING STATUS |  |  | ESTADO ARCHIVO AUTOMATICO |  |  | ESTADO DO ARQUIVO AUTOMATICO |  |  | СТАТУС АВТОМАТИЧЕСКОЙ АРХИВАЦИИ |  |  | AUTOMATIC ARCHIVING STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Archivage Auto |  |  | Auto archiving |  |  | Archivo Auto |  |  | Arquivo Auto |  |  | Авто архивация |  |  | Auto archiving
| 8 ¦ CentralArchiving |  |  | 8 ¦ CentralArchiving |  |  | 8 ¦ CentralArchiving |  |  | 8 ¦ CentralArchiving |  |  | 8 ¦ CentralArchiving |  |  | 8 ¦ CentralArchiving
| ETAT DE LA BD HISTORIAN |  |  | HISTORIAN DATABASE STATUS |  |  | ESTADO BASE DE DATOS HISTORIAN |  |  | ESTADO BASE DE DADOS HISTORIAN |  |  | Статус БД Историк |  |  | HISTORIAN DATABASE STATUS
| Archive Centrale |  |  | Central archive |  |  | Archivo Central |  |  | Archivo Central |  |  | Центр. архив |  |  | Central archive
| 8 ¦ CommDevice |  |  | 8 ¦ CommDevice |  |  | 8 ¦ CommDevice |  |  | 8 ¦ CommDevice |  |  | 8 ¦ CommDevice |  |  | 8 ¦ CommDevice
| ETAT DU LIEN SBUS |  |  | OI SBUS LINK |  |  | ENLACE OI SBUS |  |  | ESTADO DA CONEXAO SBUS |  |  | СОЕДИНЕНИЕ OI и SBUS |  |  | OI SBUS LINK
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Lien SBUS |  |  | Device link |  |  | Enlace SBUS |  |  | Conexao SBUS |  |  | Связь устройств. |  |  | Device link
| 8 ¦ LogQueue |  |  | 8 ¦ LogQueue |  |  | 8 ¦ LogQueue |  |  | 8 ¦ LogQueue |  |  | 8 ¦ LogQueue |  |  | 8 ¦ LogQueue
| ETAT DE LA FILE D'IMPRESSION |  |  | LOGGING QUEUE STATUS |  |  | ESTADO COLA DE EVENTOS |  |  | ESTADO DA FILA DE EVENTOS |  |  | СНЯТИЕ ПОКАЗАНИЯ СТАТУСА ОЧЕРЕДИ |  |  | LOGGING QUEUE STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| File impression |  |  | Log Queue |  |  | Cola de Eventos |  |  | Fila de Eventos |  |  | Лог очереди |  |  | Log Queue
| 8 ¦ OperatingMode |  |  | 8 ¦ OperatingMode |  |  | 8 ¦ OperatingMode |  |  | 8 ¦ OperatingMode |  |  | 8 ¦ OperatingMode |  |  | 8 ¦ OperatingMode
| MODE OPERATIONNEL |  |  | OPERATING MODE |  |  | MODO OPERACIONAL |  |  | MODO DE OPERACAO |  |  | РЕЖИМ РАБОТЫ |  |  | OPERATING MODE
| Mode d'Operation |  |  | Operating mode |  |  | Modo Operacional |  |  | Modo do operacao |  |  | Режим работы |  |  | Operating mode
| 8 ¦ RedDevice |  |  | 8 ¦ RedDevice |  |  | 8 ¦ RedDevice |  |  | 8 ¦ RedDevice |  |  | 8 ¦ RedDevice |  |  | 8 ¦ RedDevice
| MODE DE REDONDANCE |  |  | REDUNDANCY MODE |  |  | MODO REDUNDANCIA |  |  | MODO REDUNDANCIA |  |  | РЕЖИМ РЕЗЕРВА |  |  | REDUNDANCY MODE
| ACTIF |  |  | ACTIVE |  |  | ACTIVO |  |  | ATIVO |  |  | ОСНОВНОЙ |  |  | AKTIV
| RESERVE |  |  | STANDBY |  |  | EN ESPERA |  |  | RESERVA |  |  | РЕЗЕРВНЫЙ |  |  | RESERVE
| Mode Redondance |  |  | Redundancy mode |  |  | Modo Redundancia |  |  | Modo Redundancia |  |  | Режим резерва |  |  | Redundanzmodus
| 8 ¦ SyncDevice |  |  | 8 ¦ SyncDevice |  |  | 8 ¦ SyncDevice |  |  | 8 ¦ SyncDevice |  |  | 8 ¦ SyncDevice |  |  | 8 ¦ SyncDevice
| ETAT DE SYNCHRONISATION |  |  | SYNCHRONIZATION STATUS |  |  | ESTADO SINCRONIZACION |  |  | ESTADO DA SINCRONIZACAO |  |  | СТАТУС СИНХРОНИЗАЦИИ |  |  | SYNCHRONISIERUNG STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Synchronisation |  |  | Synchronisation |  |  | Sincronización |  |  | Sincronizacao |  |  | Синхронизация |  |  | Synchronisation
| 8 ¦ CouplingStatus |  |  | 8 ¦ CouplingStatus |  |  | 8 ¦ CouplingStatus |  |  | 8 ¦ CouplingStatus |  |  | 8 ¦ CouplingStatus |  |  | 8 ¦ CouplingStatus
| ETAT DU COUPLAGE AGENCE |  |  | SBUS ACQUISITION STATUS |  |  | ESTADO ADQUISICION SBUS |  |  | ESTADO AQUISICAO SBUS |  |  | SBUS СТАТУС СБОРА ДАННЫХ |  |  | SBUS ACQUISITION STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Couplage IEC |  |  | IEC Coupling |  |  | Acople IEC |  |  | Aquisicao IEC |  |  | Связь с IEC |  |  | IEC Coupling
| 8 ¦ CommS2K_C |  |  | 8 ¦ CommS2K_C |  |  | 8 ¦ CommS2K_C |  |  | 8 ¦ CommS2K_C |  |  | 8 ¦ CommS2K_C |  |  | 8 ¦ CommS2K_C
| ETAT DE LA CONNECTION |  |  | CONNECTION STATUS |  |  | ESTADO CONEXIÓN |  |  | ESTADO DA CONEXAO |  |  | СТАТУС СОЕДИНЕНИЯ |  |  | VERBINDUNG STATUS
| NORMAL |  |  | HEALTHY |  |  | CORRECTO |  |  | NORMAL |  |  | ИСПРАВНЫЙ |  |  | BETRIEB
| DEFAUT |  |  | FAULTY |  |  | EN FALLA |  |  | FALHA |  |  | НЕИСПРАВНЫЙ |  |  | FEHLER
| Lien OI CLIENT |  |  | OI client link |  |  | Enlace CLIENTE |  |  | Conexao CLIENTE |  |  | Связь клиента |  |  | OI client link
Note on B16: Board Use SCE board named like -> "SlotX_Y_Z" Where : X = Slot Number [1, 18] Y = Board type "DIU", "DOU", "AIU" or "TMU" Z = Logical Number Or use board named like -> "X N" Where : X = Board type "DIU20x", "DOU20x", "AIU" or "TMU" Relay IED name from Equipments sheet Printer Printer name from Equipments sheet Scada Scada number
Note on B33: Board Use SCE board named like -> "SlotX_Y_Z" Where : X = Slot Number [1, 18] Y = Board type "DIU", "DOU", "AIU" or "TMU" Z = Logical Number Or use board named like -> "X N" Where : X = Board type "DIU20x", "DOU20x", "AIU" or "TMU" Relay IED name from Equipments sheet Printer Printer name from Equipments sheet Scada Scada number
Note on B39: Board Use SCE board named like -> "SlotX_Y_Z" Where : X = Slot Number [1, 18] Y = Board type "DIU", "DOU", "AIU" or "TMU" Z = Logical Number Or use board named like -> "X N" Where : X = Board type "DIU20x", "DOU20x", "AIU" or "TMU" Relay IED name from Equipments sheet Printer Printer name from Equipments sheet Scada Scada number
Note on B105: Board Use SCE board named like -> "SlotX_Y_Z" Where : X = Slot Number [1, 18] Y = Board type "DIU", "DOU", "AIU" or "TMU" Z = Logical Number Or use board named like -> "X N" Where : X = Board type "DIU20x", "DOU20x", "AIU" or "TMU" Relay IED name from Equipments sheet Printer Printer name from Equipments sheet Scada Scada number
Note on B132: Board Use SCE board named like -> "SlotX_Y_Z" Where : X = Slot Number [1, 18] Y = Board type "DIU", "DOU", "AIU" or "TMU" Z = Logical Number Or use board named like -> "X N" Where : X = Board type "DIU20x", "DOU20x", "AIU" or "TMU" Relay IED name from Equipments sheet Printer Printer name from Equipments sheet Scada Scada number
Note on B138: Board Use SCE board named like -> "SlotX_Y_Z" Where : X = Slot Number [1, 18] Y = Board type "DIU", "DOU", "AIU" or "TMU" Z = Logical Number Or use board named like -> "X N" Where : X = Board type "DIU20x", "DOU20x", "AIU" or "TMU" Relay IED name from Equipments sheet Printer Printer name from Equipments sheet Scada Scada number
Note on B153: Board Use SCE board named like -> "SlotX_Y_Z" Where : X = Slot Number [1, 18] Y = Board type "DIU", "DOU", "AIU" or "TMU" Z = Logical Number Or use board named like -> "X N" Where : X = Board type "DIU20x", "DOU20x", "AIU" or "TMU" Relay IED name from Equipments sheet Printer Printer name from Equipments sheet Scada Scada number
Note on B170: Board Use SCE board named like -> "SlotX_Y_Z" Where : X = Slot Number [1, 18] Y = Board type "DIU", "DOU", "AIU" or "TMU" Z = Logical Number Or use board named like -> "X N" Where : X = Board type "DIU20x", "DOU20x", "AIU" or "TMU" Relay IED name from Equipments sheet Printer Printer name from Equipments sheet Scada Scada number

## RESERVED Profiles (hidden)
SPSPrf ¦ SPSNoAlLogArc | ;
DPSPrf ¦ DPSNoAlLogArc | ;
MPSPrf ¦ MPSNoAlLogArc | ;
SPCPrf ¦ SPCNoAlLogArc | ;
DPCPrf ¦ DPCNoAlLogArc | ;
MVPrf ¦ MVNoAlLogArc | ;
SetPointPrf ¦ SPNoAlLogArc | ;
CounterPrf ¦ CTNoAlLogArc | ;

## Access Level (hidden)
Designation : | #REF! |  |  | Symbol : | #REF!
Issue : | #REF! |  |  | Ref : | #REF!
Date : | #REF! | Substation Automation |  | Data Of : | #REF!
This sheet is used to choose what are the default Menu Options for this Datalist
The goal is to allow only given Menu Options to a customer for example.
| GE Menu: | Menu Option | Display in Datalist Menu
|  | Show Datalist | Yes
|  | Hide Sheets | Yes
|  | Display Sheets | Yes
|  | Check Datalist consistency | Yes
|  | Set Default parameter Values | Yes
|  | Add or Modify a BCU, UCA2 IED or IEC 61850 IED | Yes
|  | Import PES Signal List | Yes
|  | Count SPARE Data | Yes
|  | Translate this Datalist | Yes
|  | About this Datalist | Yes
| CUSTOMER Menu: | Menu Option | Display in Datalist Menu
|  | Show Datalist | Yes
|  | Hide Sheets | No
|  | Display Sheets | No
|  | Check Datalist consistency | No
|  | Set Default parameter Values | No
|  | Add or Modify a BCU, UCA2 IED or IEC 61850 IED | Yes
|  | Import PES Signal List | Yes
|  | Count SPARE Data | Yes
|  | Translate this Datalist | No
|  | About this Datalist | Yes
GE Reserved
END OF DATA

## C264_Template (hidden)
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF!
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
MiCOM C264 DESCRIPTION
Keys :
|  |  | Computer Name | [6 empty] | GE Reserved
|  |  | Redundant Computer | [6 empty] | Auto generated
|  |  | Computer type (C264/C264C) | [6 empty] | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
SCADA 1
SCADA 2
SCADA 3
SCADA 4
DIGITAL INPUT BOARD DIU2xx
Digital Inputs Board Number
Digital Inputs Board Slot
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  | 1 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 2 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 3 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 4 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 5 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 6 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 7 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 8 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 9 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 10 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 11 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 12 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 13 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 14 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 15 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
A |  |  |  | 16 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARD DIU2xx
DIGITAL OUTPUT BOARD DOU20x
Digital Outputs Board Number
Digital Outputs Board Slot
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  | 1 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 2 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 3 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 4 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 5 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 6 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 7 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 8 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 9 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 10 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
HIGH BREAK UNIT BOARD HBU20x
HBU Board Number
HBU Board Slot
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  | 1 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 2 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 3 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 4 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 5 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 6 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 7 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 8 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 9 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
A |  |  |  | 10 | SPARE | SPC | [25 empty] | NO/NC | [5 empty] | 2 | DIGITAL OUTPUT BOARD DOU20x
DIGITAL INPUT/OUTPUT BOARD CCU20x
DI/DO Board Number
DI/DO Board Slot
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  | 1 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARDS CCU20x
A |  |  |  | 2 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARDS CCU20x
A |  |  |  | 3 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARDS CCU20x
A |  |  |  | 4 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARDS CCU20x
A |  |  |  | 5 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARDS CCU20x
A |  |  |  | 6 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARDS CCU20x
A |  |  |  | 7 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARDS CCU20x
A |  |  |  | 8 | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INPUT BOARDS CCU20x
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  | 1 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARDS CCU20x
A |  |  |  | 2 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARDS CCU20x
A |  |  |  | 3 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARDS CCU20x
A |  |  |  | 4 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DIGITAL OUTPUT BOARDS CCU20x
ANALOG INPUT BOARD AIU20x
Analog Input Board Number
Analog Input Board Slot
Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Channel | Transducer Type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU20x
A |  |  | 2 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU20x
A |  |  | 3 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU20x
A |  |  | 4 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU20x
ANALOG INPUT BOARD AIU21x
Analog Input Board Number
Analog Input Board Slot
Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Channel | Transducer Type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 2 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 3 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 4 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 5 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 6 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 7 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
A |  |  | 8 |  | SPARE | [32 empty] | 6 | ANALOG INPUT BOARD AIU21x
CT/VT ANALOG INPUT BOARD TMU2x0
CT/VT Board Number
CT/VT Board Slot
CT/VT Board Model
CT acquisition
VT acquisition
|  |  | Nominal Current |  |  | (1A/5A)
|  |  | Nominal Voltage |  |  | [1V … 500V]
Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Input type (U/I) |  | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | Va |  | Mv0000Voltage | kV | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Vb |  | Mv0000Voltage | kV | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Vc |  | Mv0000Voltage | kV | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Vbusbar |  | Mv0000Voltage | kV | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ia |  | Mv0000Current | A | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ib |  | Mv0000Current | A | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ic |  | Mv0000Current | A | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Uab |  | Mv0000Voltage | kV | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Ubc |  | Mv0000Voltage | kV | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Uca |  | Mv0000Voltage | kV | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Freq (Line) |  | Mv000Freq | Hz | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | DV |  | Mv0000Voltage | kV | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | DF |  | Mv000Freq | Hz | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Dj |  | Mv0000Current | ° | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | P total (MW) |  | Mv0000Power | MW | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Q total (Mvar) |  | Mv0000RePower | Mvar | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
A |  |  | Power Factor |  | Mv000PowerF | - | [31 empty] | 6 | CT/VT ANALOG INPUT BOARD TMU2x0
DSP210 BOARD
DSP210 Board Number
DSP210 Board Slot
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  | 1 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DSP210 BOARD
A |  |  |  | 5 | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | DSP210 BOARD
ANALOG OUTPUT BOARD AOU20x
Analog Output Board Number
Analog Output Board Slot
Iss. | Customer Ref |  | AO Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  | 1 | SPARE | [32 empty] | 13 | ANALOG OUTPUT BOARD AOU20x
A |  |  |  | 2 | SPARE | [32 empty] | 13 | ANALOG OUTPUT BOARD AOU20x
A |  |  |  | 3 | SPARE | [32 empty] | 13 | ANALOG OUTPUT BOARD AOU20x
A |  |  |  | 4 | SPARE | [32 empty] | 13 | ANALOG OUTPUT BOARD AOU20x
IED NAME :
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED IED name
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C264 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C264 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C264 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C264 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C264 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on AC99: HMI Display : Specify if the data appears in HMI.
Note on AD99: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE99: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC110: HMI Display : Specify if the data appears in HMI.
Note on AD110: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE110: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC130: HMI Display : Specify if the data appears in HMI.
Note on AD130: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE130: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D173: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E173: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type if defined Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model Sheet. No data type to be entered for SPS and MPS datapoints (and hence no separator ';').
Note on D193: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E193: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D207: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E207: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AC207: HMI Display : Specify if the data appears in HMI.
Note on AD207: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE207: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D215: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E215: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator: ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU if defined;Data type (separator: ';') OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on D221: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E221: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type Data type for T10X MASTER is the profile number of the datapoint defined in the T10X Master Model sheet.
Note on AB221: LCD Display : Specify if the data appears in computer LCD.
Note on AC221: HMI Display : Specify if the data appears in HMI.
Note on AD221: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE221: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC285: HMI Display : Specify if the data appears in HMI.
Note on AD285: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE285: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB305: LCD Display : Specify if the data appears in computer LCD.
Note on AC305: HMI Display : Specify if the data appears in HMI.
Note on AD305: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE305: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## C364_Template (hidden)
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF!
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
MiCOM C364 DESCRIPTION
Keys :
GE Reserved
|  |  | Computer Name | [6 empty] | Auto generated
|  |  | Redundant Computer | [6 empty] | Read Only
ERROR
|  |  |  | Gateway | Port used (on gateway)
SCADA 1
SCADA 2
SCADA 3
SCADA 4
IED NAME :
|  |  | DIGITAL INFORMATION FROM IED |  |  |  | IED name
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | DIGITAL INFORMATION FROM IED IED name
|  |  | DIGITAL INFORMATION TO IED |  |  |  | IED name
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
A |  |  |  |  | SPARE | SPC | [31 empty] | 2 | DIGITAL INFORMATION TO IED IED name
|  |  | ANALOG INFORMATION FROM IED |  |  |  | IED name
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | ANALOG INFORMATION FROM IED IED name
|  |  | ANALOG INFORMATION TO IED |  |  |  | IED name
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name
A |  |  |  |  | SPARE | [32 empty] | 13 | ANALOG INFORMATION TO IED IED name
|  |  | COUNTER INFORMATION FROM IED |  |  |  | IED name
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED name
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED name
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED name
A |  |  |  |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | COUNTER INFORMATION FROM IED name
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 DI GROUPS
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 DI GROUPS
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 DI GROUPS
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 DI GROUPS
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 DI GROUPS
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 DI GROUPS
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 DI GROUPS
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 DI GROUPS
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 DI GROUPS
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 DI GROUPS
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 DI GROUPS
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 DI GROUPS
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 DI GROUPS
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 DI GROUPS
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 DI GROUPS
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 DI GROUPS
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 SELF GENERATED DIGITAL INFORMATION
A |  |  | 2 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 SELF GENERATED DIGITAL INFORMATION
A |  |  | 3 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 SELF GENERATED DIGITAL INFORMATION
A |  |  | 4 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 SELF GENERATED DIGITAL INFORMATION
A |  |  | 5 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 SELF GENERATED DIGITAL INFORMATION
A |  |  | 6 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 SELF GENERATED DIGITAL INFORMATION
A |  |  | 7 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 SELF GENERATED DIGITAL INFORMATION
A |  |  | 8 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 SELF GENERATED DIGITAL INFORMATION
A |  |  | 9 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 SELF GENERATED DIGITAL INFORMATION
A |  |  | 10 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 SELF GENERATED DIGITAL INFORMATION
A |  |  | 11 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 SELF GENERATED DIGITAL INFORMATION
A |  |  | 12 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 SELF GENERATED DIGITAL INFORMATION
A |  |  | 13 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 SELF GENERATED DIGITAL INFORMATION
A |  |  | 14 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 SELF GENERATED DIGITAL INFORMATION
A |  |  | 15 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 SELF GENERATED DIGITAL INFORMATION
A |  |  | 16 |  | SPARE | SPS | [19 empty] | None |  | No | [9 empty] | 1 | C364 SELF GENERATED DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  | Local Control |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C364 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 2 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C364 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 3 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C364 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 4 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C364 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 5 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C364 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 6 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C364 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 7 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C364 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 8 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C364 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 9 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C364 SELF GENERATED DIGITAL OUTPUT INFORMATION
A |  |  | 10 |  | SPARE | SPC | [25 empty] | NO | [5 empty] | 2 | C364 SELF GENERATED DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C364 SELF GENERATED ANALOG INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C364 SELF GENERATED ANALOG INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C364 SELF GENERATED ANALOG INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C364 SELF GENERATED ANALOG INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C364 SELF GENERATED ANALOG INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C364 SELF GENERATED ANALOG INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C364 SELF GENERATED ANALOG INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C364 SELF GENERATED ANALOG INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C364 SELF GENERATED ANALOG INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C364 SELF GENERATED ANALOG INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C364 SELF GENERATED ANALOG INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C364 SELF GENERATED ANALOG INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C364 SELF GENERATED ANALOG INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C364 SELF GENERATED ANALOG INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C364 SELF GENERATED ANALOG INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 6 | C364 SELF GENERATED ANALOG INFORMATION
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C364 SELF GENERATED COUNTER INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C364 SELF GENERATED COUNTER INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C364 SELF GENERATED COUNTER INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C364 SELF GENERATED COUNTER INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C364 SELF GENERATED COUNTER INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C364 SELF GENERATED COUNTER INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C364 SELF GENERATED COUNTER INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C364 SELF GENERATED COUNTER INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C364 SELF GENERATED COUNTER INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C364 SELF GENERATED COUNTER INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C364 SELF GENERATED COUNTER INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C364 SELF GENERATED COUNTER INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C364 SELF GENERATED COUNTER INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C364 SELF GENERATED COUNTER INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C364 SELF GENERATED COUNTER INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 39 | C364 SELF GENERATED COUNTER INFORMATION
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
A |  |  | 1 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C364 SELF GENERATED SETPOINT INFORMATION
A |  |  | 2 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C364 SELF GENERATED SETPOINT INFORMATION
A |  |  | 3 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C364 SELF GENERATED SETPOINT INFORMATION
A |  |  | 4 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C364 SELF GENERATED SETPOINT INFORMATION
A |  |  | 5 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C364 SELF GENERATED SETPOINT INFORMATION
A |  |  | 6 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C364 SELF GENERATED SETPOINT INFORMATION
A |  |  | 7 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C364 SELF GENERATED SETPOINT INFORMATION
A |  |  | 8 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C364 SELF GENERATED SETPOINT INFORMATION
A |  |  | 9 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C364 SELF GENERATED SETPOINT INFORMATION
A |  |  | 10 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C364 SELF GENERATED SETPOINT INFORMATION
A |  |  | 11 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C364 SELF GENERATED SETPOINT INFORMATION
A |  |  | 12 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C364 SELF GENERATED SETPOINT INFORMATION
A |  |  | 13 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C364 SELF GENERATED SETPOINT INFORMATION
A |  |  | 14 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C364 SELF GENERATED SETPOINT INFORMATION
A |  |  | 15 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C364 SELF GENERATED SETPOINT INFORMATION
A |  |  | 16 |  | SPARE | [22 empty] | Yes | [9 empty] | 13 | C364 SELF GENERATED SETPOINT INFORMATION
END OF DATA
Note on D19: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address
Note on E19: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset
Note on D39: T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address
Note on E39: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType
Note on D53: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E53: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used
Note on AC53: HMI Display : Specify if the data appears in HMI.
Note on AD53: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE53: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D61: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E61: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator : ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute
Note on D67: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address
Note on E67: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used
Note on AB67: LCD Display : Specify if the data appears in computer LCD.
Note on AC67: HMI Display : Specify if the data appears in HMI.
Note on AD67: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE67: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC131: HMI Display : Specify if the data appears in HMI.
Note on AD131: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE131: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB151: LCD Display : Specify if the data appears in computer LCD.
Note on AC151: HMI Display : Specify if the data appears in HMI.
Note on AD151: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE151: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## Column Presence Checking (hidden)
Designation : |  |  | Project Name | [30 empty] | Symbol : |  | SAM-DTL-DS Agile-4.3.0.0
Issue : |  |  | A | [30 empty] | Ref : |  | PROJECTNAME-Xnn-DTL
Date : |  |  | 0 | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | Site Name
Keys :
|  | This sheet is to be used to indicate the cells/columns that are : | [13 empty] | GE Reserved
|  |  |  | - P : present in all corresponding sheets but the contents shall not be used by automatic tools | [11 empty] | Auto generated
|  |  |  | - U : present in all corresponding sheets and shall be used by automatic tools | [11 empty] | Read Only
- A : not present in corresponding sheets
- PH : hide in all corresponding sheets but the contents shall not be used by automatic tools
- UH : hide in all corresponding sheets and shall be used by automatic tools
GE Reserved
MiCOM CXXX DESCRIPTION
DIGITAL INPUT BOARD DIU2xx
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U
DIGITAL OUTPUT BOARD DOU20x
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | A | U | U | U | U | U | A | U | U | U | U | U
HIGH BREAK UNIT BOARD HBU20x
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | A | U | U | U | U | U | A | U | U | U | U | U
DIGITAL INPUT/OUTPUT BOARD CCU20x
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U |  | U | U | U
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | A | U | U | U | U | U | A | U | U | U | U | U
ANALOG INPUT BOARD AIU20x
Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Channel | Transducer Type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | A | U | U | U | U | U | U | U | U | U | U | U
ANALOG INPUT BOARD AIU21x
Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Channel | Transducer Type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | A | U | U | U | U | U | U | U | U | U | U | U
CT/VT ANALOG INPUT BOARD TMU2x0
Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Input type (U/I) |  | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | A | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | A | U | U | U | U | U | U | U | U | U | U | U
DSP210 BOARD
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | A | U | U | U | U | U | A | U | U | U | U | U
ANALOG OUTPUT BOARD AOU20x
Iss. | Customer Ref |  | AO Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | A | A | U | U | A | U | U | A | U | U | U | U | U
DIGITAL INFORMATION FROM IED
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U
DIGITAL INFORMATION TO IED
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | A | U | U | U | U | U | A | U | U | U | U | U
ANALOG INFORMATION FROM IED
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | A | U | U | U | U | U | U | U | U | U | U | U
ANALOG INFORMATION TO IED
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | A | A | U | U | A | U | U | A | U | U | U | U | U
COUNTER INFORMATION FROM IED
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | A | A | U | U | U | U | U | A | U | U | U | U | U
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | A | U | U | U | U | U | A | U | U | U | U | U
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | A | U | U | U | U | U | U | U | U | U | U | U
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Type |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | A | A | U | U | U | U | U | A | U | U | U | U | U
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | A | A | U | U | A | U | U | A | U | U | U | U | U
SUBSTATION DATA DESCRIPTION
SUBSTATION DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Managed by Computer | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U
SYSTEM INFORMATION DATA DESCRIPTION
SYSTEM INFORMATION SERVER OI
Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
U | A | A | U | A | U | U | A | A | A | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | U | U | U | A | U | U | U | A | A | U | U | U
SYSTEM INFORMATION CLIENT OI
Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
U | A | A | U | A | U | U | A | A | A | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | U | U | U | A | U | U | U | A | A | U | U | U
SYSTEM INFORMATION MiCOM C264
Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
U | A | A | U | A | U | U | A | A | A | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | U | U | A | A | U | U | U
SYSTEM INFORMATION MiCOM C364
Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
U | A | A | U | A | U | U | A | A | A | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | U | U | A | A | U | U | U
SYSTEM INFORMATION UCA2 IED
Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
U | A | A | U | A | U | U | A | A | A | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | U | U | A | A | U | U | U
SYSTEM INFORMATION GATEWAY
Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
U | A | A | U | A | U | U | A | A | A | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | U | U | U | A | U | U | U | A | A | U | U | U
SYSTEM INFORMATION IEC 61850
Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
U | A | A | U | A | U | U | A | A | A | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | U | U | A | A | U | U | U
SYSTEM INFORMATION BAY OI
Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
U | A | A | U | A | U | U | A | A | A | U | U | U | U | U | U | U | U | U | U | U | U | U | U | A | U | U | U | U | A | U | U | U | A | A | U | U | U
END OF DATA
Note on AC51: HMI Display : Specify if the data appears in HMI.
Note on AD51: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE51: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC57: HMI Display : Specify if the data appears in HMI.
Note on AD57: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE57: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC63: HMI Display : Specify if the data appears in HMI.
Note on AD63: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE63: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D81: T101: Information Address T103: ASDU numberb;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E81: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset
Note on D86: T101: Information Address T103: ASDU numberb;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E86: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type
Note on D91: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E91: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used
Note on AC91: HMI Display : Specify if the data appears in HMI.
Note on AD91: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE91: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D96: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E96: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator : ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU;Data type OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute
Note on D101: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on E101: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type
Note on AB101: LCD Display : Specify if the data appears in computer LCD.
Note on AC101: HMI Display : Specify if the data appears in HMI.
Note on AD101: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE101: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC123: HMI Display : Specify if the data appears in HMI.
Note on AD123: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE123: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB128: LCD Display : Specify if the data appears in computer LCD.
Note on AC128: HMI Display : Specify if the data appears in HMI.
Note on AD128: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE128: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## Column Default Value (hidden)
Designation : |  |  | #REF! | [31 empty] | Symbol : |  | #REF! |  | BABA
Issue : |  |  | #REF! | [31 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [12 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
Keys :
|  |  | This sheet is used to set default parameter value for each data. | [13 empty] | GE Reserved
|  |  |  | - set the Old parameter value to change in the "Old Value" line | [12 empty] | Auto generated
|  |  |  | - set the New parameter value used to overwrite Old one in the "New Value" line | [12 empty] | Read Only
- It is possible to use regular expressions as 'Old value' to locate data by using:
? Any single character.
* Zero or more characters.
# Any single digit (0-9).
[charlist] Any single character in charlist.
[!charlist] Any single character not in charlist.
- A group of one or more characters (charlist) enclosed in brackets ([ ]) can be used to
match any single character in string and can include almost any character code,
including digits.
- Note: To match the special characters left bracket ([), question mark (?), number sign (#),
and asterisk (*), enclose them in brackets. The right bracket (]) can't be used within a group
to match itself, but it can be used outside a group as an individual character.
- By using a hyphen (-) to separate the upper and lower bounds of the range, charlist can
specify a range of characters. For example, [A-Z] results in a match if the corresponding
character position in string contains any uppercase letters in the range A-Z. Multiple ranges
Example:
'aBBBa' is like 'a*a'
'F' is like '[A-Z]'
'F' is NOT like '[!A-Z]'
'a2a' is like 'a#a'
'aM5b' is like 'a[L-P]#[!c-e]'
'BAT123khg' is like 'B?T*'
'CAT123khg' is NOT like 'B?T*'
GE Reserved
MiCOM CXXX DESCRIPTION
DIGITAL INPUT BOARD DIU2xx
| Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
DIGITAL OUTPUT BOARD DOU20x
| Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
HIGH BREAK UNIT BOARD HBU20x
| Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
DIGITAL INPUT/OUTPUT BOARD CCU20x
| Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
| Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
ANALOG INPUT BOARD AIU20x
| Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Channel | Transducer Type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
ANALOG INPUT BOARD AIU21x
| Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Channel | Transducer Type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
CT/VT ANALOG INPUT BOARD TMU2x0
| Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Input type (U/I) |  | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
DSP210 BOARD
| Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
ANALOG OUTPUT BOARD AOU20x
| Iss. | Customer Ref |  | AO Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Slot | Channel | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
DIGITAL INFORMATION FROM IED
| Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
DIGITAL INFORMATION TO IED
| Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
ANALOG INFORMATION FROM IED
| Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
ANALOG INFORMATION TO IED
| Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
COUNTER INFORMATION FROM IED
| Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
END OF IED DATA
DI GROUPS
| Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
SELF GENERATED DIGITAL INFORMATION
| Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
SELF GENERATED DIGITAL OUTPUT INFORMATION
| Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
SELF GENERATED ANALOG INFORMATION
| Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
SELF GENERATED COUNTER INFORMATION
| Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
SELF GENERATED SETPOINT INFORMATION
| Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
SUBSTATION DATA DESCRIPTION
SUBSTATION DI GROUPS
| Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
| Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Managed by Computer | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
Old Value
New Value
SYSTEM INFORMATION DATA DESCRIPTION
SYSTEM INFORMATION SERVER OI
| Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
| Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
Old Value
New Value
SYSTEM INFORMATION CLIENT OI
| Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
| Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
Old Value
New Value
SYSTEM INFORMATION MiCOM C264
| Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
| Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
Old Value
New Value
SYSTEM INFORMATION MiCOM C364
| Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
| Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
Old Value
New Value
SYSTEM INFORMATION UCA2 IED
| Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
| Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
Old Value
New Value
SYSTEM INFORMATION GATEWAY
| Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
| Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
Old Value
New Value
SYSTEM INFORMATION IEC 61850
| Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
| Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
Old Value
New Value
SYSTEM INFORMATION BAY OI
| Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
| Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
Old Value
New Value
END OF DATA
Note on AD82: HMI Display : Specify if the data appears in HMI.
Note on AE82: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AF82: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AD89: HMI Display : Specify if the data appears in HMI.
Note on AE89: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AF89: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AD96: HMI Display : Specify if the data appears in HMI.
Note on AE96: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AF96: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on E117: T101: Information Address T103: ASDU numberb;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address
Note on F117: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset
Note on E123: T101: Information Address T103: ASDU numberb;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address
Note on F123: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType
Note on E129: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on F129: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used
Note on AD129: HMI Display : Specify if the data appears in HMI.
Note on AE129: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AF129: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on E135: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on F135: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator : ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute
Note on E141: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address
Note on F141: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used
Note on AC141: LCD Display : Specify if the data appears in computer LCD.
Note on AD141: HMI Display : Specify if the data appears in HMI.
Note on AE141: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AF141: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AD167: HMI Display : Specify if the data appears in HMI.
Note on AE167: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AF167: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC173: LCD Display : Specify if the data appears in computer LCD.
Note on AD173: HMI Display : Specify if the data appears in HMI.
Note on AE173: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AF173: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## Column Selection For Data Copy (hidden)
Designation : |  |  | #REF! | [30 empty] | Symbol : |  | #REF!
Issue : |  |  | #REF! | [30 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [11 empty] | Substation Automation | [18 empty] | Data Of : |  | #REF!
Keys :
|  | This sheet is to be used to indicate the cells/columns for which the contents shall be copied to a new DataList release. | [13 empty] | GE Reserved
|  | The possible values are : | [13 empty] | Auto generated
|  |  |  | - N : do not copy in any case | [11 empty] | Read Only
- C : copy in any case (when the line is significant)
- E : copy only if the cell within new release is empty
GE Reserved
MiCOM CXXX DESCRIPTION
DIGITAL INPUT BOARD DIU2xx
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E
DIGITAL OUTPUT BOARD DOU20x
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | N | E | E | E | E | E | N | E | E | E | E | E
HIGH BREAK UNIT BOARD HBU20x
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | N | E | E | E | E | E | N | E | E | E | E | E
DIGITAL INPUT/OUTPUT BOARD CCU20x
Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | N | E | E | E | E | E | N | E | E | E | E | E
ANALOG INPUT BOARD AIU20x
Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Channel | Transducer Type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | N | E | E | E | E | E | E | E | E | E | E | E
ANALOG INPUT BOARD AIU21x
Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Channel | Transducer Type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | N | E | E | E | E | E | E | E | E | E | E | E
CT/VT ANALOG INPUT BOARD TMU2x0
Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Input type (U/I) |  | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | N | E | E | E | E | E | E | E | E | E | E | E
DSP210 BOARD
Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | N | E | E | E | E | E | N | E | E | E | E | E
ANALOG OUTPUT BOARD AOU20x
Iss. | Customer Ref |  | AO Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Slot | Channel | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | N | N | E | E | N | E | E | N | E | E | E | E | E
DIGITAL INFORMATION FROM IED
Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E
DIGITAL INFORMATION TO IED
Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | N | E | E | E | E | E | N | E | E | E | E | E
ANALOG INFORMATION FROM IED
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | N | E | E | E | E | E | E | E | E | E | E | E
ANALOG INFORMATION TO IED
Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | N | N | E | E | N | E | E | N | E | E | E | E | E
COUNTER INFORMATION FROM IED
Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | N | N | E | E | E | E | E | N | E | E | E | E | E
END OF IED DATA
DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E
SELF GENERATED DIGITAL INFORMATION
Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E
SELF GENERATED DIGITAL OUTPUT INFORMATION
Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | N | E | E | E | E | E | N | E | E | E | E | E
SELF GENERATED ANALOG INFORMATION
Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | N | E | E | E | E | E | E | E | E | E | E | E
SELF GENERATED COUNTER INFORMATION
Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | N | N | E | E | E | E | E | N | E | E | E | E | E
SELF GENERATED SETPOINT INFORMATION
Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | N | N | E | E | N | E | E | N | E | E | E | E | E
SUBSTATION DATA DESCRIPTION
SUBSTATION DI GROUPS
Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Managed by Computer | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
E | E | E | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E
SYSTEM INFORMATION DATA DESCRIPTION
SYSTEM INFORMATION SERVER OI
Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
E | N | N | E | N | E | E | N | N | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | E | E | E | N | E | E | E | N | N | E | E | E
SYSTEM INFORMATION CLIENT OI
Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
E | N | N | E | N | E | E | N | N | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | E | E | E | N | E | E | E | N | N | E | E | E
SYSTEM INFORMATION MiCOM C264
Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
E | N | N | E | N | E | E | N | N | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | E | E | N | N | E | E | E
SYSTEM INFORMATION MiCOM C364
Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
E | N | N | E | N | E | E | N | N | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | E | E | N | N | E | E | E
SYSTEM INFORMATION UCA2 IED
Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
E | N | N | E | N | E | E | N | N | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | E | E | N | N | E | E | E
SYSTEM INFORMATION GATEWAY
Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
E | N | N | E | N | E | E | N | N | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | E | E | E | N | E | E | E | N | N | E | E | E
SYSTEM INFORMATION IEC 61850
Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
E | N | N | E | N | E | E | N | N | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | E | E | N | N | E | E | E
SYSTEM INFORMATION BAY OI
Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
E | N | N | E | N | E | E | N | N | N | E | E | E | E | E | E | E | E | E | E | E | E | E | E | N | E | E | E | E | N | E | E | E | N | N | E | E | E
END OF DATA
Note on AC50: HMI Display : Specify if the data appears in HMI.
Note on AD50: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE50: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC56: HMI Display : Specify if the data appears in HMI.
Note on AD56: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE56: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC62: HMI Display : Specify if the data appears in HMI.
Note on AD62: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE62: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D81: T101: Information Address T103: ASDU numberb;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address
Note on E81: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset
Note on D86: T101: Information Address T103: ASDU numberb;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address
Note on E86: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType
Note on D91: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E91: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used
Note on AC91: HMI Display : Specify if the data appears in HMI.
Note on AD91: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE91: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on D96: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E96: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator : ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute
Note on D101: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address
Note on E101: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used
Note on AB101: LCD Display : Specify if the data appears in computer LCD.
Note on AC101: HMI Display : Specify if the data appears in HMI.
Note on AD101: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE101: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AC123: HMI Display : Specify if the data appears in HMI.
Note on AD123: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE123: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AB128: LCD Display : Specify if the data appears in computer LCD.
Note on AC128: HMI Display : Specify if the data appears in HMI.
Note on AD128: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AE128: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## Matrix (hidden)
Designation : |  |  | #REF! | [32 empty] | Symbol : |  | #REF!
Issue : |  |  | #REF! | [32 empty] | Ref : |  | #REF!
Date : |  |  | #REF! | [12 empty] | Substation Automation | [19 empty] | Data Of : |  | #REF!
Keys :
|  |  | This sheet indicates the cells/columns used for building comparison criteria. | [13 empty] | GE Reserved
|  |  | The possible values are : | [13 empty] | Auto generated
[5 empty] | - P : present in all corresponding sheets but the contents shall not be used to build comparison criteria | [11 empty] | Read Only
- U : present in all corresponding sheets and shall be used to build comparison criteria
- A : not present in corresponding sheets
GE Reserved
MiCOM CXXX DESCRIPTION
DIGITAL INPUT BOARD DIU2xx
| Description | Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | Digital Inputs Board Number | Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
P | U | P | P | P | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
DIGITAL OUTPUT BOARD DOU20x
| Description | Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | Digital Outputs Board Number | Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
P | U | P | P | P | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
HIGH BREAK UNIT BOARD HBU20x
| Description | Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | Digital Outputs Board Number | Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
P | U | P | P | P | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
DIGITAL INPUT/OUTPUT BOARD CCU20x
| Description | Iss. | Customer Ref |  | DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | DI/DO Board Number | Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
P | U | P | P | P | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
| Description | Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | DI/DO Board Number | Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
P | U | P | P | P | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
ANALOG INPUT BOARD AIU20x
| Description | Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | Analog Input Board Number | Issue | Panel Number | Tag Number | Channel | Transducer Type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
P | U | P | P | P | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
ANALOG INPUT BOARD AIU21x
| Description | Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | Analog Input Board Number | Issue | Panel Number | Tag Number | Channel | Transducer Type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
P | U | P | P | P | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
CT/VT ANALOG INPUT BOARD TMU2x0
| Description | Iss. | Customer Ref |  | AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | CT/VT Board Number | Issue | Panel Number | Tag Number | Input type (U/I) |  | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | P | P | P | P | A | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | A | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | A | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | A | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | A | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | A | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | A | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | A | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | A | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | A | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | A | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | A | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | A | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | A | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | A | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | A | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | A | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | A | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
P | U | P | P | P | P | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
P | P | P | P | P | P | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
DSP210 BOARD
| Description | Iss. | Customer Ref |  | DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | DSP210 Board Number | Issue | Panel Number | Tag Number | Slot | Channel | Function | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
P | U | P | P | P | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
ANALOG OUTPUT BOARD AOU20x
| Description | Iss. | Customer Ref |  | AO Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | Analog Output Board Number | Issue | Panel Number | Tag Number | Slot | Channel | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
P | U | P | P | P | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
DIGITAL INFORMATION FROM IED
| Description | Iss. | Customer Ref |  | IED DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | IED name | Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
DIGITAL INFORMATION TO IED
| Description | Iss. | Customer Ref |  | IED DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | IED name | Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
ANALOG INFORMATION FROM IED
| Description | Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | IED name | Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | U | P | P | P | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
ANALOG INFORMATION TO IED
| Description | Iss. | Customer Ref |  | IED AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | IED name | Issue | Panel Number | Tag Number | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at minimum | Corresponding AI Value at Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | P | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
COUNTER INFORMATION FROM IED
| Description | Iss. | Customer Ref |  | IED Counter Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | IED name | Issue | Panel Number | Tag Number | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | U | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | U | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | P | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | U | P | P | P | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
END OF IED DATA
DI GROUPS
|  | Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case |  | Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | A | P | P | P | P | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | U | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | U | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | U | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | U | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | U | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | U | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | U | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | U | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
P | A | P | P | P | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
P | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
SELF GENERATED DIGITAL INFORMATION
|  | Iss. | Customer Ref |  | Self DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case |  | Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | A | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
P | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
P | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
SELF GENERATED DIGITAL OUTPUT INFORMATION
|  | Iss. | Customer Ref |  | Self DO Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Control | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case |  | Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Type (SPC=Single/DPC=Dual) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Control | HMI Control | Has a xPS Feedback | Is activated by xPS | Used by ISaGRAF | Relay | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | A | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
P | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
P | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | A | P | P | P | P | P
SELF GENERATED ANALOG INFORMATION
|  | Iss. | Customer Ref |  | Self AI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case |  | Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding AI Value at Transducer minimum | Corresponding AI Value at Transducer Maximum | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  | Automations links (separator ";") (add "<" if output) |  | LCD Display | HMI Display | Integrated by COUNTER | Trend Viewer | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | A | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
P | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
P | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | A | P | P | P | P | P | P | P | P | P | P | P
SELF GENERATED COUNTER INFORMATION
|  | Iss. | Customer Ref |  | Self Counter Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case |  | Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Counter Type | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display | Integrate MV | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | A | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
P | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
P | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | P | P | P | A | P | P | P | P | P
SELF GENERATED SETPOINT INFORMATION
|  | Iss. | Customer Ref |  | SetPoint Reference |  | Electrical Data |  |  |  |  | Description | Labels |  | Description | Scada Interface | [7 empty] | IEC Interface |  |  |  |  | Local Display | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case |  | Issue | Panel Number | Tag Number | Number | Automation Origin (if any) | Function | Unit | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Corresponding Minimal Value | Corresponding Maximal Value | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) |  |  |  | LCD Display | HMI Display |  | Trend Viewer | Used by ISaGRAF |  | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | A | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
U | A | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
P | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
P | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | A | A | P | P | A | P | P | A | P | P | P | P | P
SUBSTATION DATA DESCRIPTION
SUBSTATION DI GROUPS
|  | Iss. | Customer Ref |  | Group DI Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | DI/DO Link |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case |  | Issue | Panel Number | Tag Number | Number | Group Operator | Function | Type (S=Single) | Voltage Level Short Name (16 char) | Bay Short Name (16 char) | Module Short Name (16 char) | Long name (35 char) | Single : Text at electrical state = 1 (16 char) | Single : Text at electrical state = 0 (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Managed by Computer | Automations links (separator ";") (add "<" if output) | LED | LCD Display | HMI Display | Is a xPC Feedback | Acts on xPC | Used by ISaGRAF | Is used by distributed Automation (GOOSE) | Bay Name (in SCE Template) or Bay Type | Module Name (in SCE Template) or Module Type | Datapoint Name (in SCE Template) or Datapoint Type | Process | Comments
U | A | P | P | P | P | U | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | U | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | U | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | U | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | U | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | U | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | U | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | U | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | U | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | U | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | U | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
U | A | P | P | P | P | P | U | U | P | P | P | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
P | A | P | P | P | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
P | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P
SYSTEM INFORMATION DATA DESCRIPTION
SYSTEM INFORMATION SERVER OI
| Description | Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | SERVER OI Name : | Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
U | U | P | A | A | U | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | U | U | A | A | A | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
P | U | P | A | A | U | A | P | P | A | A | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
P | P | P | A | A | P | A | P | P | A | A | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
SYSTEM INFORMATION CLIENT OI
| Description | Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | CLIENT OI Name : | Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
U | U | P | A | A | U | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | U | U | A | A | A | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
P | U | P | A | A | U | A | P | P | A | A | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
P | P | P | A | A | P | A | P | P | A | A | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
SYSTEM INFORMATION MiCOM C264
| Description | Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | MiCOM C264 Name : | Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
U | U | P | A | A | U | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | U | U | A | A | A | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
P | U | P | A | A | U | A | P | P | A | A | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
P | P | P | A | A | P | A | P | P | A | A | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
SYSTEM INFORMATION MiCOM C364
| Description | Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | MiCOM C364 Name : | Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
U | U | P | A | A | U | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | U | U | A | A | A | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
P | U | P | A | A | U | A | P | P | A | A | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
P | P | P | A | A | P | A | P | P | A | A | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
SYSTEM INFORMATION UCA2 IED
| Description | Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | UCA2 IED Name : | Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
U | U | P | A | A | U | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | U | U | A | A | A | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
P | U | P | A | A | U | A | P | P | A | A | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
P | P | P | A | A | P | A | P | P | A | A | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
SYSTEM INFORMATION GATEWAY
| Description | Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | GATEWAY Name : | Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
U | U | P | A | A | U | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | U | U | A | A | A | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
P | U | P | A | A | U | A | P | P | A | A | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
P | P | P | A | A | P | A | P | P | A | A | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
SYSTEM INFORMATION IEC 61850
| Description | Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | IEC 61850 Name : | Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
U | U | P | A | A | U | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | P | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | U | U | A | A | A | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
P | U | P | A | A | U | A | P | P | A | A | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
P | P | P | A | A | P | A | P | P | A | A | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | A | A | P | P | P
SYSTEM INFORMATION BAY OI
| Description | Iss. |  |  | Reference |  | Electrical Data |  |  |  |  | Description | Labels / States |  | Description | Scada Interface | [7 empty] | IEC Interface |  | Groups |  | Local Display |  | HMI | Special |  | Automation |  | Template |  |  | Conf. Mng.
Use this Matrix Case | BAY OI Name : | Issue |  |  | Equipment Link |  | Function | Type |  |  |  | Long name (35 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Short Name (16 char) | SCADA 1 Address | SCADA1 Data type | SCADA 2 Address | SCADA2 Data type | SCADA 3 Address | SCADA3 Data type | SCADA 4 Address | SCADA4 Data type | IEC Address Part 1 (IEC: LD;LN) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Computers Groups (separator ";") | Automations links (separator ";") (add "<" if output) | LED MV : Not used | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : HMI Display xPC : HMI Control MV : HMI Display |  | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | Used by ISaGRAF | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used |  |  | Datapoint Name (in SCE Template) | Process | Comments
U | U | P | A | A | U | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | P | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | U | U | U | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | P | P | A | A | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | P | P | A | A | A | P | P | P | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | U | U | U | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | U | A | U | U | A | A | A | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
U | U | P | A | A | P | A | U | U | A | A | A | U | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
P | U | P | A | A | U | A | P | P | A | A | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
P | P | P | A | A | P | A | P | P | A | A | A | P | P | P | P | P | P | P | P | P | P | P | P | P | P | A | P | P | P | P | A | P | P | P | A | A | P | P | P
END OF DATA
Note on AE144: HMI Display : Specify if the data appears in HMI.
Note on AF144: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AG144: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AE169: HMI Display : Specify if the data appears in HMI.
Note on AF169: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AG169: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AE194: HMI Display : Specify if the data appears in HMI.
Note on AF194: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AG194: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on F270: T101: Information Address T103: ASDU numberb;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on G270: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode T10X MASTER: Common address ASDU;Data type Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset
Note on F296: T101: Information Address T103: ASDU numberb;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on G296: T101: Common address of ASDU;;OrderType T103: Information number;Common address of ASDU;OrderType (separator : ';') MODBUS: Function;;OrderType DNP3: ;;OrderType T10X MASTER: Common address ASDU;Data type
Note on F322: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address T10X MASTER: Information Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on G322: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type
Note on AE322: HMI Display : Specify if the data appears in HMI.
Note on AF322: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AG322: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on F348: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address T10X MASTER: Information Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on G348: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator : ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType T10X MASTER: Common address ASDU;Data type OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute
Note on F374: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type (separator : ';') MODBUS: Mapping address;InputFormat (separator : ';') DNP3: Address T10X MASTER: Information Address
Note on G374: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU (separator : ';') MODBUS : Function DNP3 : Not used T10X MASTER: Common address ASDU;Data type
Note on AD374: LCD Display : Specify if the data appears in computer LCD.
Note on AE374: HMI Display : Specify if the data appears in HMI.
Note on AF374: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AG374: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AE457: HMI Display : Specify if the data appears in HMI.
Note on AF457: Is integrated by COUNTER : Specify if this MV is integrated by a Counter. How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AG457: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI
Note on AD472: LCD Display : Specify if the data appears in computer LCD.
Note on AE472: HMI Display : Specify if the data appears in HMI.
Note on AF472: Integrate an MV : Specify if this Counter integrates a MV How to fill : In this column, put the same index in the MV line and the COUNTER line to link them. The index must be a numeric index [1 … 65535]
Note on AG472: Trend Viewer: Use a Trend Viewer to represent the measure on the HMI

## Translation (hidden)
Mapping Language English | Français | English | Spanish | Português Brasil | Russian | German
SHEET : Customer Front Page | SHEET : Page de Garde Client | SHEET : Customer Front Page | SHEET : Página principal Cliente | SHEET : Página Inicial Cliente | SHEET : Первая Страница Клиента | SHEET : Customer Front Page
SHEET : GE Front Page | SHEET : Page de Garde GE | SHEET : GE Front Page | SHEET : Página principal GE | SHEET : Pagina Inicial GE | SHEET : Первая Страница GE | SHEET : GE Front Page
ISSUE | REVISION | ISSUE | REVISION | REVISÃO | ВЕРСИЯ | VERSION
DESCRIPTION | DESCRIPTION | DESCRIPTION | DESCRIPCION | DESCRIÇÃO | ОПИСАНИЕ | BESCHREIBUNG
DATE | DATE | DATE | FECHA | DATA | ДАТА | DATUM
CUSTOMER | CLIENT | CUSTOMER | CLIENTE | Cliente | ЗАКАЗЧИК | KUNDE
GE | GE | GE | GE | GE | GE | GE
CUSTOMER | CLIENT | CUSTOMER | CLIENTE | Cliente | ЗАКАЗЧИК | KUNDE
CONTRACT No. | CONTRAT N° | CONTRACT No. | NO. de CONTRATO | Num. do CONTRATO | КОНТРАКТ No. | AUFTRAG Nr.
ORDER No. | Commande N° | ORDER No. | No. De ORDEN | Num. Da Ordem | ЗАКАЗ No. | BESTELL Nr.
PROJECT: | PROJET: | PROJECT: | PROYECTO: | PROJETO: | ПРОЕКТ: | PROJEKT:
Project Name | Nom du Projet | Project Name | Nombre del proyecto | Nome do projeto | Название проекта : | Projektname
SITE: | SITE: | SITE: | SITIO: | OBRA: | ОБЪЕКТ: | Anlage:
DOCUMENT NUMBER: | Numéro de Document : | DOCUMENT NUMBER: | DOCUMENTO NUMERO: | DOCUMENTO Número: | НОМЕР ДОКУМЕНТА: | Dokument Nummer:
Site Name | Nom du Site | Site Name | Nombre del sitio | Nome da obra | Название объекта | Anlagen Name
xyz-SC-DTL | xyz-SC-DTL | xyz-SC-DTL | xyz-SC-DTL | xez-SC-DTL | xyz-SC-DTL | xyz-SC-DTL
DATE | DATE | DATE | FECHA | DATA | ДАТА | DATUM
SIGNATURE | SIGNATURE | SIGNATURE | FIRMA | Assinatura | ПОДПИСЬ | UNTERSCHRIFT
DOCUMENT TITLE SUBSTATION CONTROL SYSTEM DATA LIST | Titre du document LISTE DE DONNEES DU SYSTEME DE Contrôle DE SOUS-STATION | DOCUMENT TITLE SUBSTATION CONTROL SYSTEM DATA LIST | TITULO DEL DOCUMENTO LISTADO DE DATOS DEL SISTEMA DE CONTROL DE LA SUBESTACION | Título DO DOCUMENTO Lista de DADOS DO Sistema de CONTROLE DA SUBESTAÇÃO | Заголовок документа ТАБЛИЦА СИГНАЛОВ АСУ | DOKUMENT TITEL LEITTECHNIKSYSTEM DatumNPUNKTLISTE
DRAWN | CREE | DRAWN | DRAWN | Desenho | МНЕМОСХЕМЫ | ERSTELLT
DSAgile SUBSTATION CONTROL SYSTEM Data List | DSAgile SYSTEME DE COMMANDE DE SOUS-STATION Liste de données | DSAgile SUBSTATION CONTROL SYSTEM Data List | DSAgile SISTEMA DE CONTROL DE SUBESTACIONES Data List | DSAgile Sistema de CONTROLE de SUBESTAÇÕES Lista de Dados | DSAgile АВТОМАТИЗИРОВАННАЯ СИСТЕМА УПРАВЛЕНИЯ Таблица Сигналов | DSAgile LEITTECHNIK Data List
CHECKED | VERIFIE | CHECKED | REVISADO | REVISADO | ПРОВЕРЕНО | GEPRÜFT
APPROVED | APPROUVE | APPROVED | APROBADO | APROVADO | УТВЕРЖДЕНО | BESTÄTIGT
ISSUED BY: | EDITE PAR: | ISSUED BY: | EMITIDO POR: | EMITIDO POR: | Выпущено: | ERSTELLT VON:
SIZE | TAILLE | SIZE | TAMAÑO | TAMANHO | РАЗМЕР | Größe
PAGES | PAGES | PAGES | PAGINAS | PÁGINAS | СТРАНИЦЫ | SEITEN
ISSUE | REVISION | ISSUE | REVISION | REVISÃO | ВЕРСИЯ | VERSION
A3 | A3 | A3 | A3 | A3 | A3 | A3
GE Parc Eurêka 81, rue Euclide 34000 MONTPELLIER | GE Parc Eurêka 81, rue Euclide 34000 MONTPELLIER | GE Parc Eurêka 81, rue Euclide 34000 MONTPELLIER | GE Parc Eurêka 81, rue Euclide 34000 MONTPELLIER | GE Parc Eurêka 81, rue Euclide 34000 MONTPELLIER | GE Parc Eurêka 81, rue Euclide 34000 MONTPELLIER | GE Parc Eurêka 81, rue Euclide 34000 MONTPELLIER
ESTABLISHED | ETABLI PAR | ESTABLISHED | ESTABLISHED | ESTABLISHED | ESTABLISHED | ESTABLISHED
SHEET : History | SHEET : Journal | SHEET : History | SHEET : Historia | SHEET : Histórico | SHEET : История | SHEET : History
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
PACIDL-A | PACIDL-A | PACIDL-A | PACIDL-A | PACIDL-A | PACIDL-A | PACIDL-A
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
BEGIN DATA | DEBUT DES DONNEES | BEGIN DATA | INICIO DE DATOS | INICIO DOS DADOS | НАЧАЛО ДАННЫХ | BEGIN DATA
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Date | Date | Date | Fecha | Data | Дата | Datum
Author | Auteur | Author | Autor | Autor | Автор | Autor
Company | Compagnie | Company | Compañia | Companhia | Компания | Firma
Modifications | Modifications | Modifications | Modificaciones | Modificações | Изменения | Änderungen
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : Equipments | SHEET : Equipements | SHEET : Equipments | SHEET : Equipos | SHEET : Equipamentos | SHEET : Оборудование | SHEET : Equipments
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
EQUIPMENT LIST | LISTE DES EQUIPEMENTS | EQUIPMENT LIST | LISTA DE EQUIPOS | Lista de Equipamentos | СПИСОК ОБОРУДОВАНИЯ | EQUIPMENT LISTE
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
Usual Communication | Communication usuelle | Usual Communication | Habitual Comunicación | Comunicação usual | Передача данных | Ublichen Kommunikation
Legacy T104 Master | Legacy T104 Maître | Legacy T104 Master | Legacy T104 Master | Legacy T104 Master | Legacy T104 Master | Legacy T104 Master
Legacy T101 Master | Legacy T101 Maître | Legacy T101 Master | Legacy T101 Master | Legacy T101 Master | Legacy T101 Master | Legacy T101 Master
Boards | Cartes | Boards | Tarjetas | Placa | Платы | Karten
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
NAME | NOM | NAME | NOMBRE | NOME | ИМЯ | NAME
DESCRIPTION (LONG NAME) | DESCRIPTION (NOM LONG) | DESCRIPTION (LONG NAME) | DESCRIPCION (NOMBRE COMPLETO) | Descrição (Nome COMPLETO) | ОПИСАНИЕ (ДЛИННОЕ ИМЯ) | Beschreibung(Long Name)
LINK | COMMUNICATION | LINK | VINCULO | VINCULO | СВЯЗЬ | LINK
REDUNDANT | REDONDANCE | REDUNDANT | REDUNDANTE | REDUNDANTE | С РЕЗЕРВИРОВАНИЕМ | REDUNDANT
TYPE | TYPE | TYPE | TIPO | TIPO | МОДЕЛЬ | TYPE
Substation Name | Nom de la Sous-station | Substation Name | Nombre de subestación | Nome do Substação | Имя подстанции | Stationsname:
Bay mimic | Tranche mimic | Bay mimic | Mímico de bahía | Mímico do Painel | Мнемосхема Ячейки | Bay mimic
Synchronisation mode | MODE DE SYNCHRONISATION | Synchronisation mode | Modo de sincronización | Modo de Sincronização | Режим синхронизации | Synchronisation mode
Network Name | NOM DU RESEAU | Network Name | Nombre de red | Nome da rede | Сетевое Имя | Netzwerk Name
TCP/IP (IEC) Address | Adresse TCP/IP (IEC) | TCP/IP (IEC) Address | Dirección TCP/IP (IEC) | Endereço TCP/IP (IEC) | TCP/IP (IEC) Адрес | TCP/IP (IEC) Addresse
Port 1 | Port 1 | Port 1 | Puerto 1 | Porta 1 | Порт 1 | Port 1
Protocol Name | Nom de protocole | Protocol Name | Nombre de Protocolo | Nome do Protocolo | ИМЯ Протокола | Protocol Name
Port 2 | Port 2 | Port 2 | Puerto 2 | Porta 2 | Порт 2 | Port 2
Protocol Name | Nom de protocole | Protocol Name | Nombre de Protocolo | Nome do Protocolo | ИМЯ Протокола | Protocol Name
Port 3 | Port 3 | Port 3 | Puerto 3 | Porta 3 | Порт 3 | Port 3
Protocol Name | Nom de protocole | Protocol Name | Nombre de Protocolo | Nome do Protocolo | ИМЯ Протокола | Protocol Name
Port 4 | Port 4 | Port 4 | Puerto 4 | Porta 4 | Порт 4 | Port 4
Protocol Name | Nom de protocole | Protocol Name | Nombre de Protocolo | Nome do Protocolo | ИМЯ Протокола | Protocol Name
Id1 T104M (+ IED Addr) | Id1 T104M (+ IED Adr) | Id1 T104M (+ IED Addr) | Id1 T104M (Direcc + IED) | Id1 T104M (Direcc + IED) | Id1 T104M (+ адрес IED) | Id1 T104M (+ IED Addr)
Id2 T104M (+ IED Addr) | Id2 T104M (+ IED Adr) | Id2 T104M (+ IED Addr) | Id2 T104M (Direcc + IED) | Id2 T104M (Direcc + IED) | Id2 T104M (+ адрес IED) | Id2 T104M (+ IED Addr)
Id3 T104M (+ IED Addr) | Id3 T104M (+ IED Adr) | Id3 T104M (+ IED Addr) | Id3 T104M (Direcc + IED) | Id3 T104M (Direcc + IED) | Id3 T104M (+ адрес IED) | Id3 T104M (+ IED Addr)
Id4 T104M (+ IED Addr) | Id4 T104M (+ IED Adr) | Id4 T104M (+ IED Addr) | Id4 T104M (Direcc + IED) | Id4 T104M (Direcc + IED) | Id4 T104M (+ адрес IED) | Id4 T104M (+ IED Addr)
Id1 T101M (+ IED Addr) | Id1 T101M (+ IED Adr) | Id1 T101M (+ IED Addr) | Id1 T101M (Direcc + IED) | Id1 T101M (Direcc + IED) | Id1 T101M (+ адрес IED) | Id1 T101M (+ IED Addr)
Id2 T101M (+ IED Addr) | Id2 T101M (+ IED Adr) | Id2 T101M (+ IED Addr) | Id2 T101M (Direcc + IED) | Id2 T101M (Direcc + IED) | Id2 T101M (+ адрес IED) | Id2 T101M (+ IED Addr)
Id3 T101M (+ IED Addr) | Id3 T101M (+ IED Adr) | Id3 T101M (+ IED Addr) | Id3 T101M (Direcc + IED) | Id3 T101M (Direcc + IED) | Id3 T101M (+ адрес IED) | Id3 T101M (+ IED Addr)
Id4 T101M (+ IED Addr) | Id4 T101M (+ IED Adr) | Id4 T101M (+ IED Addr) | Id4 T101M (Direcc + IED) | Id4 T101M (Direcc + IED) | Id4 T101M (+ адрес IED) | Id4 T101M (+ IED Addr)
IEC61850 Protocol Id | Id Protocole IEC61850 | IEC61850 Protocol Id | IEC61850 Protocolo Id | IEC61850 Protocolo Id | IEC61850 Протокола Id | IEC61850 Protocol Id
OPC Protocol Id | Id Protocole OPC | OPC Protocol Id | OPC Protocolo Id | OPC Protocolo Id | OPC Протокола Id | OPC Protocol Id
DIU2xx | DIU2xx | DIU2xx | DIU2xx | DIU2xx | DIU2xx | DIU2xx
CCU20x | CCU20x | CCU20x | CCU20x | CCU20x | CCU20x | CCU20x
DOU20x | DOU20x | DOU20x | DOU20x | DOU20x | DOU20x | DOU20x
HBU20x | HBU20x | HBU20x | HBU20x | HBU20x | HBU20x | HBU20x
AIU20x | AIU20x | AIU20x | AIU20x | AIU20x | AIU20x | AIU20x
AIU21x | AIU21x | AIU21x | AIU21x | AIU21x | AIU21x | AIU21x
TMU2x0 | TMU2x0 | TMU2x0 | TMU2x0 | TMU2x0 | TMU2x0 | TMU2x0
DSP210 | DSP210 | DSP210 | DSP210 | DSP210 | DSP210 | DSP210
AOU20x | AOU20x | AOU20x | AOU20x | AOU20x | AOU20x | AOU20x
SWx | SWx | SWx | SWx | SWx | SWx | SWx
Extension Racks | Racks d'Extension | Extension Racks | Extensión bastidores | Extensão Racks | продление стеллажи | Erweiterung Racks
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Sheet Name | Nom de la Feuille | Sheet Name | Nombre de hoja | Nome da Planilha | Имя Страницы | Sheet Name
DIU32 | DIU32 | DIU32 | DIU32 | DIU32 | DIU32 | DIU32
SUMMARY | RESUME | SUMMARY | RESUMEN | RESUMO | КРАТКИЙ | ZUSAMMENFASSUNG
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : Computers Arrangement | SHEET : Arrangement des Calculateurs | SHEET : Computers Arrangement | SHEET : Computadors Arrangement | SHEET : Arranjo dos Computadores | SHEET : Компановка контроллеров | SHEET : Computers Arrangement
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
MiCOM COMPUTERS HARDWARE DESCRIPTION | DESCRIPTION MATERIELLE DES CALCULATEURS MICOM | MiCOM COMPUTERS HARDWARE DESCRIPTION | DESCRIPCION DEL HARDWARE COMPUTADOR MiCOM | Descrição DO HARDWARE COMPUTADOR MiCOM | ОПИСАНИЕ УСТРОЙСТВА КОНТРОЛЛЕРОВ MiCOM | MiCOM COMPUTERS HARDWARE BESCHREIBUNG
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Auto generated | Génération automatique | Auto generated | Auto generado | Auto Geração | Автоматически сгенерировано | Auto generated
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
ERROR | ERREUR | ERROR | ERROR | ERRO | ОШИБКА | FEHLER
C264 Ext Rack | C264 Rack d'Ext. | C264 Ext Rack | C264 Ext Rack | C264 Ext Rack | C264 Ext Rack | C264 Ext Rack
C264C Ext Rack | C264C Rack d'Ext. | C264C Ext Rack | C264C Ext Rack | C264C Ext Rack | C264C Ext Rack | C264C Ext Rack
Computer type (C264/C264C): | Type de Calculateur (C264/C264C): | Computer type (C264/C264C): | Typo de computador (C264/C264C): | Tipo de computador (C264/C264C): | Тип контроллера (C264/C264C): | Computer type (C264/C264C):
C264 | C264 | C264 | C264 | C264 | C264 | C264
back face | Face arriere | back face | panel posterior | Painel Traseiro | Тыльная сторона | back face
APPLICABLE | PRINCIPAL | APPLICABLE | APLICABLE | Aplicável | ПРИМЕНЯЕМЫЙ | APPLICABLE
REDUNDANT | REDONDANCE | REDUNDANT | REDUNDANTE | REDUNDANTE | С РЕЗЕРВИРОВАНИЕМ | REDUNDANT
PANEL | ECRAN | PANEL | PANEL | PAINEL | ПАНЕЛЬ | PANEL
COMMENTS | COMMENTAIRES | COMMENTS | COMENTARIOS | COMENTÃRIOS | КОММЕНТАРИИ | KOMMENTAR
Port 1 | Port 1 | Port 1 | Puerto 1 | Porta 1 | Порт 1 | Port 1
Port 2 | Port 2 | Port 2 | Puerto 2 | Porta 2 | Порт 2 | Port 2
Port 3 | Port 3 | Port 3 | Puerto 3 | Porta 3 | Порт 3 | Port 3
Port 4 | Port 4 | Port 4 | Puerto 4 | Porta 4 | Порт 4 | Port 4
front slot number: | Numéro de position devant: | front slot number: | número de slot frontal: | Número do Slot Frontal: | номер слота на фронтальной стороне: | front slot number:
COMPUTER NAME | NOM DU CALCULATEUR | COMPUTER NAME | NOMBRE DEL COMPUTADOR | Nome do Computador | ИМЯ КОНТРОЛЛЕРА | COMPUTER NAME
NUMBER | NUMERO | NUMBER | NUMERO | NUMERO | НОМЕР | ANZAHL
BIU240 Port 1 | BIU240 Port 1 | BIU240 Port 1 | BIU240 Puerto 1 | BIU240 Porta 1 | BIU240 Порт 1 | BIU240 Port 1
BIU240 Port 2 | BIU240 Port 2 | BIU240 Port 2 | BIU240 Puerto 2 | BIU240 Porta 2 | BIU240 Порт 2 | BIU240 Port 2
CPU Port 1 | CPU Port 1 | CPU Port 1 | CPU Puerto 1 | CPU Porta 1 | CPU Портt 1 | CPU Port 1
CPU Port 2 | CPU Port 2 | CPU Port 2 | CPU Puerto 2 | CPU Porta 2 | CPU Порт 2 | CPU Port 2
back slot number: | Numéro de position arrière: | back slot number: | número de slot posterior: | número de Slot posterior: | номер слота на тыльной стороне: | back slot number:
Protocol Type | Type de Protocole | Protocol Type | Tipo de protocolo | Tipo de Protocolo | Тип протокола | Protocol Type
CPU 260 + COMMUNICATION | CPU 260 + COMMUNICATION | CPU 260 + COMMUNICATION | CPU 260 + COMUNICACION | CPU 260 + COMUNICAÇÃO | CPU 260 + ЛИНИИ СВЯЗИ | CPU 260 + COMMUNICATION
BIU 241 | BIU 241 | BIU 241 | BIU 241 | BIU 241 | BIU 241 | BIU 241
Baud Rate | Vitesse de la communication (en Baud) | Baud Rate | Bauidos | Baud Rate | Скорость в бодах | Baud Rate
RS Type | RS Type | RS Type | Tipo de RS | Tipo de RS | Тип RS | RS Type
Parity | Parité | Parity | Paridad | Paridade | Четность | Parity
Number Stop bits | Nombre de bits de stop | Number Stop bits | Número de bits de paro | Número de bits de paro | Number Stop bits | Anzahl Stop bits
Number bits | Nombre de bits | Number bits | Número de bits | Número de bits | Number bits | Anzahl bits
Rx Management | Gestion de RX | Rx Management | Administración de Rx | Administração de Rx | Управление Rx | Rx Management
Tx Management | Gestion de TX | Tx Management | Administración de Tx | Administração de Tx | Управление Tx | Tx Management
CTS wired | CTS Câblé | CTS wired | CTS cableadas | CTS Linkados | CTS wired | CTS wired
DTS wired | Câblage de DTS | DTS wired | DTS cableadas | DTS Linkados | DTS wired | DTS wired
CD wired | Câblage de CD | CD wired | CD cableadas | CD Linkados | CD wired | CD wired
logical number: | Numéro logique: | logical number: | número lógico: | número lógico: | логический номер: | logical number:
DCR wired | Câblage de DCR | DCR wired | DCR cableadas | DCR Linkados | DCR wired | DCR wired
CPU 270 + COMMUNICATION | CPU 270 + COMMUNICATION | CPU 270 + COMMUNICATION | CPU 270 + COMUNICACION | CPU 270 + COMUNICAÇÃO | CPU 270 + ЛИНИИ СВЯЗИ | CPU 270 + COMMUNICATION
Computer type (C264/C264C): | Type de Calculateur (C264/C264C): | Computer type (C264/C264C): | Typo de computador (C264/C264C): | Tipo de computador (C264/C264C): | Тип контроллера (C264/C264C): | Computer type (C264/C264C):
C264C | C264C | C264C | C264C | C264C | C264C | C264C
back face | Face arriere | back face | panel posterior | Painel Traseiro | Тыльная сторона | back face
APPLICABLE | PRINCIPAL | APPLICABLE | APLICABLE | Aplicável | ПРИМЕНЯЕМЫЙ | APPLICABLE
REDUNDANT | REDONDANCE | REDUNDANT | REDUNDANTE | REDUNDANTE | С РЕЗЕРВИРОВАНИЕМ | REDUNDANT
PANEL | ECRAN | PANEL | PANEL | PAINEL | ПАНЕЛЬ | PANEL
COMMENTS | COMMENTAIRES | COMMENTS | COMENTARIOS | COMENTÃRIOS | КОММЕНТАРИИ | KOMMENTAR
Port 1 | Port 1 | Port 1 | Puerto 1 | Porta 1 | Порт 1 | Port 1
Port 2 | Port 2 | Port 2 | Puerto 2 | Porta 2 | Порт 2 | Port 2
Port 3 | Port 3 | Port 3 | Puerto 3 | Porta 3 | Порт 3 | Port 3
Port 4 | Port 4 | Port 4 | Puerto 4 | Porta 4 | Порт 4 | Port 4
front slot number: | Numéro de position devant: | front slot number: | número de slot frontal: | Número do Slot Frontal: | номер слота на фронтальной стороне: | front slot number:
COMPUTER NAME | NOM DU CALCULATEUR | COMPUTER NAME | NOMBRE DEL COMPUTADOR | Nome do Computador | ИМЯ КОНТРОЛЛЕРА | COMPUTER NAME
NUMBER | NUMERO | NUMBER | NUMERO | NUMERO | НОМЕР | ANZAHL
BIU240 Port 1 | BIU240 Port 1 | BIU240 Port 1 | BIU240 Puerto 1 | BIU240 Porta 1 | BIU240 Порт 1 | BIU240 Port 1
BIU240 Port 2 | BIU240 Port 2 | BIU240 Port 2 | BIU240 Puerto 2 | BIU240 Porta 2 | BIU240 Порт 2 | BIU240 Port 2
CPU Port 1 | CPU Port 1 | CPU Port 1 | CPU Puerto 1 | CPU Porta 1 | CPU Портt 1 | CPU Port 1
CPU Port 2 | CPU Port 2 | CPU Port 2 | CPU Puerto 2 | CPU Porta 2 | CPU Порт 2 | CPU Port 2
back slot number: | Numéro de position arrière: | back slot number: | número de slot posterior: | número de Slot posterior: | номер слота на тыльной стороне: | back slot number:
Protocol Type | Type de Protocole | Protocol Type | Tipo de protocolo | Tipo de Protocolo | Тип протокола | Protocol Type
TMU2x0 (slot 2/2) | TMU2x0 (slot 2/2) | TMU2x0 (slot 2/2) | TMU2x0 (slot 2/2) | TMU2x0 (Slot 2/2) | TMU2x0 (слот 2/2) | TMU2x0 (slot 2/2)
TMU2x0 (slot 1/2) | TMU2x0 (slot 1/2) | TMU2x0 (slot 1/2) | TMU2x0 (slot 1/2) | TMU2x0 (Slot 1/2) | TMU2x0 (слот 1/2) | TMU2x0 (slot 1/2)
CPU 260 + COMMUNICATION | CPU 260 + COMMUNICATION | CPU 260 + COMMUNICATION | CPU 260 + COMUNICACION | CPU 260 + COMUNICAÇÃO | CPU 260 + ЛИНИИ СВЯЗИ | CPU 260 + COMMUNICATION
BIU 241 | BIU 241 | BIU 241 | BIU 241 | BIU 241 | BIU 241 | BIU 241
Baud Rate | Vitesse de la communication (en Baud) | Baud Rate | Bauidos | Baud Rate | Скорость в бодах | Baud Rate
RS Type | RS Type | RS Type | Tipo de RS | Tipo de RS | Тип RS | RS Type
Parity | Parité | Parity | Paridad | Paridade | Четность | Parity
Number Stop bits | Nombre de bits de stop | Number Stop bits | Número de bits de paro | Número de bits de paro | Number Stop bits | Anzahl Stop bits
Number bits | Nombre de bits | Number bits | Número de bits | Número de bits | Number bits | Anzahl bits
Rx Management | Gestion de RX | Rx Management | Administración de Rx | Administração de Rx | Управление Rx | Rx Management
Tx Management | Gestion de TX | Tx Management | Administración de Tx | Administração de Tx | Управление Tx | Tx Management
CTS wired | CTS Câblé | CTS wired | CTS cableadas | CTS Linkados | CTS wired | CTS wired
DTS wired | Câblage de DTS | DTS wired | DTS cableadas | DTS Linkados | DTS wired | DTS wired
CD wired | Câblage de CD | CD wired | CD cableadas | CD Linkados | CD wired | CD wired
logical number: | Numéro logique: | logical number: | número lógico: | número lógico: | логический номер: | logical number:
DCR wired | Câblage de DCR | DCR wired | DCR cableadas | DCR Linkados | DCR wired | DCR wired
CPU 270 + COMMUNICATION | CPU 270 + COMMUNICATION | CPU 270 + COMMUNICATION | CPU 270 + COMUNICACION | CPU 270 + COMUNICAÇÃO | CPU 270 + ЛИНИИ СВЯЗИ | CPU 270 + COMMUNICATION
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : C264_Template | SHEET : C264_Template | SHEET : C264_Template | SHEET : C264_Template | SHEET : C264_Template | SHEET : C264_Template | SHEET : C264_Template
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
MiCOM C264 DESCRIPTION | DESCRIPTION DU MiCOM C264 | MiCOM C264 DESCRIPTION | DESCRIPCION MiCOM C264 | Descrição MiCOM C264 | ОПИСАНИЕ MiCOM C264 | MiCOM C264 BESCHREIBUNG
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
Computer Name | Nom du Calculateur | Computer Name | Nombre de computador | Nome do computador | Имя контроллера | Computer Name
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Redundant Computer | Calculateur Redondant | Redundant Computer | Computador Redundante | Computador Redundante | Резервный компьютер | Redundant Computer
Auto generated | Génération automatique | Auto generated | Auto generado | Auto Geração | Автоматически сгенерировано | Auto generated
Computer type (C264/C264C) | Type de Calculateur (C264/C264C) | Computer type (C264/C264C) | Tipo de computador (C264/C264C) | Tipo de computador (C264/C264C) | Тип контроллера (C264/C264C) | Computer type (C264/C264C)
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
Gateway | Passerelle | Gateway | UTR | UTR | Шлюз | Gateway
Port used (on gateway) | Ports utilisés (sur la passerelle) | Port used (on gateway) | Puerto utilizado (en UTR) | Porta utilizada (em UTR) | Используемый порт (на шлюз) | benutzter Port (Gateway)
SCADA 1 | SCADA 1 | SCADA 1 | SCADA 1 | SCADA 1 | SCADA 1 | SCADA 1
SCADA 2 | SCADA 2 | SCADA 2 | SCADA 2 | SCADA 2 | SCADA 2 | SCADA 2
SCADA 3 | SCADA 3 | SCADA 3 | SCADA 3 | SCADA 3 | SCADA 3 | SCADA 3
SCADA 4 | SCADA 4 | SCADA 4 | SCADA 4 | SCADA 4 | SCADA 4 | SCADA 4
DIGITAL INPUT BOARD DIU32 | Carte d'entrées numériques DIU32 | DIGITAL INPUT BOARD DIU32 | TARJETAS DE ENTRADAS DIGITALES DIU32 | Etiquetas de Entradas Digitais DIU32 | ПЛАТЫ DIU32 | DIGITALE EINGANGSKARTE DIU32
DIGITAL INPUT BOARD DIU2xx | Carte d'entrées numériques DIU2xx | DIGITAL INPUT BOARD DIU2xx | TARJETAS DE ENTRADAS DIGITALES DIU2xx | Etiquetas de Entradas Digitais DIU2xx | ПЛАТЫ DIU2xx | DIGITALE EINGANGSKARTE DIU2xx
Digital Inputs Board Number | Numéro de la carte d'entrées numériques | Digital Inputs Board Number | Tarjeta de entradas digitales Número | Etiqueta de Entradas digitais Número | Номер платы DI | Digital Inputs Board Number
Digital Inputs Board Slot | Position de la carte d'entrées numériques | Digital Inputs Board Slot | Tarjeta de entradas digitales Slot | Etiqueta de Entradas digitais Slot | Слот платы DI | Digital Inputs Board Slot
Digital Inputs Extension Rack Number | Numéro rack d'extension de la carte d'entrées numériques | Digital Inputs Extension Rack Number | Tarjeta de entradas digitales Extensión Rack Número | Etiqueta de Entradas digitais Extensão Rack Número | продлению стойки Количество DI | Digital Inputs Extension Rack Number
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
DI Reference | Référence DI | DI Reference | DI Referencia | DI Referência | Ссылка DI | DI Referenz
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels / States | Libellés/Etats | Labels / States | Etiquetas/Estados | Etiquetas/Estados | Метки / Состояния | Labels / States
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Groups | Groupes | Groups | Grupos | Grupos | Группы | Gruppen
Local Display | Affichage Local | Local Display | Despliegue Local | Display Local | Локальный дисплей | Local Display
HMI | HMI | HMI | IHM | IHM | HMI | HMI
DI/DO Link | Lien DI/DO | DI/DO Link | DI/DO Vínculo | DI/DO Vínculo | DI/DO связи | DI/DO Link
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
Slot | Position | Slot | Slot | Slot | Слот | Slot
Channel | Voie | Channel | Canal | Canal | Канал | Channel
Function | Fonction | Function | Función | Função | Функция | Function
Type (SPS=Single/DPS=Dual/MPS=Multiple) | Type (SPS=Simple/DPS=Double/MPS=Multiple) | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Tipo (SPS=Sencilla/DPS=Dual/MPS=Multiple) | Tipo (SPS=Simples/DPS=Duplo/MPS=Múltiplo) | Тип (SPS=Single/DPS=Dual/MPS=Multiple) | Type (SPS=Single/DPS=Dual/MPS=Multiple)
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Simple : Texte à l'état électrique = 1 Double : Texte à l'état électrique = 10 Multiple : label d'état (16 car) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Sencilla : Texto en estado eléctrico = 1 Dual : Texto en estado eléctrico = 10 Multiple : Texto (16 caract) | Simples: Texto em estado Elétrico = 1 Duplo : Texto em estado Elétrico = 10 Múltiplo : Texto (16 caract) | Одиночный : Обозначение электрического состояния = 1 Двойной : Обозначение электрического состояния = 10 Множественный: Обозначение (16 символов) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char)
Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Simple : Texte à l'état électrique = 0 Double : Texte à l'état électrique = 01 Multiple : Numéro d'état (16 car) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Sencilla : Texto en estado eléctrico = 0 Dual : Texto en estado eléctrico = 01 Multiple : Número de estado (16 caract) | Simples: Texto em estado Elétrico = 0 Duplo : Texto em estado Elétrico = 01 Múltiplo : Número de estado (16 caract) | Одиночный : Обозначение электрического состояния = 0 Двойной : Обозначение электрического состояния = 01 Множественный : Состояние Number (16 символов) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char)
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
Computers Groups (separator ";") | Groupes de calculateur (séparateur ";") | Computers Groups (separator ";") | Grupos de Computadoras (separador ";") | Grupos de Computadores (separador ";") | Группы контроллеров (разделитель ";") | Computers Gruppen (separator ";")
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
LED | LED | LED | LED | LED | индикатор | LED
LCD Display | Affichage LCD | LCD Display | Pantalla LCD | Vista LCD | LCD Дисплей | LCD Display
HMI Display | Affichage HMI | HMI Display | Pantalla IHM | Vista IHM | HMI Дисплей | HMI Display
Is a xPC Feedback | Est un retour de position xPC | Is a xPC Feedback | Es una xPC de retroalimentación | É FeedBack de xPC | Присутствует xPC обратная связь | Is a xPC Feedback
Acts on xPC | Acté sur xPC | Acts on xPC | Actúa en xPC | Atua em xPC | Действует на с xPC | Acts on xPC
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Is used by distributed Automation (GOOSE) | Est utilisé par la distribution automatique (GOOSE) | Is used by distributed Automation (GOOSE) | Se utiliza por automatización distribuida (GOOSE) | Se utiliza por Automação distribuida (GOOSE) | Используется распределенной автоматикой (GOOSE) | Is used by distributed Automation (GOOSE)
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
DIGITAL OUTPUT BOARD DOU20x | Carte de sorties numériques DOU20x | DIGITAL OUTPUT BOARD DOU20x | TARJETAS DIGITALES SALIDAS DOU20x | Placas de Saídas Digitais DOU20x | ПЛАТЫ DOU20x | DIGITALE AUSGANGSKARTE DOU20x
Digital Outputs Board Number | Numéro de la carte de sorties numériques | Digital Outputs Board Number | Número de tarjeta de salidas digitales | Número de Etiqueta de saidas digitais | Номер платы DO | Digitale Ausgangskarte Nummer
Digital Outputs Board Slot | Position de la carte de sorties numériques | Digital Outputs Board Slot | Slot de trajeta de salidas digitales | Slot de trajeta de saidas digitais | Слот платы DO | Digitale Ausgangskarte Steckplatz
Digital Outputs Extension Rack Number | Numéro rack d'extension de la carte de sorties numériques | Digital Outputs Extension Rack Number | Tarjeta de salidas digitales Extensión Rack Número | Etiqueta de saidas digitais Extensão Rack Número | продлению стойки Количество DO | Digitale Ausgangskarte Extension Rack Nummer
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
DO Reference | Référence DO | DO Reference | Referencia DO | Referência DO | Ссылка DO | DO Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Local Control | Contrôle Local | Local Control | Control Local | Controle Local | местного контроля | Local Control
HMI | HMI | HMI | IHM | IHM | HMI | HMI
DI/DO Link | Lien DI/DO | DI/DO Link | DI/DO Vínculo | DI/DO Vínculo | DI/DO связи | DI/DO Link
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
Slot | Position | Slot | Slot | Slot | Слот | Slot
Channel | Voie | Channel | Canal | Canal | Канал | Channel
Function | Fonction | Function | Función | Função | Функция | Function
Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Type (SPC=Simple/DPC=Double/DS=Dual Switch) | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Tipo (SPC=Sencilla/DPC=Dual/DS=Dual Switch) | Tipo (SPC=Simples/DPC=Duplo/DS=Dual Switch) | Тип (SPC=Single/DPC=Dual/DS=Dual Switch) | Type (SPC=Single/DPC=Dual/DS=Dual Switch)
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Simple : Texte à l'état électrique = 1 Double : Texte à l'état électrique = 10 (16 car) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Sencilla : Texto en estado eléctrico = 1 Dual : Texto en estado eléctrico = 10 (16 caract) | Simples: Texto em estado Elétrico = 1 Duplo : Texto em estado Elétrico = 10 (16 caract) | Одиночный : Обозначение электрического состояния = 1 Двойной : Обозначение электрического состояния = 10 (16 символов) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char)
Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Simple : Texte à l'état électrique = 0 Double : Texte à l'état électrique =01 (16 car) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Sencilla : Texto en estado eléctrico = 0 Dual : Texto en estado eléctrico = 01 (16 caract) | Simples: Texto em estado Elétrico = 0 Duplo : Texto em estado Elétrico = 01 (16 caract) | Одиночный : Обозначение электрического состояния = 0 Двойной : Обозначение электрического состояния = 01 (16 символов) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char)
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
LCD Control | Contrôle LCD | LCD Control | Control LCD | Ordem desde LCD | Управление LCD | LCD Control
HMI Control | Contrôle HMI | HMI Control | Control IHM | Ordem desde IHM | Управление HMI | HMI Control
Has a xPS Feedback | A un retour de position xPS | Has a xPS Feedback | Contiene retroalimentación xPS | Possui FeedBack xPS | имеет xPS отзывы | Has a xPS Feedback
Is activated by xPS | Est activé par xPS | Is activated by xPS | Es activado por xPS | É ativado por xPS | Активируется с помощью xPS | Is activated by xPS
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Relay | Relais | Relay | Relé | Relé | Реле | Relay
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
HIGH BREAK UNIT BOARD HBU20x | Carte de sorties numériques HBU20x | HIGH BREAK UNIT BOARD HBU20x | TARJETAS HBU SALIDAS HBU20x | Placas de Saídas Digitais DOU20x | ПЛАТЫ HBU20x | HBU AUSGANGSKARTE HBU20x
HBU Board Number | Numéro de la carte de sorties numériques HBU | HBU Board Number | Número de tarjeta de salidas digitales | Número de Etiqueta de saidas HBU | Номер платы HBU | HBU Ausgangskarte Nummer
HBU Board Slot | Position de la carte de sorties numériques HBU | HBU Board Slot | Slot de trajeta de salidas digitales | Slot de trajeta de saidas HBU | Слот платы HBU | HBU Ausgangskarte Steckplatz
HBU Extension Rack Number | Numéro rack d'extension de la carte de sorties numériques HBU | HBU Extension Rack Number | Tarjeta de salidas digitales Extensión Rack Número | Etiqueta de saidas HBU Extensão Rack Número | продлению стойки Количество HBU | HBU Ausgangskarte Extension Rack Nummer
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
DO Reference | Référence DO | DO Reference | Referencia DO | Referência DO | Ссылка DO | DO Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Local Control | Contrôle Local | Local Control | Control Local | Controle Local | местного контроля | Local Control
HMI | HMI | HMI | IHM | IHM | HMI | HMI
DI/DO Link | Lien DI/DO | DI/DO Link | DI/DO Vínculo | DI/DO Vínculo | DI/DO связи | DI/DO Link
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
Slot | Position | Slot | Slot | Slot | Слот | Slot
Channel | Voie | Channel | Canal | Canal | Канал | Channel
Function | Fonction | Function | Función | Função | Функция | Function
Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Type (SPC=Simple/DPC=Double/DS=Dual Switch) | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Tipo (SPC=Sencilla/DPC=Dual/DS=Dual Switch) | Tipo (SPC=Simples/DPC=Duplo/DS=Dual Switch) | Тип (SPC=Single/DPC=Dual/DS=Dual Switch) | Type (SPC=Single/DPC=Dual/DS=Dual Switch)
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Simple : Texte à l'état électrique = 1 Double : Texte à l'état électrique = 10 (16 car) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Sencilla : Texto en estado eléctrico = 1 Dual : Texto en estado eléctrico = 10 (16 caract) | Simples: Texto em estado Elétrico = 1 Duplo : Texto em estado Elétrico = 10 (16 caract) | Одиночный : Обозначение электрического состояния = 1 Двойной : Обозначение электрического состояния = 10 (16 символов) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char)
Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Simple : Texte à l'état électrique = 0 Double : Texte à l'état électrique =01 (16 car) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Sencilla : Texto en estado eléctrico = 0 Dual : Texto en estado eléctrico = 01 (16 caract) | Simples: Texto em estado Elétrico = 0 Duplo : Texto em estado Elétrico = 01 (16 caract) | Одиночный : Обозначение электрического состояния = 0 Двойной : Обозначение электрического состояния = 01 (16 символов) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char)
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
LCD Control | Contrôle LCD | LCD Control | Control LCD | Ordem desde LCD | Управление LCD | LCD Control
HMI Control | Contrôle HMI | HMI Control | Control IHM | Ordem desde IHM | Управление HMI | HMI Control
Has a xPS Feedback | A un retour de position xPS | Has a xPS Feedback | Contiene retroalimentación xPS | Possui FeedBack xPS | имеет xPS отзывы | Has a xPS Feedback
Is activated by xPS | Est activé par xPS | Is activated by xPS | Es activado por xPS | É ativado por xPS | Активируется с помощью xPS | Is activated by xPS
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Relay | Relais | Relay | Relé | Relé | Реле | Relay
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
DIGITAL INPUT/OUTPUT BOARD CCU20x | Carte entrées/sorties numériques CCU20x | DIGITAL INPUT/OUTPUT BOARD CCU20x | TARJETAS DIGITALES ENTRADAS/SALIDAS CCU20x | Etiquetas digitais Entradas/saidas CCU20x | ПЛАТЫ CCU20x | DIGITAL EINGANGS-/AUSGANGSKARTE U200
DI/DO Board Number | Numéro de la carte DI/DO | DI/DO Board Number | Número de tarjeta DI/DO | Número de Etiqueta DI/DO | Номер плат DI/DO | DI/DO Karte Nummer
DI/DO Board Slot | Position de la carte DI/DO | DI/DO Board Slot | Slot de Tarjeta DI/DO | Slot do Cartão DI/DO | Слот платы DI/DO | DI/DO Karte Steckplatz
DI/DO Extension Rack Number | Numéro rack d'extension de la carte DI/DO | DI/DO Extension Rack Number | Tarjeta DI/DO Extensión Rack Número | Etiqueta DI/DO Extensão Rack Número | продлению стойки Количество DI/DO | DI/DO Extension Rack Nummer
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
DI Reference | Référence DI | DI Reference | DI Referencia | DI Referência | Ссылка DI | DI Referenz
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels / States | Libellés/Etats | Labels / States | Etiquetas/Estados | Etiquetas/Estados | Метки / Состояния | Labels / States
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Groups | Groupes | Groups | Grupos | Grupos | Группы | Gruppen
Local Display | Affichage Local | Local Display | Despliegue Local | Display Local | Локальный дисплей | Local Display
HMI | HMI | HMI | IHM | IHM | HMI | HMI
DI/DO Link | Lien DI/DO | DI/DO Link | DI/DO Vínculo | DI/DO Vínculo | DI/DO связи | DI/DO Link
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
Slot | Position | Slot | Slot | Slot | Слот | Slot
Channel | Voie | Channel | Canal | Canal | Канал | Channel
Function | Fonction | Function | Función | Função | Функция | Function
Type (SPS=Single/DPS=Dual/MPS=Multiple) | Type (SPS=Simple/DPS=Double/MPS=Multiple) | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Tipo (SPS=Sencilla/DPS=Dual/MPS=Multiple) | Tipo (SPS=Simples/DPS=Duplo/MPS=Múltiplo) | Тип (SPS=Single/DPS=Dual/MPS=Multiple) | Type (SPS=Single/DPS=Dual/MPS=Multiple)
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Simple : Texte à l'état électrique = 1 Double : Texte à l'état électrique = 10 Multiple : label d'état (16 car) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Sencilla : Texto en estado eléctrico = 1 Dual : Texto en estado eléctrico = 10 Multiple : Texto (16 caract) | Simples: Texto em estado Elétrico = 1 Duplo : Texto em estado Elétrico = 10 Múltiplo : Texto (16 caract) | Одиночный : Обозначение электрического состояния = 1 Двойной : Обозначение электрического состояния = 10 Множественный: Обозначение (16 символов) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char)
Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Simple : Texte à l'état électrique = 0 Double : Texte à l'état électrique = 01 Multiple : Numéro d'état (16 car) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Sencilla : Texto en estado eléctrico = 0 Dual : Texto en estado eléctrico = 01 Multiple : Número de estado (16 caract) | Simples: Texto em estado Elétrico = 0 Duplo : Texto em estado Elétrico = 01 Múltiplo : Número de estado (16 caract) | Одиночный : Обозначение электрического состояния = 0 Двойной : Обозначение электрического состояния = 01 Множественный : Состояние Number (16 символов) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char)
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
Computers Groups (separator ";") | Groupes de calculateur (séparateur ";") | Computers Groups (separator ";") | Grupos de Computadoras (separador ";") | Grupos de Computadores (separador ";") | Группы контроллеров (разделитель ";") | Computers Gruppen (separator ";")
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
LED | LED | LED | LED | LED | индикатор | LED
LCD Display | Affichage LCD | LCD Display | Pantalla LCD | Vista LCD | LCD Дисплей | LCD Display
HMI Display | Affichage HMI | HMI Display | Pantalla IHM | Vista IHM | HMI Дисплей | HMI Display
Is a xPC Feedback | Est un retour de position xPC | Is a xPC Feedback | Es una xPC de retroalimentación | É FeedBack de xPC | Присутствует xPC обратная связь | Is a xPC Feedback
Acts on xPC | Acté sur xPC | Acts on xPC | Actúa en xPC | Atua em xPC | Действует на с xPC | Acts on xPC
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Is used by distributed Automation (GOOSE) | Est utilisé par la distribution automatique (GOOSE) | Is used by distributed Automation (GOOSE) | Se utiliza por automatización distribuida (GOOSE) | Se utiliza por Automação distribuida (GOOSE) | Используется распределенной автоматикой (GOOSE) | Is used by distributed Automation (GOOSE)
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
DO Reference | Référence DO | DO Reference | Referencia DO | Referência DO | Ссылка DO | DO Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Local Control | Contrôle Local | Local Control | Control Local | Controle Local | местного контроля | Local Control
HMI | HMI | HMI | IHM | IHM | HMI | HMI
DI/DO Link | Lien DI/DO | DI/DO Link | DI/DO Vínculo | DI/DO Vínculo | DI/DO связи | DI/DO Link
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
Slot | Position | Slot | Slot | Slot | Слот | Slot
Channel | Voie | Channel | Canal | Canal | Канал | Channel
Function | Fonction | Function | Función | Função | Функция | Function
Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Type (SPC=Simple/DPC=Double/DS=Dual Switch) | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Tipo (SPC=Sencilla/DPC=Dual/DS=Dual Switch) | Tipo (SPC=Simples/DPC=Duplo/DS=Dual Switch) | Тип (SPC=Single/DPC=Dual/DS=Dual Switch) | Type (SPC=Single/DPC=Dual/DS=Dual Switch)
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Simple : Texte à l'état électrique = 1 Double : Texte à l'état électrique = 10 (16 car) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Sencilla : Texto en estado eléctrico = 1 Dual : Texto en estado eléctrico = 10 (16 caract) | Simples: Texto em estado Elétrico = 1 Duplo : Texto em estado Elétrico = 10 (16 caract) | Одиночный : Обозначение электрического состояния = 1 Двойной : Обозначение электрического состояния = 10 (16 символов) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char)
Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Simple : Texte à l'état électrique = 0 Double : Texte à l'état électrique =01 (16 car) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Sencilla : Texto en estado eléctrico = 0 Dual : Texto en estado eléctrico = 01 (16 caract) | Simples: Texto em estado Elétrico = 0 Duplo : Texto em estado Elétrico = 01 (16 caract) | Одиночный : Обозначение электрического состояния = 0 Двойной : Обозначение электрического состояния = 01 (16 символов) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char)
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
LCD Control | Contrôle LCD | LCD Control | Control LCD | Ordem desde LCD | Управление LCD | LCD Control
HMI Control | Contrôle HMI | HMI Control | Control IHM | Ordem desde IHM | Управление HMI | HMI Control
Has a xPS Feedback | A un retour de position xPS | Has a xPS Feedback | Contiene retroalimentación xPS | Possui FeedBack xPS | имеет xPS отзывы | Has a xPS Feedback
Is activated by xPS | Est activé par xPS | Is activated by xPS | Es activado por xPS | É ativado por xPS | Активируется с помощью xPS | Is activated by xPS
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Relay | Relais | Relay | Relé | Relé | Реле | Relay
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
ANALOG INPUT BOARD AIU21x | Carte d'entrées analogiques AIU21x | ANALOG INPUT BOARD AIU21x | TARJETAS DE ENTRADAS ANALOGICAS AIU21x | Etiquetas de Entradas Analógicas AIU21x | ПЛАТЫ AIU21x | ANALOGE EINGANGSKARTE AIU21x
ANALOG INPUT BOARD AIU20x | Carte d'entrées analogiques AIU20x | ANALOG INPUT BOARD AIU20x | TARJETAS DE ENTRADAS ANALOGICAS AIU20x | Etiquetas de Entradas Analógicas AIU20x | ПЛАТЫ AIU20x | ANALOGE EINGANGSKARTE AIU20x
Analog Input Board Number | Numéro de la carte d'entrées analogiques | Analog Input Board Number | Número de tarjeta de entradas analógicas | Número de Etiqueta de Entradas Analógicas | Номер платы AI | Analogeingangskarten Nummer
Analog Input Board Slot | Position de la carte d'entrées analogiques | Analog Input Board Slot | Slot de Tarjeta de entradas analógicas | Slot do Cartão de Entradas Analógicas | Слот платы AI | Analogeingangskarten Steckplatz
Analog Input Extension Rack Number | Numéro rack d'extension de la carte d'entrées analogiques | Analog Input Extension Rack Number | Tarjeta de entradas analógicas Extensión Rack Número | Etiqueta de Entradas Analógicas Extensão Rack Número | продлению стойки Количество AI | Analogeingangskarten Extension Rack Nummer
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
AI Reference | Référence AI | AI Reference | Referencia AI | Referência AI | Ссылка AI | AI Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Local Display | Affichage Local | Local Display | Despliegue Local | Display Local | Локальный дисплей | Local Display
HMI | HMI | HMI | IHM | IHM | HMI | HMI
Special | Spécial | Special | Especial | Especial | Специальный | Special
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Link | Lien | Link | Vínculo | Vínculo | Связь | Link
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
Channel | Voie | Channel | Canal | Canal | Канал | Channel
Transducer Type | Type de Transducteur | Transducer Type | Tipo de transductor | Tipo de Transdutor | Тип преобразователя | Transducer Type
Function | Fonction | Function | Función | Função | Функция | Function
Unit | Unité | Unit | Unidad | Unidade | Плата | Unit
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Corresponding AI Value at Transducer minimum | Correspond à la valeur AI minimum du transducteur | Corresponding AI Value at Transducer minimum | Valor AI correspondiente al mínimo del transductor | Valor AI correspondente ao Mínimo do Transdutor | Значение AI, соответствующее минимуму преобразователя | Corresponding AI Value at Transducer minimum
Corresponding AI Value at Transducer Maximum | Correspond à la valeur AI maximum du transducteur | Corresponding AI Value at Transducer Maximum | Valor AI correspondiente al Máximo del transductor | Valor AI correspondente ao Máximo do Transdutor | Значение AI, соответствующее максимуму преобразователя | Corresponding AI Value at Transducer Maximum
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
LCD Display | Affichage LCD | LCD Display | Pantalla LCD | Vista LCD | LCD Дисплей | LCD Display
HMI Display | Affichage HMI | HMI Display | Pantalla IHM | Vista IHM | HMI Дисплей | HMI Display
Trend Viewer | Archivé | Trend Viewer | Archivado | Arquivado | Просмотр кривых | Trend Viewer
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Integrated by COUNTER | Intégré par le Compteur | Integrated by COUNTER | Integrated by COUNTER | Integrated by COUNTER | Integrated by COUNTER | Integrated by COUNTER
Is used by distributed Automation (GOOSE) | Est utilisé par la distribution automatique (GOOSE) | Is used by distributed Automation (GOOSE) | Se utiliza por automatización distribuida (GOOSE) | Se utiliza por Automação distribuida (GOOSE) | Используется распределенной автоматикой (GOOSE) | Is used by distributed Automation (GOOSE)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
CT/VT ANALOG INPUT BOARD TMU2x0 | Module Analogique CT/VT TMU2x0 | CT/VT ANALOG INPUT BOARD TMU2x0 | CT/VT TARJETAS DE ENTRADAS ANALOGICAS TMU2x0 | CT/VT Etiquetas de Entradas Analógicas TMU2x0 | ПЛАТЫ АНАЛОГОВЫЙ ВХОД CT/VT TMU2x0 | CT/VT ANALOGE EINGANGSKARTE TMU2x0
CT/VT Board Number | Numéro du module CT/VT | CT/VT Board Number | CT/VT Número de tarjeta | Número do Cartão CT/VT | Номер платы CT/VT | CT/VT Karte Nummer
CT/VT Board Slot | Position du module CT/VT | CT/VT Board Slot | CT/VT Slot de Tarjeta | CT/VT Slot do Cartão | Слот платы CT/VT | CT/VT Karte Steckplatz
CT acquisition | Acquisition TC | CT acquisition | CT adquisición | CT aquisição | Снятие значения тока | CT acquisition
VT acquisition | Acquisition TT | VT acquisition | VT adquisición | VT aquisição | Снятие значения напряжения | VT acquisition
Nominal Current | Courant Nominal | Nominal Current | Corriente nominal | Corrente Nominal | Номинальный ток | Nennstrom
(1A/5A) | (1A/5A) | (1A/5A) | (1A/5A) | (1A/5A) | (1A/5A) | (1A/5A)
Nominal Voltage | Tension Nominale | Nominal Voltage | Voltaje nominal | Tensão Nominal | Номинальное напряжение | Nennspannung
[1V … 500V] | [1V … 500V] | [1V … 500V] | [1V … 500V] | [1V … 500V] | [1V … 250V] | [1V … 500V]
CT/VT Board Model | Modèle de carte CT/VT | CT/VT Board Model | CT/VT Modelo de Tarjeta | CT/VT Modo do Cartão | CT/VT борту модели | CT/VT Board Model
CT/VT Extension Rack Number | Numéro rack d'extension de la carte CT/VT | CT/VT Extension Rack Number | CT/VT Extensión Rack Número | CT/VT Extensão Rack Número | продлению стойки Количество CT/VT | CT/VT Extension Rack Nummer
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
AI Reference | Référence AI | AI Reference | Referencia AI | Referência AI | Ссылка AI | AI Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Local Display | Affichage Local | Local Display | Despliegue Local | Display Local | Локальный дисплей | Local Display
HMI | HMI | HMI | IHM | IHM | HMI | HMI
Special | Spécial | Special | Especial | Especial | Специальный | Special
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Link | Lien | Link | Vínculo | Vínculo | Связь | Link
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
Input type (U/I) | Type d'entrée (U/I) | Input type (U/I) | Tipo de entrada (U/I) | Tipo de Entrada (U/I) | Тип входа (U/I) | Input type (U/I)
Function | Fonction | Function | Función | Função | Функция | Function
Unit | Unité | Unit | Unidad | Unidade | Плата | Unit
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Corresponding AI Value at minimum | Correspond à la valeur AI minimum | Corresponding AI Value at minimum | Valor AI correspondiente al mínimo | Valor AI correspondente ao Mínimo | Значение AI, соответствующее минимуму | Corresponding AI Value at minimum
Corresponding AI Value at Maximum | Correspond à la valeur AI maximum | Corresponding AI Value at Maximum | Valor AI correspondiente al Máximo | Valor AI correspondente ao Máximo | Значение AI, соответствующее максимуму | Corresponding AI Value at Maximum
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
LCD Display | Affichage LCD | LCD Display | Pantalla LCD | Vista LCD | LCD Дисплей | LCD Display
HMI Display | Affichage HMI | HMI Display | Pantalla IHM | Vista IHM | HMI Дисплей | HMI Display
Trend Viewer | Archivé | Trend Viewer | Archivado | Arquivado | Просмотр кривых | Trend Viewer
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Integrated by COUNTER | Intégré par le Compteur | Integrated by COUNTER | Integrated by COUNTER | Integrated by COUNTER | Integrated by COUNTER | Integrated by COUNTER
Is used by distributed Automation (GOOSE) | Est utilisé par la distribution automatique (GOOSE) | Is used by distributed Automation (GOOSE) | Se utiliza por automatización distribuida (GOOSE) | Se utiliza por Automação distribuida (GOOSE) | Используется распределенной автоматикой (GOOSE) | Is used by distributed Automation (GOOSE)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
IED NAME : | NOM DE l'IED : | IED NAME : | NOMBRE DE IED : | Nome do IED : | ИМЯ IED : | IED NAME :
DIGITAL INFORMATION FROM IED | ENTREES NUMERIQUES DE l'IED | DIGITAL INFORMATION FROM IED | INFORMACION DIGITAL DESDE IED | Informação Digital deste IED | ЦИФРОВАЯ ИНФОРМАЦИЯ С IED | DIGITALE INFORMATIONEN VON IED
IED name | NOM DE l'IED | IED name | NOMBRE DE IED | Nome do IED | Имя IED | IED name
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
IED DI Reference | Référence de la carte d'entrée numérique de l'IED | IED DI Reference | DI Referencia IED | DI Referência IED | IED DI ссылка | IED DI Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels / States | Libellés/Etats | Labels / States | Etiquetas/Estados | Etiquetas/Estados | Метки / Состояния | Labels / States
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Groups | Groupes | Groups | Grupos | Grupos | Группы | Gruppen
Local Display | Affichage Local | Local Display | Despliegue Local | Display Local | Локальный дисплей | Local Display
HMI | HMI | HMI | IHM | IHM | HMI | HMI
DI/DO Link | Lien DI/DO | DI/DO Link | DI/DO Vínculo | DI/DO Vínculo | DI/DO связи | DI/DO Link
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Information Adresse T103: ASDU nb;Fonction type MODBUS: Mapping Adresse;Bit nb DNP3: Adresse IEC: LD;LN T10X MASTER: Information Address | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Dirección de información T103: ASDU no;Tipo de función MODBUS: Dirección de mapeo;Bit no. DNP3: Dirección IEC: LD;LN T10X MASTER: Information Address | T101: Endereço de Informação T103: ASDU no;Tipo de Função MODBUS: Endereço de Mapeamento;Bit no. DNP3: Endereço IEC: LD;LN T10X MASTER: Information Address | T101: адрес информации T103: Номер ASDU ;Тип функции MODBUS: Адрес сигнала;Номер бита DNP3: Адрес IEC: LD;LN T10X MASTER: Information Address | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address
T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101:Adresse Commune ASDU;;Mode de détection T103: Information nb;Adresse CommuneASDU;Mode de détection MODBUS: Fonction;;Mode de détection DNP3: ;;Mode de détection IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Dirección común ASDU;;DetectMode T103: No. de información;Dirección común ASDU;DetectMode MODBUS: Función;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Endereço comum ASDU;;DetectMode T103: No. de Informação;Endereço comum ASDU;DetectMode MODBUS: Função;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Общий адрес ASDU;;DetectMode T103: информационный номер;Общий адрес ASDU;DetectMode MODBUS: Функция;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Common address ASDU;;DetectMode T103: Information nb;Common address ASDU;DetectMode MODBUS: Function;;DetectMode DNP3: ;;DetectMode IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type
Function | Fonction | Function | Función | Função | Функция | Function
Type (SPS=Single/DPS=Dual/MPS=Multiple) | Type (SPS=Simple/DPS=Double/MPS=Multiple) | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Tipo (SPS=Sencilla/DPS=Dual/MPS=Multiple) | Tipo (SPS=Simples/DPS=Duplo/MPS=Múltiplo) | Тип (SPS=Single/DPS=Dual/MPS=Multiple) | Type (SPS=Single/DPS=Dual/MPS=Multiple)
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Simple : Texte à l'état électrique = 1 Double : Texte à l'état électrique = 10 Multiple : label d'état (16 car) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Sencilla : Texto en estado eléctrico = 1 Dual : Texto en estado eléctrico = 10 Multiple : Texto (16 caract) | Simples: Texto em estado Elétrico = 1 Duplo : Texto em estado Elétrico = 10 Múltiplo : Texto (16 caract) | Одиночный : Обозначение электрического состояния = 1 Двойной : Обозначение электрического состояния = 10 Множественный: Обозначение (16 символов) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char)
Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Simple : Texte à l'état électrique = 0 Double : Texte à l'état électrique = 01 Multiple : Numéro d'état (16 car) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Sencilla : Texto en estado eléctrico = 0 Dual : Texto en estado eléctrico = 01 Multiple : Número de estado (16 caract) | Simples: Texto em estado Elétrico = 0 Duplo : Texto em estado Elétrico = 01 Múltiplo : Número de estado (16 caract) | Одиночный : Обозначение электрического состояния = 0 Двойной : Обозначение электрического состояния = 01 Множественный : Состояние Number (16 символов) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char)
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
Computers Groups (separator ";") | Groupes de calculateur (séparateur ";") | Computers Groups (separator ";") | Grupos de Computadoras (separador ";") | Grupos de Computadores (separador ";") | Группы контроллеров (разделитель ";") | Computers Gruppen (separator ";")
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
LED | LED | LED | LED | LED | индикатор | LED
LCD Display | Affichage LCD | LCD Display | Pantalla LCD | Vista LCD | LCD Дисплей | LCD Display
HMI Display | Affichage HMI | HMI Display | Pantalla IHM | Vista IHM | HMI Дисплей | HMI Display
Is a xPC Feedback | Est un retour de position xPC | Is a xPC Feedback | Es una xPC de retroalimentación | É FeedBack de xPC | Присутствует xPC обратная связь | Is a xPC Feedback
Acts on xPC | Acté sur xPC | Acts on xPC | Actúa en xPC | Atua em xPC | Действует на с xPC | Acts on xPC
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Is used by distributed Automation (GOOSE) | Est utilisé par la distribution automatique (GOOSE) | Is used by distributed Automation (GOOSE) | Se utiliza por automatización distribuida (GOOSE) | Se utiliza por Automação distribuida (GOOSE) | Используется распределенной автоматикой (GOOSE) | Is used by distributed Automation (GOOSE)
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
DIGITAL INFORMATION TO IED | SORTIES NUMERIQUES DE l'IED | DIGITAL INFORMATION TO IED | INFORMACION DIGITAL HACIA IED | Informação Digital Ajuste do IED | ЦИФРОВАЯ ИНФОРМАЦИЯ К IED | DIGITALE INFORMATIONEN AN IED
IED name | NOM DE l'IED | IED name | NOMBRE DE IED | Nome do IED | Имя IED | IED name
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
IED DO Reference | Référence de la carte de sortie numérique de l'IED | IED DO Reference | IED Referencia DO | IED Referência DO | IED DO ссылка | IED DO Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Local Control | Contrôle Local | Local Control | Control Local | Controle Local | местного контроля | Local Control
HMI | HMI | HMI | IHM | IHM | HMI | HMI
DI/DO Link | Lien DI/DO | DI/DO Link | DI/DO Vínculo | DI/DO Vínculo | DI/DO связи | DI/DO Link
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Information Adresse T103: ASDU nb;Fonction type MODBUS: Mapping Adresse;Bit nb DNP3: Adresse IEC: LD;LN T10X MASTER: Information Address | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Dirección de información T103: ASDU no;Tipo de función MODBUS: Dirección de mapeo;Bit no. DNP3: Dirección IEC: LD;LN T10X MASTER: Information Address | T101: Endereço de Informação T103: ASDU no;Tipo de Função MODBUS: Endereço de Mapeamento;Bit no. DNP3: Endereço IEC: LD;LN T10X MASTER: Information Address | T101: адрес информации T103: Номер ASDU ;Тип функции MODBUS: Адрес сигнала;Номер бита DNP3: Адрес IEC: LD;LN T10X MASTER: Information Address | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;Bit nb DNP3: Address IEC: LD;LN T10X MASTER: Information Address
T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101:Adresse Commune ASDU;;Type d'Ordre T103: Information nb;Adresse Commune ASDU;Type d'Ordre MODBUS: Fonction;;Type d'Ordre DNP3: ;;Type d'Ordre IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Dirección común ASDU;;OrderType T103: No. de información;Dirección común ASDU;OrderType MODBUS: Función;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Endereço comum ASDU;;OrderType T103: No. de Informação;Endereço comum ASDU;OrderType MODBUS: Função;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Общий адрес ASDU;;OrderType T103: информационный номер;Общий адрес ASDU;OrderType MODBUS: Функция;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type
Function | Fonction | Function | Función | Função | Функция | Function
Type (SPC=Single/DPC=Dual) | Type (SPC=Simple/DPC=Double) | Type (SPC=Single/DPC=Dual) | Tipo (SPC=Sencilla/DPC=Dual) | Tipo (SPC=Simples/DPC=Duplo) | Тип (SPC=Single/DPC=Dual) | Type (SPC=Single/DPC=Dual)
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Simple : Texte à l'état électrique = 1 Double : Texte à l'état électrique = 10 (16 car) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Sencilla : Texto en estado eléctrico = 1 Dual : Texto en estado eléctrico = 10 (16 caract) | Simples: Texto em estado Elétrico = 1 Duplo : Texto em estado Elétrico = 10 (16 caract) | Одиночный : Обозначение электрического состояния = 1 Двойной : Обозначение электрического состояния = 10 (16 символов) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char)
Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Simple : Texte à l'état électrique = 0 Double : Texte à l'état électrique =01 (16 car) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Sencilla : Texto en estado eléctrico = 0 Dual : Texto en estado eléctrico = 01 (16 caract) | Simples: Texto em estado Elétrico = 0 Duplo : Texto em estado Elétrico = 01 (16 caract) | Одиночный : Обозначение электрического состояния = 0 Двойной : Обозначение электрического состояния = 01 (16 символов) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char)
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
LCD Control | Contrôle LCD | LCD Control | Control LCD | Ordem desde LCD | Управление LCD | LCD Control
HMI Control | Contrôle HMI | HMI Control | Control IHM | Ordem desde IHM | Управление HMI | HMI Control
Has a xPS Feedback | A un retour de position xPS | Has a xPS Feedback | Contiene retroalimentación xPS | Possui FeedBack xPS | имеет xPS отзывы | Has a xPS Feedback
Is activated by xPS | Est activé par xPS | Is activated by xPS | Es activado por xPS | É ativado por xPS | Активируется с помощью xPS | Is activated by xPS
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
ANALOG INFORMATION FROM IED | ENTREES ANALOGIQUES DE l'IED | ANALOG INFORMATION FROM IED | INFORMACION ANALOGICA DESDE IED | Informação Analógica deste IED | АНАЛОГОВАЯ ИНФОРМАЦИЯ С IED | ANALOGINFORMATIONEN VON IED
IED name | NOM DE l'IED | IED name | NOMBRE DE IED | Nome do IED | Имя IED | IED name
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
IED AI Reference | Référence de la carte d'entrée analogique de l'IED | IED AI Reference | Referencia AI IED | Referência AI IED | IED AI ссылка | IED AI Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Local Display | Affichage Local | Local Display | Despliegue Local | Display Local | Локальный дисплей | Local Display
HMI | HMI | HMI | IHM | IHM | HMI | HMI
Special | Spécial | Special | Especial | Especial | Специальный | Special
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Link | Lien | Link | Vínculo | Vínculo | Связь | Link
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Information Adresse T103: ASDU nb;Fonction type; Unité de la MV MODBUS: Mapping Adresse;Format de la donnée DNP3: Adresse IEC: LD;LN T10X MASTER: Information Address | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Dirección de información T103: ASDU no;Tipo de función;Unidad de MV MODBUS: Dirección de mapeo;Format de Dado DNP3: Dirección IEC: LD;LN T10X MASTER: Information Address | T101: Endereço de Informação T103: ASDU no;Tipo de Função;Unidade do MV MODBUS: Endereço de Mapeamento;Format de Dado DNP3: Endereço IEC: LD;LN T10X MASTER: Information Address | T101: адрес информации T103: Номер ASDU ;Тип функции;Unit ofr the MV MODBUS: Адрес сигнала;DataFormat DNP3: Адрес IEC: LD;LN T10X MASTER: Information Address | T101: Information Address T103: ASDU nb;Function type;Unit of the MEAS MODBUS: Mapping address;Data Format DNP3: Address IEC: LD;LN T10X MASTER: Information Address
T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101:Adresse Commune ASDU T103: Information nb;Adresse Commune ASDU; index dans l'ASDU MODBUS: Fonction DNP3: Non utilisé IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Dirección común ASDU T103: No. de información;Dirección común ASDU;Indice in ASDU MODBUS: Función DNP3: No utilizado IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Endereço comum ASDU T103: No. de Informação;Endereço comum ASDU;Indice in ASDU MODBUS: Função DNP3: Não Utilizado IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Общий адрес ASDU T103: информационный номер;Общий адрес ASDU;Index in ASDU MODBUS: Функция DNP3: Не используется IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Common address ASDU T103: Information nb;Common address ASDU;Index in ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type
Function | Fonction | Function | Función | Função | Функция | Function
Unit | Unité | Unit | Unidad | Unidade | Плата | Unit
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Corresponding AI Value at minimum | Correspond à la valeur AI minimum | Corresponding AI Value at minimum | Valor AI correspondiente al mínimo | Valor AI correspondente ao Mínimo | Значение AI, соответствующее минимуму | Corresponding AI Value at minimum
Corresponding AI Value at Maximum | Correspond à la valeur AI maximum | Corresponding AI Value at Maximum | Valor AI correspondiente al Máximo | Valor AI correspondente ao Máximo | Значение AI, соответствующее максимуму | Corresponding AI Value at Maximum
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
LCD Display | Affichage LCD | LCD Display | Pantalla LCD | Vista LCD | LCD Дисплей | LCD Display
HMI Display | Affichage HMI | HMI Display | Pantalla IHM | Vista IHM | HMI Дисплей | HMI Display
Trend Viewer | Archivé | Trend Viewer | Archivado | Arquivado | Просмотр кривых | Trend Viewer
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Integrated by COUNTER | Intégré par le Compteur | Integrated by COUNTER | Integrated by COUNTER | Integrated by COUNTER | Integrated by COUNTER | Integrated by COUNTER
Is used by distributed Automation (GOOSE) | Est utilisé par la distribution automatique (GOOSE) | Is used by distributed Automation (GOOSE) | Se utiliza por automatización distribuida (GOOSE) | Se utiliza por Automação distribuida (GOOSE) | Используется распределенной автоматикой (GOOSE) | Is used by distributed Automation (GOOSE)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
ANALOG INFORMATION TO IED | SORTIES ANALOGIQUES DE l'IED | ANALOG INFORMATION TO IED | INFORMACION ANALOGICA HACIA IED | Informação Analógica Ajuste do IED | АНАЛОГОВАЯ ИНФОРМАЦИЯ К IED | ANALOGINFORMATIONEN AN IED
IED name | NOM DE l'IED | IED name | NOMBRE DE IED | Nome do IED | Имя IED | IED name
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
IED AI Reference | Référence de la carte d'entrée analogique de l'IED | IED AI Reference | Referencia AI IED | Referência AI IED | IED AI ссылка | IED AI Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Local Display | Affichage Local | Local Display | Despliegue Local | Display Local | Локальный дисплей | Local Display
HMI | HMI | HMI | IHM | IHM | HMI | HMI
Special | Spécial | Special | Especial | Especial | Специальный | Special
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Information Adresse;Format de Sortie T103: ASDU nb;Fonction type;Format de Sortie MODBUS: Mapping Adresse DNP3: Adresse IEC: LD;LN T10X MASTER: Information Address | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Dirección de información;Output Format T103: ASDU no;Tipo de función;Output Format MODBUS: Dirección de mapeo DNP3: Dirección IEC: LD;LN T10X MASTER: Information Address | T101: Endereço de Informação;Output Format T103: ASDU no;Tipo de Função;Output Format MODBUS: Endereço de Mapeamento DNP3: Endereço IEC: LD;LN T10X MASTER: Information Address | T101: адрес информации;Output Format T103: Номер ASDU ;Тип функции;Output Format MODBUS: Адрес сигнала DNP3: Адрес IEC: LD;LN T10X MASTER: Information Address | T101: Information Address;Output Format T103: ASDU nb;Function type;Output Format MODBUS: Mapping address DNP3: Address IEC: LD;LN T10X MASTER: Information Address
T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101:Adresse Commune ASDU;;Type d'Ordre T103: Information nb;Adresse Commune ASDU;Type d'Ordre MODBUS: Fonction;;Type d'Ordre DNP3: ;;Type d'Ordre IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Dirección común ASDU;;OrderType T103: No. de información;Dirección común ASDU;OrderType MODBUS: Función;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Endereço comum ASDU;;OrderType T103: No. de Informação;Endereço comum ASDU;OrderType MODBUS: Função;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Общий адрес ASDU;;OrderType T103: информационный номер;Общий адрес ASDU;OrderType MODBUS: Функция;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Common address ASDU;;OrderType T103: Information nb;Common address ASDU;OrderType MODBUS: Function;;OrderType DNP3: ;;OrderType IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type
Function | Fonction | Function | Función | Função | Функция | Function
Unit | Unité | Unit | Unidad | Unidade | Плата | Unit
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Corresponding AI Value at minimum | Correspond à la valeur AI minimum | Corresponding AI Value at minimum | Valor AI correspondiente al mínimo | Valor AI correspondente ao Mínimo | Значение AI, соответствующее минимуму | Corresponding AI Value at minimum
Corresponding AI Value at Maximum | Correspond à la valeur AI maximum | Corresponding AI Value at Maximum | Valor AI correspondiente al Máximo | Valor AI correspondente ao Máximo | Значение AI, соответствующее максимуму | Corresponding AI Value at Maximum
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
LCD Display | Affichage LCD | LCD Display | Pantalla LCD | Vista LCD | LCD Дисплей | LCD Display
HMI Display | Affichage HMI | HMI Display | Pantalla IHM | Vista IHM | HMI Дисплей | HMI Display
Trend Viewer | Archivé | Trend Viewer | Archivado | Arquivado | Просмотр кривых | Trend Viewer
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
END OF IED DATA | FIN DES DONNEES DE l'IED | END OF IED DATA | FIN DE DATOS IED | FIM DOS DADOS IED | КОНЕЦ ДАННЫХ ПО IED | END OF IED DATA
DI GROUPS | GROUPES ENTREES NUMERIQUES | DI GROUPS | Grupos DI | Grupos DI | Группы DI | DI GROUPS
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
Group DI Reference | Référence du Groupes des DI | Group DI Reference | Referencia de grupo DI | Referência de grupo DI | Группа DI ссылку | Gruppe DI Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Groups | Groupes | Groups | Grupos | Grupos | Группы | Gruppen
Local Display | Affichage Local | Local Display | Despliegue Local | Display Local | Локальный дисплей | Local Display
HMI | HMI | HMI | IHM | IHM | HMI | HMI
DI/DO Link | Lien DI/DO | DI/DO Link | DI/DO Vínculo | DI/DO Vínculo | DI/DO связи | DI/DO Link
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
Number | Numéro | Number | Número | Número | Номер | Number
Group Operator | Opérateur du Groupe | Group Operator | Operador de grupo | Operador de grupo | Группа оператора | Gruppe Operator
Function | Fonction | Function | Función | Função | Функция | Function
Type (S=Single) | Type (S=Simple) | Type (S=Single) | Tipo (S=Sencilla) | Tipo (S=Simples) | Тип (S=Single) | Type (S=Single)
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Single : Text at electrical state = 1 (16 char) | Simple : Texte à l'état électrique = 1 (16 car) | Single : Text at electrical state = 1 (16 char) | Sencilla : Texto en estado eléctrico = 1 (16 caract) | Simples: Texto em estado Elétrico = 1 (16 caract) | Одиночный : Обозначение электрического состояния = 1 (16 символов) | Single : Text at electrical state = 1 (16 char)
Single : Text at electrical state = 0 (16 char) | Simple : Texte à l'état électrique = 0 (16 car) | Single : Text at electrical state = 0 (16 char) | Sencilla : Texto en estado eléctrico = 0 (16 caract) | Simples: Texto em estado Elétrico = 0 (16 caract) | Одиночный : Обозначение электрического состояния = 0 (16 символов) | Single : Text at electrical state = 0 (16 char)
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
Computers Groups (separator ";") | Groupes de calculateur (séparateur ";") | Computers Groups (separator ";") | Grupos de Computadoras (separador ";") | Grupos de Computadores (separador ";") | Группы контроллеров (разделитель ";") | Computers Gruppen (separator ";")
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
LED | LED | LED | LED | LED | индикатор | LED
LCD Display | Affichage LCD | LCD Display | Pantalla LCD | Vista LCD | LCD Дисплей | LCD Display
HMI Display | Affichage HMI | HMI Display | Pantalla IHM | Vista IHM | HMI Дисплей | HMI Display
Is a xPC Feedback | Est un retour de position xPC | Is a xPC Feedback | Es una xPC de retroalimentación | É FeedBack de xPC | Присутствует xPC обратная связь | Is a xPC Feedback
Acts on xPC | Acté sur xPC | Acts on xPC | Actúa en xPC | Atua em xPC | Действует на с xPC | Acts on xPC
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Is used by distributed Automation (GOOSE) | Est utilisé par la distribution automatique (GOOSE) | Is used by distributed Automation (GOOSE) | Se utiliza por automatización distribuida (GOOSE) | Se utiliza por Automação distribuida (GOOSE) | Используется распределенной автоматикой (GOOSE) | Is used by distributed Automation (GOOSE)
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
SELF GENERATED DIGITAL INFORMATION | ENTREES NUMERIQUES AUTOMATIQUES | SELF GENERATED DIGITAL INFORMATION | INFORMACION DIGITAL AUTO GENERADA | Informação Digital Auto Gerada | ЦИФРОВАЯ ИНФОРМАЦИЯ, СГЕНЕРИРОВАННАЯ | SELBSTGENERIERTE DIGITALE INFORMATIONEN
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
Self DI Reference | Référence interne DI | Self DI Reference | Referencia DI auto | Referência DI Auto | Собственная ссылка DI | Self DI Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels / States | Libellés/Etats | Labels / States | Etiquetas/Estados | Etiquetas/Estados | Метки / Состояния | Labels / States
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Groups | Groupes | Groups | Grupos | Grupos | Группы | Gruppen
Local Display | Affichage Local | Local Display | Despliegue Local | Display Local | Локальный дисплей | Local Display
HMI | HMI | HMI | IHM | IHM | HMI | HMI
DI/DO Link | Lien DI/DO | DI/DO Link | DI/DO Vínculo | DI/DO Vínculo | DI/DO связи | DI/DO Link
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
Number | Numéro | Number | Número | Número | Номер | Number
Function | Fonction | Function | Función | Função | Функция | Function
Type (SPS=Single/DPS=Dual/MPS=Multiple) | Type (SPS=Simple/DPS=Double/MPS=Multiple) | Type (SPS=Single/DPS=Dual/MPS=Multiple) | Tipo (SPS=Sencilla/DPS=Dual/MPS=Multiple) | Tipo (SPS=Simples/DPS=Duplo/MPS=Múltiplo) | Тип (SPS=Single/DPS=Dual/MPS=Multiple) | Type (SPS=Single/DPS=Dual/MPS=Multiple)
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Simple : Texte à l'état électrique = 1 Double : Texte à l'état électrique = 10 Multiple : label d'état (16 car) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char) | Sencilla : Texto en estado eléctrico = 1 Dual : Texto en estado eléctrico = 10 Multiple : Texto (16 caract) | Simples: Texto em estado Elétrico = 1 Duplo : Texto em estado Elétrico = 10 Múltiplo : Texto (16 caract) | Одиночный : Обозначение электрического состояния = 1 Двойной : Обозначение электрического состояния = 10 Множественный: Обозначение (16 символов) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Text label (16 char)
Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Simple : Texte à l'état électrique = 0 Double : Texte à l'état électrique = 01 Multiple : Numéro d'état (16 car) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char) | Sencilla : Texto en estado eléctrico = 0 Dual : Texto en estado eléctrico = 01 Multiple : Número de estado (16 caract) | Simples: Texto em estado Elétrico = 0 Duplo : Texto em estado Elétrico = 01 Múltiplo : Número de estado (16 caract) | Одиночный : Обозначение электрического состояния = 0 Двойной : Обозначение электрического состояния = 01 Множественный : Состояние Number (16 символов) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : State Number (16 char)
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
Computers Groups (separator ";") | Groupes de calculateur (séparateur ";") | Computers Groups (separator ";") | Grupos de Computadoras (separador ";") | Grupos de Computadores (separador ";") | Группы контроллеров (разделитель ";") | Computers Gruppen (separator ";")
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
LED | LED | LED | LED | LED | индикатор | LED
LCD Display | Affichage LCD | LCD Display | Pantalla LCD | Vista LCD | LCD Дисплей | LCD Display
HMI Display | Affichage HMI | HMI Display | Pantalla IHM | Vista IHM | HMI Дисплей | HMI Display
Is a xPC Feedback | Est un retour de position xPC | Is a xPC Feedback | Es una xPC de retroalimentación | É FeedBack de xPC | Присутствует xPC обратная связь | Is a xPC Feedback
Acts on xPC | Acté sur xPC | Acts on xPC | Actúa en xPC | Atua em xPC | Действует на с xPC | Acts on xPC
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Is used by distributed Automation (GOOSE) | Est utilisé par la distribution automatique (GOOSE) | Is used by distributed Automation (GOOSE) | Se utiliza por automatización distribuida (GOOSE) | Se utiliza por Automação distribuida (GOOSE) | Используется распределенной автоматикой (GOOSE) | Is used by distributed Automation (GOOSE)
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Automation Origin (if any) | Automatisme d'origine (si existant) | Automation Origin (if any) | Automation Origin (if any) | Automation Origin (if any) | Automation Origin (if any) | Automation Origin (if any)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
SELF GENERATED DIGITAL OUTPUT INFORMATION | SORTIES NUMERIQUES AUTOMATIQUES | SELF GENERATED DIGITAL OUTPUT INFORMATION | INFORMACION DE SALIDAS DIGITALES AUTO GENERADAS | Informação de saidas Digitais Auto Geradas | ИНФОРМАЦИЯ, СГЕНЕРИРОВАННАЯ ЦИФРОВЫМИ ВЫХОДАМИ | SELBSTGENERIERTE DIGITALE AUSGANGSINFORMATIONEN
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
Self DO Reference | Référence interne DO | Self DO Reference | Referencia DO Auto | Referência DO Auto | Собственная DO ссылка | Self DO Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Local Control | Contrôle Local | Local Control | Control Local | Controle Local | местного контроля | Local Control
HMI | HMI | HMI | IHM | IHM | HMI | HMI
DI/DO Link | Lien DI/DO | DI/DO Link | DI/DO Vínculo | DI/DO Vínculo | DI/DO связи | DI/DO Link
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
Number | Numéro | Number | Número | Número | Номер | Number
Function | Fonction | Function | Función | Função | Функция | Function
Type (SPC=Single/DPC=Dual) | Type (SPC=Simple/DPC=Double) | Type (SPC=Single/DPC=Dual) | Tipo (SPC=Sencilla/DPC=Dual) | Tipo (SPC=Simples/DPC=Duplo) | Тип (SPC=Single/DPC=Dual) | Type (SPC=Single/DPC=Dual)
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Simple : Texte à l'état électrique = 1 Double : Texte à l'état électrique = 10 (16 car) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Sencilla : Texto en estado eléctrico = 1 Dual : Texto en estado eléctrico = 10 (16 caract) | Simples: Texto em estado Elétrico = 1 Duplo : Texto em estado Elétrico = 10 (16 caract) | Одиночный : Обозначение электрического состояния = 1 Двойной : Обозначение электрического состояния = 10 (16 символов) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char)
Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Simple : Texte à l'état électrique = 0 Double : Texte à l'état électrique =01 (16 car) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Sencilla : Texto en estado eléctrico = 0 Dual : Texto en estado eléctrico = 01 (16 caract) | Simples: Texto em estado Elétrico = 0 Duplo : Texto em estado Elétrico = 01 (16 caract) | Одиночный : Обозначение электрического состояния = 0 Двойной : Обозначение электрического состояния = 01 (16 символов) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char)
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
LCD Control | Contrôle LCD | LCD Control | Control LCD | Ordem desde LCD | Управление LCD | LCD Control
HMI Control | Contrôle HMI | HMI Control | Control IHM | Ordem desde IHM | Управление HMI | HMI Control
Has a xPS Feedback | A un retour de position xPS | Has a xPS Feedback | Contiene retroalimentación xPS | Possui FeedBack xPS | имеет xPS отзывы | Has a xPS Feedback
Is activated by xPS | Est activé par xPS | Is activated by xPS | Es activado por xPS | É ativado por xPS | Активируется с помощью xPS | Is activated by xPS
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Relay | Relais | Relay | Relé | Relé | Реле | Relay
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Automation Origin (if any) | Automatisme d'origine (si existant) | Automation Origin (if any) | Automation Origin (if any) | Automation Origin (if any) | Automation Origin (if any) | Automation Origin (if any)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
SELF GENERATED ANALOG INFORMATION | ENTREES ANALOGIQUES AUTOMATIQUES | SELF GENERATED ANALOG INFORMATION | INFORMACION ANALOGICA AUTO GENERADA | Informação Analógica Auto Gerada | АНАЛОГОВАЯ ИНФОРМАЦИЯ, СГЕНЕРИРОВАННАЯ | SELBST GENERIERTE ANALOGINFORMATIONEN
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
Self AI Reference | Référence interne AI | Self AI Reference | Referencia AI auto | Referência AI Automática | Собственная ссылка AI | Self AI Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Local Display | Affichage Local | Local Display | Despliegue Local | Display Local | Локальный дисплей | Local Display
HMI | HMI | HMI | IHM | IHM | HMI | HMI
Special | Spécial | Special | Especial | Especial | Специальный | Special
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Link | Lien | Link | Vínculo | Vínculo | Связь | Link
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
Number | Numéro | Number | Número | Número | Номер | Number
Function | Fonction | Function | Función | Função | Функция | Function
Unit | Unité | Unit | Unidad | Unidade | Плата | Unit
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Corresponding AI Value at Transducer minimum | Correspond à la valeur AI minimum du transducteur | Corresponding AI Value at Transducer minimum | Valor AI correspondiente al mínimo del transductor | Valor AI correspondente ao Mínimo do Transdutor | Значение AI, соответствующее минимуму преобразователя | Corresponding AI Value at Transducer minimum
Corresponding AI Value at Transducer Maximum | Correspond à la valeur AI maximum du transducteur | Corresponding AI Value at Transducer Maximum | Valor AI correspondiente al Máximo del transductor | Valor AI correspondente ao Máximo do Transdutor | Значение AI, соответствующее максимуму преобразователя | Corresponding AI Value at Transducer Maximum
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
LCD Display | Affichage LCD | LCD Display | Pantalla LCD | Vista LCD | LCD Дисплей | LCD Display
HMI Display | Affichage HMI | HMI Display | Pantalla IHM | Vista IHM | HMI Дисплей | HMI Display
Trend Viewer | Archivé | Trend Viewer | Archivado | Arquivado | Просмотр кривых | Trend Viewer
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Integrated by COUNTER | Intégré par le Compteur | Integrated by COUNTER | Integrated by COUNTER | Integrated by COUNTER | Integrated by COUNTER | Integrated by COUNTER
Is used by distributed Automation (GOOSE) | Est utilisé par la distribution automatique (GOOSE) | Is used by distributed Automation (GOOSE) | Se utiliza por automatización distribuida (GOOSE) | Se utiliza por Automação distribuida (GOOSE) | Используется распределенной автоматикой (GOOSE) | Is used by distributed Automation (GOOSE)
Automation Origin (if any) | Automatisme d'origine (si existant) | Automation Origin (if any) | Automation Origin (if any) | Automation Origin (if any) | Automation Origin (if any) | Automation Origin (if any)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : C364_Template | SHEET : C364_Template | SHEET : C364_Template | SHEET : C364_Template | SHEET : C364_Template | SHEET : C364_Template | SHEET : C364_Template
MiCOM C364 DESCRIPTION | DESCRIPTION DU MiCOM C364 | MiCOM C364 DESCRIPTION | Descripción MiCOM C364 | Descrição MiCOM C364 | ОПИСАНИЕ MiCOM C364 | MiCOM C364 BESCHREIBUNG
DI GROUPS | GROUPES DES ENTREES NUMERIQUES | DI GROUPS | Grupos DI | Grupos DI | DI Группы | DI GROUPS
SELF GENERATED DIGITAL INFORMATION | ENTREES NUMERIQUES AUTOMATIQUES | SELF GENERATED DIGITAL INFORMATION | INFORMACION DIGITAL AUTO GENERADA | Informação Digital Auto Gerada | ЦИФРОВАЯ ИНФОРМАЦИЯ, СГЕНЕРИРОВАННАЯ | SELBSTGENERIERTE DIGITALE INFORMATIONEN
SELF GENERATED DIGITAL OUTPUT INFORMATION | SORTIES NUMERIQUES AUTOMATIQUES | SELF GENERATED DIGITAL OUTPUT INFORMATION | INFORMACION DE SALIDAS DIGITALES AUTO GENERADAS | Informação de saidas digitais Auto Geradas | ИНФОРМАЦИЯ, СГЕНЕРИРОВАННАЯ ЦИФРОВЫМИ ВЫХОДАМИ | SELBSTGENERIERTE DIGITALE AUSGANGS INFORMATIONEN
SELF GENERATED ANALOG INFORMATION | ENTREES ANALOGIQUES AUTOMATIQUES | SELF GENERATED ANALOG INFORMATION | INFORMACION ANALOGICA AUTO GENERADA | Informação Analógica Auto Gerada | АНАЛОГОВАЯ ИНФОРМАЦИЯ, СГЕНЕРИРОВАННАЯ | SELBSTGENERIERTE ANALOG INFORMATIONEN
SHEET : Substation data | SHEET : Données de la Soustation | SHEET : Substation data | SHEET : Datos de subestación | SHEET : Dados da Substação | SHEET : Данные подстанции | SHEET : Substation data
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
SUBSTATION DATA DESCRIPTION | DESCRIPTION DES DONNEES DE SOUS-STATION | SUBSTATION DATA DESCRIPTION | DESCRIPCION DE DATOS DE SUBESTACION | Descrição de Dados de Substação | ДАННЫЕ ОПИСАНИЯ ПОДСТАНЦИИ | SUBSTATION DATA DESCRIPTION
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
Substation Name | Nom de la Sous-station | Substation Name | Nombre de subestación | Nome do Substação | Имя подстанции | Stationsname:
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Control Uniqueness | Contrôle Uniquement | Control Uniqueness | Unequidad de control | Unicidade de Controle | Однозначность управления | Control Uniqueness
Substation | Sous-station | Substation | Subestación | Substação | Подстанция | Substation
No / Substation / Bay / Specific | Non / Sous-station / Tranche / Spécifique | No / Substation / Bay / Specific | No / Subestación / Bahía / Specifico | Não/ Substação / Painel / Específico | No / Substation / Bay / Specific | No / Substation / Bay / Specific
Auto generated | Génération automatique | Auto generated | Auto generado | Auto Geração | Автоматически сгенерировано | Auto generated
Site taking control | Emplacement prenant le contrôle | Site taking control | Toma de control de sitio | Controle de Sítio | Site taking control | Site taking control
SCADA & Local | SCADA & Local | SCADA & Local | SCADA & Local | SCADA & Local | SCADA & Local | SCADA & Local
SCADA / Local / SCADA & Local | SCADA / Local / SCADA & Local | SCADA / Local / SCADA & Local | SCADA / Local / SCADA & Local | SCADA / Local / SCADA & Local | SCADA / Local / SCADA & Local | SCADA / Local / SCADA & Local
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
Gateway | Passerelle | Gateway | UTR | UTR | Шлюз | Gateway
Port used (on gateway) | Ports utilisés (sur la passerelle) | Port used (on gateway) | Puerto utilizado (en UTR) | Porta utilizada (em UTR) | Используемый порт (на шлюз) | benutzter Port (Gateway)
SCADA 1 | SCADA 1 | SCADA 1 | SCADA 1 | SCADA 1 | SCADA 1 | SCADA 1
SCADA 2 | SCADA 2 | SCADA 2 | SCADA 2 | SCADA 2 | SCADA 2 | SCADA 2
SCADA 3 | SCADA 3 | SCADA 3 | SCADA 3 | SCADA 3 | SCADA 3 | SCADA 3
SCADA 4 | SCADA 4 | SCADA 4 | SCADA 4 | SCADA 4 | SCADA 4 | SCADA 4
Default Computer that manages Substation | Calculateur par défaut gérant la Sous-station | Default Computer that manages Substation | Equipo que gestiona Subestación | Computador que gerencia Subestação | компьютер, который управляет Подстанция | Computer verwaltet Substation
SUBSTATION DI GROUPS | GROUPES DES DI DE LA SOUS-STATION | SUBSTATION DI GROUPS | GRUPOS DI SUBSTATION | GRUPOS DE SUBSTAÇÃO | Группы DI подстанции | SUBSTATION DI GROUPS
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
Group DI Reference | Référence du Groupes des DI | Group DI Reference | Referencia de grupo DI | Referência de grupo DI | Группа DI ссылку | Gruppe DI Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Groups | Groupes | Groups | Grupos | Grupos | Группы | Gruppen
Local Display | Affichage Local | Local Display | Despliegue Local | Display Local | Локальный дисплей | Local Display
HMI | HMI | HMI | IHM | IHM | HMI | HMI
DI/DO Link | Lien DI/DO | DI/DO Link | DI/DO Vínculo | DI/DO Vínculo | DI/DO связи | DI/DO Link
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
Number | Numéro | Number | Número | Número | Номер | Number
Group Operator | Opérateur du Groupe | Group Operator | Operador de grupo | Operador de grupo | Группа оператора | Gruppe Operator
Function | Fonction | Function | Función | Função | Функция | Function
Type (S=Single) | Type (S=Simple) | Type (S=Single) | Tipo (S=Sencilla) | Tipo (S=Simples) | Тип (S=Single) | Type (S=Single)
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Single : Text at electrical state = 1 (16 char) | Simple : Texte à l'état électrique = 1 (16 car) | Single : Text at electrical state = 1 (16 char) | Sencilla : Texto en estado eléctrico = 1 (16 caract) | Simples: Texto em estado Elétrico = 1 (16 caract) | Одиночный : Обозначение электрического состояния = 1 (16 символов) | Single : Text at electrical state = 1 (16 char)
Single : Text at electrical state = 0 (16 char) | Simple : Texte à l'état électrique = 0 (16 car) | Single : Text at electrical state = 0 (16 char) | Sencilla : Texto en estado eléctrico = 0 (16 caract) | Simples: Texto em estado Elétrico = 0 (16 caract) | Одиночный : Обозначение электрического состояния = 0 (16 символов) | Single : Text at electrical state = 0 (16 char)
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
Managed by Computer | Géré par le Calcultateur | Managed by Computer | Manejado por la computadora | Controlado por Computador | управляет компьютер | Managed by Computer
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
LED | LED | LED | LED | LED | индикатор | LED
LCD Display | Affichage LCD | LCD Display | Pantalla LCD | Vista LCD | LCD Дисплей | LCD Display
HMI Display | Affichage HMI | HMI Display | Pantalla IHM | Vista IHM | HMI Дисплей | HMI Display
Is a xPC Feedback | Est un retour de position xPC | Is a xPC Feedback | Es una xPC de retroalimentación | É FeedBack de xPC | Присутствует xPC обратная связь | Is a xPC Feedback
Acts on xPC | Acté sur xPC | Acts on xPC | Actúa en xPC | Atua em xPC | Действует на с xPC | Acts on xPC
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Is used by distributed Automation (GOOSE) | Est utilisé par la distribution automatique (GOOSE) | Is used by distributed Automation (GOOSE) | Se utiliza por automatización distribuida (GOOSE) | Se utiliza por Automação distribuida (GOOSE) | Используется распределенной автоматикой (GOOSE) | Is used by distributed Automation (GOOSE)
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : Electric Functions | SHEET : Fonctions Electriques | SHEET : Electric Functions | SHEET : Funciones eléctricas | SHEET : FUNÇÕES ELÉTRICAS | SHEET : Функции электрической части | SHEET : Electric Functions
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
ELECTRICAL PROFILES | PROFILS ELECTRIQUES | ELECTRICAL PROFILES | PERFILES ELECTRICOS | Perfis Elétricos | ПРОФИЛИ ЭЛЕКТРИЧЕСКОЙ ЧАСТИ | ELECTRICAL PROFILES
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
Single Digital Inputs Profiles | Profils des entrées numériques simples (SPS) | Single Digital Inputs Profiles | Perfiles de entradas digitales sencillas | Perfis de Entradas Digitais Únicas | Профили одинарных DI | Single Digital Inputs Profiles
Single System Digital Inputs Profiles | Profils des entrées numériques systèmes simples (SPS) | Single System Digital Inputs Profiles | Pérfiles de sistema de entradas digitales sencillas | Perfis de Sistema de Entradas Digitais Únicas | Профили одинарных системных DI | Single System Digital Inputs Profiles
Function Name | Nom de la fonction | Function Name | Nombre de función | Nome da Função | Функция Name | Function Name
SCE Name (13 char) | Nom dans le SCE (13 char) | SCE Name (13 char) | Nombre SCE (13 caract) | Nome SCE (13 caract) | Имя SCE (13 символов) | SCE Name (13 char)
SPS General Parameters | Paramètres généraux de la SPS | SPS General Parameters | Parámetros generales SPS | Parâmetros Geração SPS | Основные параметры SPS | SPS General Parameters
Generation Condition | Condition de la Génération | Generation Condition | Condición de generación | Condição de Geração | Основное условие | Generation Condition
Audible Alarm | Alarme audible | Audible Alarm | Alarma audible | Alarme Auditível | Звуковая тревога | Audible Alarm
Fugitive Alarm (Spurious) | Alarme fugitive | Fugitive Alarm (Spurious) | Alarma fujitiva (Spurious) | Alarme de Fuga(Spurious) | Fugitive Alarm (Spurious) | Fugitive Alarm (Spurious)
State 1 confirmation delay (x100 ms) | Etat 1 confirmation du retard (x100 ms) | State 1 confirmation delay (x100 ms) | Confirmación de retardo Estado 1 (x100 ms) | Confirmação de retardo Estado 1 (x100 ms) | Состояние 1 задержка подтверждения (х100 мс) | State 1 confirmation delay (x100 ms)
State 1 Gravity level | Etat 1 niveau de gravité | State 1 Gravity level | Nivel de gravedad estado 1 | Nivel de gravidade estado 1 | Состояние 1 уровень сложности | State 1 Gravity level
State 0 confirmation delay (x100 ms) | Etat 0 confirmation du retard (x100 ms) | State 0 confirmation delay (x100 ms) | Confirmación de retardo Estado 0 (x100 ms) | Confirmação de retardo Estado 0 (x100 ms) | Состояние 0 задержка подтверждения (х100 мс) | State 0 confirmation delay (x100 ms)
State 0 Gravity level | Etat 0 niveau de gravité | State 0 Gravity level | Nivel de gravedad estado 0 | Nivel de gravidade estado 0 | Состояние 0 - уровень сложности | State 0 Gravity level
Alarm appearance delay (0-120 s) | Retard d'apparition de l'alarme (0-120 s) | Alarm appearance delay (0-120 s) | Retardo de aparición de Alarma (0-120 s) | Retardo de aparição de Alarme (0-120 s) | Задержка появления тревоги (0-120 с) | Alarm appearance delay (0-120 s)
Clearing Mode | Mode d'effacement | Clearing Mode | Modo Clearing | Modo de Limpeza | Режим очистки | Clearing Mode
SPS Printing Parameters | Paramètres d'impression de la SPS | SPS Printing Parameters | Parámetros de impresión SPS | Parâmetros de Impressão SPS | Параметры печати SPS | SPS Printing Parameters
Printed on Sequence Of Events SOE 1 : | Imprimer sur l'imprimante Fil de l'eau 1 : | Printed on Sequence Of Events SOE 1 : | Impreso en SOE 1 : | Impresso em SOE 1 : | Вывод на SOE 1 : | Printed on Sequence Of Events SOE 1 :
Printed on Sequence Of Events SOE 2 : | Imprimer sur l'imprimante Fil de l'eau 2 : | Printed on Sequence Of Events SOE 2 : | Impreso en SOE 2 : | Impresso em SOE 1 : | Вывод на SOE 2 : | Printed on Sequence Of Events SOE 2 :
Printed on Logbook LB 1 : | Imprimer sur l'imprimante Journal de Bord 1 : | Printed on Logbook LB 1 : | Impreso en LB 1 : | Impresso em LB 1 : | Вывод на LB 1 : | Printed on Logbook LB 1 :
Printed on Logbook LB 2 : | Imprimer sur l'imprimante Journal de Bord 2 : | Printed on Logbook LB 2 : | Impreso en LB 2 : | Impresso em LB 2 : | Вывод на LB 2 : | Printed on Logbook LB 2 :
SPS Interlocking Parameters | Paramètres d'Interverrouillage de la SPS | SPS Interlocking Parameters | Parámetros de enclavamientos SPS | Parâmetros de Intertravamento SPS | Параметры блокировки SPS | SPS Interlocking Parameters
Reset Interlock Value | Reset des valeurs de l'interverrouillage | Reset Interlock Value | Reiniciar valor de enclavamiento | Reiniciar Valor de Intertravamento | Сбросить значение блокировки | Reset Interlock Value
Set Interlock Value | Niveau haut des valeurs de l'interverrouillage | Set Interlock Value | Ajustar valor de enclavamiento | Ajustar Valor de Intertravamento | Установить значение блокировки | Set Interlock Value
SPS Processing Parameters | Paramètres de traitement de la SPS | SPS Processing Parameters | Parámetros de procesamiento SPS | Parâmetros de Processamento SPS | Пораметры обработки SPS | SPS Processing Parameters
Toggling state label | Libellé de l'état de basculement | Toggling state label | Etiqueta de estado en curso | Etiqueta de estado em Curso | Метка статуса Toggling | Toggling state label
SelfCheckFault state label | Libellé de l'état d'auto vérification du défaut | SelfCheckFault state label | Etiqueta de estado FallaAutoChequeo | Etiqueta de estado FalhaAutoCheque | Метка статуса SelfCheckFault | SelfCheckFault state label
Unknown state label | Libellé de l'état inconnu | Unknown state label | Etiqueta de estado desconocido | Etiqueta de estado Desconhecido | Метка статуса Unknown | Unknown state label
Suppressed state label | Libellé de l'état supprimé | Suppressed state label | Etiqueta de estado suprimido | Etiqueta de estado Suprimido | Метка статуса Suppressed | Suppressed state label
Forced state label | Libellé de l'état forcé | Forced state label | Etiqueta de estado forzado | Etiqueta de estado Forçado | Метка статуса Forced | Forced state label
Substituted state label | Libellé de l'état substitué | Substituted state label | Etiqueta de estado sustituido | Etiqueta de estado Substituído | Метка статуса Substituted | Substituted state label
Treatment on Set state | Traitement sur l'état Set | Treatment on Set state | Manipulación en estado de Ajuste | Manipulação em estado de Ajuste | Обработка статуса Set | Treatment on Set state
Treatment on Reset state | Traitement sur l'état Reset | Treatment on Reset state | Manipulación en estado de reajuste | Manipulação em estado de Reajuste | Обработка статуса Reset | Treatment on Reset state
Treatment on Open state | Traitement sur l'état Ouvert | Treatment on Open state | Manipulación en estado Abierto | Manipulação em estado Aberto | Обработка статуса Open | Treatment on Open state
Treatment on Close state | Traitement sur l'état Fermé | Treatment on Close state | Manipulación en estado Cerrado | Manipulação em estado Fechado | Обрабока статуса Close | Treatment on Close state
Treatment on Toggling state | Traitement sur l'état de basculement | Treatment on Toggling state | Manipulación en estado en curso | Manipulação em estado em Curso | Обработка статуса Toggling | Treatment on Toggling state
Treatment on SelfCheckFault state | Traitement sur l'état d'auto vérification du défaut | Treatment on SelfCheckFault state | Manipulación en estado FallaAutoChequeo | Manipulação em estado FalhaAutoCheque | Обработка статуса SelfCheckFault | Treatment on SelfCheckFault state
Treatment on Unknown state | Traitement sur l'état inconnu | Treatment on Unknown state | Manipulación en estado Desconocido | Manipulação em estado Desconhecido | Обрабока статуса Unknown | Treatment on Unknown state
Treatment on Suppressed state | Traitement sur l'état supprimé | Treatment on Suppressed state | Manipulación en estado Suprimido | Manipulação em estado Suprimido | Обработка статуса Suppressed | Treatment on Suppressed state
Treatment on Forced state | Traitement sur l'état forcé | Treatment on Forced state | Manipulación en estado Forzado | Manipulação em estado Forçado | Обработка статуса Forced | Treatment on Forced state
Treatment on Substituted state | Traitement sur l'état substitué | Treatment on Substituted state | Manipulación en estado sustituido | Manipulação em estado Substituído | Обработка статуса Substituted | Treatment on Substituted state
Treatment on Forcing state | Traitement sur l'état de forçage | Treatment on Forcing state | Manipulación en estado Forzando | Manipulação em estado Forzando | Обработка статуса Forcing | Treatment on Forcing state
Treatment on Substitution state | Traitement sur l'état de substitution | Treatment on Substitution state | Manipulación en estado por sustitución | Manipulação em estado por Substituição | Обработка статуса Substitution | Treatment on Substitution state
Treatment on Suppression state | Traitement sur l'état de suppression | Treatment on Suppression state | Manipulación en estado por supresión | Manipulação em estado por Supressão | Обработка статуса Suppression | Treatment on Suppression state
Alarm and Gravity on Toggling state | Gravité d'alarme sur l'état de basculement | Alarm and Gravity on Toggling state | Alarma y gravedad en estado en curso | Alarme e gravidade em estado em Curso | Тревога и важность статуса Toggling | Alarm and Gravity on Toggling state
Alarm and Gravity on SelfCheckFault state | Gravité d'alarme sur l'état d'auto vérification du défaut | Alarm and Gravity on SelfCheckFault state | Alarma y gravedad en estado FallaAutoChequeo | Alarme e gravidade em estado FalhaAutoCheque | Тревога и важность статуса SelfCheckFault | Alarm and Gravity on SelfCheckFault state
Alarm and Gravity on Unknown state | Gravité d'alarme sur l'état inconnu | Alarm and Gravity on Unknown state | Alarma y gravedad en estado desconocido | Alarme e gravidade em estado Desconhecido | Тревога и важность статуса Unknown | Alarm and Gravity on Unknown state
Alarm and Gravity on Suppressed state | Gravité d'alarme sur l'état supprimé | Alarm and Gravity on Suppressed state | Alarma y gravedad en estado Suprimido | Alarme e gravidade em estado Suprimido | Тревога и важность статуса Suppressed | Alarm and Gravity on Suppressed state
Alarm and Gravity on Forced state | Gravité d'alarme sur l'état forcé | Alarm and Gravity on Forced state | Alarma y gravedad en estado forzado | Alarme e gravidade em estado Forçado | Тревога и важность статуса Forced | Alarm and Gravity on Forced state
Alarm and Gravity on Substituted state | Gravité d'alarme sur l'état substitué | Alarm and Gravity on Substituted state | Alarma y gravedad en estado Sustituido | Alarme e gravidade em estado Substituído | Тревога и важность статуса Substituted | Alarm and Gravity on Substituted state
Masking due to control | Masqué dû à la commande | Masking due to control | Enmascarar debido al control | Mascarar devido ao controle | Masking due to control | Masking due to control
SBMC dependant | Dépendance SBMC | SBMC dependant | SBMC dependiente | SBMC dependente | SBMC иждивенца | SBMC unterhaltsberechtigte
Toggling filtering | Basculement du filtrage | Toggling filtering | Curso de la filtración | Curso de filtrar | Toggling filtering | Toggling filtering
Initial status | Status initial | Initial status | Estado inicial | Estado inicial | Начальный статус | Initial status
Forced Reset Interlock Value | Reset forcé des valeurs de l'interverrouillage | Forced Reset Interlock Value | Reiniciar forzado valor de enclavamiento | Reiniciar Forçado Valor de Intertravamento | Сброс значения блокировки Forced | Forced Reset Interlock Value
Forced Set Interlock Value | Niveau haut forcé des valeurs de l'interverrouillage | Forced Set Interlock Value | Ajustar forzado valor de enclavamiento | Ajustar Forçado Valor de Intertravamento | Установка значения блокировки Forced | Forced Set Interlock Value
Substituted Reset Interlock Value | Reset substitué des valeurs de l'interverrouillage | Substituted Reset Interlock Value | Reiniciar Sustituido valor de enclavamiento | Reiniciar Substituído Valor de Intertravamento | Сброс значения блокировки Substituted | Substituted Reset Interlock Value
Substituted Set Interlock Value | Niveau haut substitué des valeurs de l'interverrouillage | Substituted Set Interlock Value | Ajustar Sustituido valor de enclavamiento | Ajustar Substituído Valor de Intertravamento | Установка значения блокировки Substituted | Substituted Set Interlock Value
Suppressed interlock value | Valeur de l'interverrouillage supprimé | Suppressed interlock value | Valor de enclavamiento suprimido | Valor de Intertravamento Suprimido | Значение блокировки Suppressed | Suppressed interlock value
Unknown interlock value | Valeur de l'interverrouillage inconnu | Unknown interlock value | Valor de enclavamiento desconocido | Valor de Intertravamento Desconhecido | Значение блокировки Unknown | Unknown interlock value
Toggling interlock value | Valeur de l'interverrouillage de basculement | Toggling interlock value | Valor de enclavamiento curso | Valor de Intertravamento Curso | Значение блокировки Toggling | Toggling interlock value
SelfCheckFault interlock value | Valeur de l'interverrouillage sur l'auto vérification du défaut | SelfCheckFault interlock value | Valor de enclavamiento FallaAutoChequeo | Valor de Intertravamento FalhaAutoCheque | Значение блокировки SelfCheckFaul | SelfCheckFault interlock value
Default State labels | Valeurs par défaut des Etats électriques | Default State labels | Por defecto las etiquetas de estado | Estado padrão rótulos | По умолчанию состояние этикетки | Default State labels
Default Text at electrical state = 1 (16 char) | Texte par défaut à l'état électrique = 1 (16 car) | Default Text at electrical state = 1 (16 char) | Texto predeterminado en estado eléctrico = 1 (16 caract) | Texto padrão em estado Elétrico = 1 (16 caract) | умолчанию текст электрического состояния = 1 (16 символов) | Default Text at electrical state = 1 (16 char)
Default Text at electrical state = 0 (16 char) | Texte par défaut à l'état électrique = 0 (16 car) | Default Text at electrical state = 0 (16 char) | Texto predeterminado en estado eléctrico = 0 (16 caract) | Texto padrão em estado Elétrico = 0 (16 caract) | умолчанию текст электрического состояния = 0 (16 символов) | Default Text at electrical state = 0 (16 char)
Enable FSS (forcing / substituting / suppressing) | Activer le FSS (forçage / substitution / suppression) | Enable FSS (forcing / substituting / suppressing) | Permitir FSS (forcing / substituting / suppressing) | Permitir FSS (forcing / substituting / suppressing) | позволить FSS (forcing / substituting / suppressing) | Enable FSS (forcing / substituting / suppressing)
Double Digital Inputs Profiles | Profils des entrées numériques doubles (DPS) | Double Digital Inputs Profiles | Perfiles entradas digitales Dobles | Perfis Entradas Digitais Duplas | Профили двоичных DI | Double Digital Inputs Profiles
Double System Digital Inputs Profiles | Profils des entrées numériques systèmes doubles (DPS) | Double System Digital Inputs Profiles | Pérfiles de sistema de entradas digitales dobles | Perfis de Sistema de Entradas Digitais Duplas | Профили двоичных системных DI | Double System Digital Inputs Profiles
Function Name | Nom de la fonction | Function Name | Nombre de función | Nome da Função | Функция Name | Function Name
SCE Name (13 char) | Nom dans le SCE (13 char) | SCE Name (13 char) | Nombre SCE (13 caract) | Nome SCE (13 caract) | Имя SCE (13 символов) | SCE Name (13 char)
DPS General Parameters | Paramètres généraux de la DPS | DPS General Parameters | Parámetros generales DPS | Parâmetros Geração DPS | Основные параметры DPS | DPS General Parameters
Generation Condition | Condition de la Génération | Generation Condition | Condición de generación | Condição de Geração | Основное условие | Generation Condition
Audible Alarm | Alarme audible | Audible Alarm | Alarma audible | Alarme Auditível | Звуковая тревога | Audible Alarm
State 10 Gravity level | Etat 10 niveau de gravité | State 10 Gravity level | Nivel de gravedad 10 | Nivel de gravidade 10 | Состояние 10 Уровень важности | State 10 Gravity level
State 10 confirmation delay (x100 ms) | Etat 10 confirmation de retard (x100 ms) | State 10 confirmation delay (x100 ms) | Confirmación de retardo Estado 10 (x100 ms) | Confirmação de retardo Estado 10 (x100 ms) | Состояние 10 задержка подтверждения (х100 мс) | State 10 confirmation delay (x100 ms)
State 01 Gravity level | Etat 01 niveau de gravité | State 01 Gravity level | Nivel de gravedad Estado 01 | Nivel de gravidade Estado 01 | Состояние 01 Уровень важности | State 01 Gravity level
State 01 confirmation delay (x100 ms) | Etat 01 confirmation du retard (x100 ms) | State 01 confirmation delay (x100 ms) | Confirmación de retardo Estado 01 (x100 ms) | Confirmação de retardo Estado 01 (x100 ms) | Состояние 01 задержка подтверждения (х100 мс) | State 01 confirmation delay (x100 ms)
Complementary [00] delay (x100 ms) | Complémentarité [00] retard (x100 ms) | Complementary [00] delay (x100 ms) | Retardo [00] complementario (x100 ms) | Retardo [00] complememtario (x100 ms) | Дополнительная [00] задержка (х100 мс) | Complementary [00] delay (x100 ms)
Complementary [11] delay (x100 ms) | Complémentarité [11] retard (x100 ms) | Complementary [11] delay (x100 ms) | Retardo [11] complementario (x100 ms) | Retardo [11] complememtario (x100 ms) | Дополнительная [11] задержка (х100 мс) | Complementary [11] delay (x100 ms)
Alarm appearance delay (0-120 s) | Retard d'apparition de l'alarme (0-120 s) | Alarm appearance delay (0-120 s) | Retardo de aparición de Alarma (0-120 s) | Retardo de aparição de Alarme (0-120 s) | Задержка появления тревоги (0-120 с) | Alarm appearance delay (0-120 s)
Clearing Mode | Mode d'effacement | Clearing Mode | Modo Clearing | Modo de Limpeza | Режим очистки | Clearing Mode
DPS Printing Parameters | Paramètres d'impression de la DPS | DPS Printing Parameters | Parámetros de impresión DPS | Parâmetros de Impressão DPS | Параметры печати DPS | DPS Printing Parameters
Printed on Sequence Of Events SOE 1 : | Imprimer sur l'imprimante Fil de l'eau 1 : | Printed on Sequence Of Events SOE 1 : | Impreso en SOE 1 : | Impresso em SOE 1 : | Вывод на SOE 1 : | Printed on Sequence Of Events SOE 1 :
Printed on Sequence Of Events SOE 2 : | Imprimer sur l'imprimante Fil de l'eau 2 : | Printed on Sequence Of Events SOE 2 : | Impreso en SOE 2 : | Impresso em SOE 1 : | Вывод на SOE 2 : | Printed on Sequence Of Events SOE 2 :
Printed on Logbook LB 1 : | Imprimer sur l'imprimante Journal de Bord 1 : | Printed on Logbook LB 1 : | Impreso en LB 1 : | Impresso em LB 1 : | Вывод на LB 1 : | Printed on Logbook LB 1 :
Printed on Logbook LB 2 : | Imprimer sur l'imprimante Journal de Bord 2 : | Printed on Logbook LB 2 : | Impreso en LB 2 : | Impresso em LB 2 : | Вывод на LB 2 : | Printed on Logbook LB 2 :
DPS Interlocking Parameters | Paramètres d'Interverrouillage de la DPS | DPS Interlocking Parameters | Parámetros de enclavamiento DPS | Parâmetros de Intertravamento DPS | Параметры блокировки DPS | DPS Interlocking Parameters
Jammed Interlock Value | Valeur "bloqué" de l'interverrouillage | Jammed Interlock Value | Valor enclavamiento bloqueado | Valor Intertravamento bloqueado | Значение блокировки Jammed | Jammed Interlock Value
Open Interlock Value | Valeur "ouvert" de l'interverrouillage | Open Interlock Value | Valor enclavamiento abierto | Valor Intertravamento Aberto | Значение блокировки Open | Open Interlock Value
Closed Interlock Value | Valeur "fermé" de l'interverrouillage | Closed Interlock Value | Valor enclavamiento cerrado | Valor Intertravamento Fechado | Значение блокировки Closed | Closed Interlock Value
DPS Processing Parameters | Paramètres de traitement de la DPS | DPS Processing Parameters | Parámetros de procesadmiento DPS | Parâmetros de Processamento DPS | Пораметры обработки DPS | DPS Processing Parameters
Jammed (=DBI 00) state label | Libellé de l'état bloqué (=DBI 00) | Jammed (=DBI 00) state label | Etiqueta de estado bloqueado (=DBI 00) | Etiqueta de estado bloqueado (=DBI 00) | Метка статуса Jammed (=DBI 00) | Jammed (=DBI 00) state label
Undefined (=DBI 11) state label | Libellé de l'état indéfini (=DBI 11) | Undefined (=DBI 11) state label | Etiqueta de estado indefinido (=DBI 11) | Etiqueta de estado Indefinido (=DBI 11) | Метка статуса Undefined (=DBI 11) | Undefined (=DBI 11) state label
Toggling state label | Libellé de l'état de basculement | Toggling state label | Etiqueta de estado en curso | Etiqueta de estado em Curso | Метка статуса Toggling | Toggling state label
SelfCheckFault state label | Libellé de l'état d'auto vérification du défaut | SelfCheckFault state label | Etiqueta de estado FallaAutoChequeo | Etiqueta de estado FalhaAutoCheque | Метка статуса SelfCheckFault | SelfCheckFault state label
Unknown state label | Libellé de l'état inconnu | Unknown state label | Etiqueta de estado desconocido | Etiqueta de estado Desconhecido | Метка статуса Unknown | Unknown state label
Suppressed state label | Libellé de l'état supprimé | Suppressed state label | Etiqueta de estado suprimido | Etiqueta de estado Suprimido | Метка статуса Suppressed | Suppressed state label
Forced state label | Libellé de l'état forcé | Forced state label | Etiqueta de estado forzado | Etiqueta de estado Forçado | Метка статуса Forced | Forced state label
Substituted state label | Libellé de l'état substitué | Substituted state label | Etiqueta de estado sustituido | Etiqueta de estado Substituído | Метка статуса Substituted | Substituted state label
Motion interlock value | Valeur de l'interverrouillage Motion | Motion interlock value | Valor de enclavamiento Motion | Valor de Intertravamento Motion | Значение блокировки Motion | Motion interlock value
Treatment on Open state | Traitement sur l'état Ouvert | Treatment on Open state | Manipulación en estado Abierto | Manipulação em estado Aberto | Обработка статуса Open | Treatment on Open state
Treatment on Close state | Traitement sur l'état Fermé | Treatment on Close state | Manipulación en estado Cerrado | Manipulação em estado Fechado | Обрабока статуса Close | Treatment on Close state
Treatment on Jammed state | Traitement sur l'état bloqué | Treatment on Jammed state | Manipulación en estado bloqueado | Manipulação em estado bloqueado | Обработка статуса Jammed | Treatment on Jammed state
Treatment on Undefined state | Traitement sur l'état indéfini | Treatment on Undefined state | Manipulación en estado Indefinido | Manipulação em estado Indefinido | Обработка статуса Undefined | Treatment on Undefined state
Treatment on Toggling state | Traitement sur l'état de basculement | Treatment on Toggling state | Manipulación en estado en curso | Manipulação em estado em Curso | Обработка статуса Toggling | Treatment on Toggling state
Treatment on SelfCheckFault state | Traitement sur l'état d'auto vérification du défaut | Treatment on SelfCheckFault state | Manipulación en estado FallaAutoChequeo | Manipulação em estado FalhaAutoCheque | Обработка статуса SelfCheckFault | Treatment on SelfCheckFault state
Treatment on Unknown state | Traitement sur l'état inconnu | Treatment on Unknown state | Manipulación en estado Desconocido | Manipulação em estado Desconhecido | Обрабока статуса Unknown | Treatment on Unknown state
Treatment on Suppressed state | Traitement sur l'état supprimé | Treatment on Suppressed state | Manipulación en estado Suprimido | Manipulação em estado Suprimido | Обработка статуса Suppressed | Treatment on Suppressed state
Treatment on Forced state | Traitement sur l'état forcé | Treatment on Forced state | Manipulación en estado Forzado | Manipulação em estado Forçado | Обработка статуса Forced | Treatment on Forced state
Treatment on Substituted state | Traitement sur l'état substitué | Treatment on Substituted state | Manipulación en estado sustituido | Manipulação em estado Substituído | Обработка статуса Substituted | Treatment on Substituted state
Treatment on Forcing state | Traitement sur l'état de forçage | Treatment on Forcing state | Manipulación en estado Forzando | Manipulação em estado Forzando | Обработка статуса Forcing | Treatment on Forcing state
Treatment on Substitution state | Traitement sur l'état de substitution | Treatment on Substitution state | Manipulación en estado por sustitución | Manipulação em estado por Substituição | Обработка статуса Substitution | Treatment on Substitution state
Treatment on Suppression state | Traitement sur l'état de suppression | Treatment on Suppression state | Manipulación en estado por supresión | Manipulação em estado por Supressão | Обработка статуса Suppression | Treatment on Suppression state
Alarm and Gravity on Jammed state | Gravité d'alarme sur l'état bloqué | Alarm and Gravity on Jammed state | Alarma y gravedad en estado bloqueado | Alarme e gravidade em estado bloqueado | Тревога и важность статуса Jammed | Alarm and Gravity on Jammed state
Alarm and Gravity on Undefined state | Gravité d'alarme sur l'état indéfini | Alarm and Gravity on Undefined state | Alarma y gravedad en estado Indefinido | Alarme e gravidade em estado Indefinido | Тревога и важность статуса Undefined | Alarm and Gravity on Undefined state
Alarm and Gravity on Toggling state | Gravité d'alarme sur l'état de basculement | Alarm and Gravity on Toggling state | Alarma y gravedad en estado en curso | Alarme e gravidade em estado em Curso | Тревога и важность статуса Toggling | Alarm and Gravity on Toggling state
Alarm and Gravity on SelfCheckFault state | Gravité d'alarme sur l'état d'auto vérification du défaut | Alarm and Gravity on SelfCheckFault state | Alarma y gravedad en estado FallaAutoChequeo | Alarme e gravidade em estado FalhaAutoCheque | Тревога и важность статуса SelfCheckFault | Alarm and Gravity on SelfCheckFault state
Alarm and Gravity on Unknown state | Gravité d'alarme sur l'état inconnu | Alarm and Gravity on Unknown state | Alarma y gravedad en estado desconocido | Alarme e gravidade em estado Desconhecido | Тревога и важность статуса Unknown | Alarm and Gravity on Unknown state
Alarm and Gravity on Suppressed state | Gravité d'alarme sur l'état supprimé | Alarm and Gravity on Suppressed state | Alarma y gravedad en estado Suprimido | Alarme e gravidade em estado Suprimido | Тревога и важность статуса Suppressed | Alarm and Gravity on Suppressed state
Alarm and Gravity on Forced state | Gravité d'alarme sur l'état forcé | Alarm and Gravity on Forced state | Alarma y gravedad en estado forzado | Alarme e gravidade em estado Forçado | Тревога и важность статуса Forced | Alarm and Gravity on Forced state
Alarm and Gravity on Substituted state | Gravité d'alarme sur l'état substitué | Alarm and Gravity on Substituted state | Alarma y gravedad en estado Sustituido | Alarme e gravidade em estado Substituído | Тревога и важность статуса Substituted | Alarm and Gravity on Substituted state
Fugitive Alarm (Spurious) | Alarme fugitive | Fugitive Alarm (Spurious) | Alarma fujitiva (Spurious) | Alarme de Fuga(Spurious) | Fugitive Alarm (Spurious) | Fugitive Alarm (Spurious)
Masking due to control | Masqué dû à la commande | Masking due to control | Enmascarar debido al control | Mascarar devido ao controle | Masking due to control | Masking due to control
SBMC dependant | Dépendance SBMC | SBMC dependant | SBMC dependiente | SBMC dependente | SBMC иждивенца | SBMC unterhaltsberechtigte
Toggling filtering | Basculement du filtrage | Toggling filtering | Curso de la filtración | Curso de filtrar | Toggling filtering | Toggling filtering
Initial status | Status initial | Initial status | Estado inicial | Estado inicial | Начальный статус | Initial status
Forced Jammed Interlock Value | Bloquage forcé des valeurs de l'interverrouillage | Forced Jammed Interlock Value | Bloqueado forzado valor de enclavamiento | Bloqueado Forçado Valor de Intertravamento | Значение блокировки Forced Jammed | Forced Jammed Interlock Value
Forced Open Interlock Value | Ouverture forcée des valeurs de l'interverrouillage | Forced Open Interlock Value | Abierto forzado valor de enclavamiento | Aberto Forçado Valor de Intertravamento | Значение блокировки Forced Open | Forced Open Interlock Value
Forced Closed Interlock Value | Fermeture forcée des valeurs de l'interverrouillage | Forced Closed Interlock Value | Cerrado forzado valor de enclavamiento | Fechado Forçado Valor de Intertravamento | Значение блокировки Forced Closed | Forced Closed Interlock Value
Substituted Jammed Interlock Value | Bloquage substitué des valeurs de l'interverrouillage | Substituted Jammed Interlock Value | Bloqueado Sustituido valor de enclavamiento | Bloqueado Substituído Valor de Intertravamento | Значение блокировки Substituted Jammed | Substituted Jammed Interlock Value
Substituted Open Interlock Value | Ouverture substituée des valeurs de l'interverrouillage | Substituted Open Interlock Value | Abierto Sustituido valor de enclavamiento | Aberto Substituído Valor de Intertravamento | Значение блокировки Substituted Open | Substituted Open Interlock Value
Substituted Closed Interlock Value | Fermeture substituée des valeurs de l'interverrouillage | Substituted Closed Interlock Value | Cerrado Sustituido valor de enclavamiento | Fechado Substituído Valor de Intertravamento | Значение блокировки Substituted Closed | Substituted Closed Interlock Value
Suppressed interlock value | Valeur de l'interverrouillage supprimé | Suppressed interlock value | Valor de enclavamiento suprimido | Valor de Intertravamento Suprimido | Значение блокировки Suppressed | Suppressed interlock value
Unknown interlock value | Valeur de l'interverrouillage inconnu | Unknown interlock value | Valor de enclavamiento desconocido | Valor de Intertravamento Desconhecido | Значение блокировки Unknown | Unknown interlock value
Toggling interlock value | Valeur de l'interverrouillage de basculement | Toggling interlock value | Valor de enclavamiento curso | Valor de Intertravamento Curso | Значение блокировки Toggling | Toggling interlock value
SelfCheckFault interlock value | Valeur de l'interverrouillage sur l'auto vérification du défaut | SelfCheckFault interlock value | Valor de enclavamiento FallaAutoChequeo | Valor de Intertravamento FalhaAutoCheque | Значение блокировки SelfCheckFaul | SelfCheckFault interlock value
Undefined interlock value | Valeur de l'interverrouillage indéfini | Undefined interlock value | Valor de enclavamiento indefinido | Valor de Intertravamento Indefinido | Значение блокировки Undefined | Undefined interlock value
Default State labels | Valeurs par défaut des Etats électriques | Default State labels | Por defecto las etiquetas de estado | Estado padrão rótulos | По умолчанию состояние этикетки | Default State labels
Default Text at electrical state = 10 (16 char) | Texte par défaut à l'état électrique = 10 (16 car) | Default Text at electrical state = 10 (16 char) | Texto predeterminado en estado eléctrico = 10 (16 caract) | Texto padrão em estado Elétrico = 10 (16 caract) | умолчанию текст электрического состояния = 10 (16 символов) | Default Text at electrical state = 10 (16 char)
Default Text at electrical state = 01 (16 char) | Texte par défaut à l'état électrique = 01 (16 car) | Default Text at electrical state = 01 (16 char) | Texto predeterminado en estado eléctrico = 01 (16 caract) | Texto padrão em estado Elétrico = 01 (16 caract) | умолчанию текст электрического состояния = 01 (16 символов) | Default Text at electrical state = 01 (16 char)
Enable FSS (forcing / substituting / suppressing) | Activer le FSS (forçage / substitution / suppression) | Enable FSS (forcing / substituting / suppressing) | Permitir FSS (forcing / substituting / suppressing) | Permitir FSS (forcing / substituting / suppressing) | позволить FSS (forcing / substituting / suppressing) | Enable FSS (forcing / substituting / suppressing)
Multiple Digital Inputs Profiles | Profils des entrées numériques multiples (MPS) | Multiple Digital Inputs Profiles | Perfiles de entradas digitales Múltiples | Perfis de Entradas digitais Múltiplas | Профили множественных DI | Multiple Digital Inputs Profiles
Multiple System Digital Inputs Profiles | Profils des entrées numériques systèmes multiples (MPS) | Multiple System Digital Inputs Profiles | Perfiles de systema de entradas digitales Múltiples | Perfis de Systema de Entradas Digitais Múltiplas | Профили множественных системных DI | Multiple System Digital Inputs Profiles
Function Name | Nom de la fonction | Function Name | Nombre de función | Nome da Função | Функция Name | Function Name
SCE Name (13 char) | Nom dans le SCE (13 char) | SCE Name (13 char) | Nombre SCE (13 caract) | Nome SCE (13 caract) | Имя SCE (13 символов) | SCE Name (13 char)
MPS General Parameters | Paramètres généraux de la MPS | MPS General Parameters | Parámetros generales MPS | Parâmetros Geração MPS | Основные параметры MPS | MPS General Parameters
Generation Condition | Condition de la Génération | Generation Condition | Condición de generación | Condição de Geração | Основное условие | Generation Condition
Audible Alarm | Alarme audible | Audible Alarm | Alarma audible | Alarme Auditível | Звуковая тревога | Audible Alarm
Alarm appearance delay (0-120 s) | Retard d'apparition de l'alarme (0-120 s) | Alarm appearance delay (0-120 s) | Retardo de aparición de Alarma (0-120 s) | Retardo de aparição de Alarme (0-120 s) | Задержка появления тревоги (0-120 с) | Alarm appearance delay (0-120 s)
Clearing Mode | Mode d'effacement | Clearing Mode | Modo Clearing | Modo de Limpeza | Режим очистки | Clearing Mode
MPS Printing Parameters | Paramètres d'impression de la MPS | MPS Printing Parameters | Parámetros de impresión MPS | Parâmetros de Impressão MPS | Параметры печати MPS | MPS Printing Parameters
Printed on Sequence Of Events SOE 1 : | Imprimer sur l'imprimante Fil de l'eau 1 : | Printed on Sequence Of Events SOE 1 : | Impreso en SOE 1 : | Impresso em SOE 1 : | Вывод на SOE 1 : | Printed on Sequence Of Events SOE 1 :
Printed on Sequence Of Events SOE 2 : | Imprimer sur l'imprimante Fil de l'eau 2 : | Printed on Sequence Of Events SOE 2 : | Impreso en SOE 2 : | Impresso em SOE 1 : | Вывод на SOE 2 : | Printed on Sequence Of Events SOE 2 :
Printed on Logbook LB 1 : | Imprimer sur l'imprimante Journal de Bord 1 : | Printed on Logbook LB 1 : | Impreso en LB 1 : | Impresso em LB 1 : | Вывод на LB 1 : | Printed on Logbook LB 1 :
Printed on Logbook LB 2 : | Imprimer sur l'imprimante Journal de Bord 2 : | Printed on Logbook LB 2 : | Impreso en LB 2 : | Impresso em LB 2 : | Вывод на LB 2 : | Printed on Logbook LB 2 :
MPS Interlocking Parameters | Paramètres d'Interverrouillage de la MPS | MPS Interlocking Parameters | Parámetros de enclavamiento MPS | Parâmetros de Intertravamento MPS | Параметры блокировки MPS | MPS Interlocking Parameters
State 0 Interlock Value | Valeur de l'interverrouillage à l'état 0 | State 0 Interlock Value | Valor de enclavamiento estado 0 | Valor de Intertravamento estado 0 | Состояние 0 значения блокировки | State 0 Interlock Value
State 1 Interlock Value | Valeur de l'interverrouillage à l'état 1 | State 1 Interlock Value | Valor de enclavamiento estado 1 | Valor de Intertravamento estado 1 | Состояние 1 значения блокировки | State 1 Interlock Value
State 2 Interlock Value | Valeur de l'interverrouillage à l'état 2 | State 2 Interlock Value | Valor de enclavamiento estado 2 | Valor de Intertravamento estado 2 | Состояние 2 значения блокировки | State 2 Interlock Value
State 3 Interlock Value | Valeur de l'interverrouillage à l'état 3 | State 3 Interlock Value | Valor de enclavamiento estado 3 | Valor de Intertravamento estado 3 | Состояние 3 значения блокировки | State 3 Interlock Value
State 4 Interlock Value | Valeur de l'interverrouillage à l'état 4 | State 4 Interlock Value | Valor de enclavamiento estado 4 | Valor de Intertravamento estado 4 | Состояние 4 значения блокировки | State 4 Interlock Value
State 5 Interlock Value | Valeur de l'interverrouillage à l'état 5 | State 5 Interlock Value | Valor de enclavamiento estado 5 | Valor de Intertravamento estado 5 | Состояние 5 значения блокировки | State 5 Interlock Value
State 6 Interlock Value | Valeur de l'interverrouillage à l'état 6 | State 6 Interlock Value | Valor de enclavamiento estado 6 | Valor de Intertravamento estado 6 | Состояние 6 значения блокировки | State 6 Interlock Value
State 7 Interlock Value | Valeur de l'interverrouillage à l'état 7 | State 7 Interlock Value | Valor de enclavamiento estado 7 | Valor de Intertravamento estado 7 | Состояние 7 значения блокировки | State 7 Interlock Value
State 8 Interlock Value | Valeur de l'interverrouillage à l'état 8 | State 8 Interlock Value | Valor de enclavamiento estado 8 | Valor de Intertravamento estado 8 | Состояние 8 значения блокировки | State 8 Interlock Value
State 9 Interlock Value | Valeur de l'interverrouillage à l'état 9 | State 9 Interlock Value | Valor de enclavamiento estado 9 | Valor de Intertravamento estado 9 | Состояние 9 значения блокировки | State 9 Interlock Value
State 10 Interlock Value | Valeur de l'interverrouillage à l'état 10 | State 10 Interlock Value | Valor de enclavamiento estado 10 | Valor de Intertravamento estado 10 | Состояние 10 значения блокировки | State 10 Interlock Value
State 11 Interlock Value | Valeur de l'interverrouillage à l'état 11 | State 11 Interlock Value | Valor de enclavamiento estado 11 | Valor de Intertravamento estado 11 | Состояние 11 значения блокировки | State 11 Interlock Value
State 12 Interlock Value | Valeur de l'interverrouillage à l'état 12 | State 12 Interlock Value | Valor de enclavamiento estado 12 | Valor de Intertravamento estado 12 | Состояние 12 значения блокировки | State 12 Interlock Value
State 13 Interlock Value | Valeur de l'interverrouillage à l'état 13 | State 13 Interlock Value | Valor de enclavamiento estado 13 | Valor de Intertravamento estado 13 | Состояние 13 значения блокировки | State 13 Interlock Value
State 14 Interlock Value | Valeur de l'interverrouillage à l'état 14 | State 14 Interlock Value | Valor de enclavamiento estado 14 | Valor de Intertravamento estado 14 | Состояние 14 значения блокировки | State 14 Interlock Value
State 15 Interlock Value | Valeur de l'interverrouillage à l'état 15 | State 15 Interlock Value | Valor de enclavamiento estado 15 | Valor de Intertravamento estado 15 | Состояние 15 значения блокировки | State 15 Interlock Value
MPS Processing Parameters | Paramètres de traitement de la MPS | MPS Processing Parameters | Parámetros de procesamiento MPS | Parâmetros de Processamento MPS | Пораметры обработки MPS | MPS Processing Parameters
State 0 label | Libellé de l'état 0 | State 0 label | Etiqueta de estado 0 | Etiqueta de estado 0 | Состояние 0 метки | State 0 label
State 1 label | Libellé de l'état 1 | State 1 label | Etiqueta de estado 1 | Etiqueta de estado 1 | Состояние 1 метки | State 1 label
State 2 label | Libellé de l'état 2 | State 2 label | Etiqueta de estado 2 | Etiqueta de estado 2 | Состояние 2 метки | State 2 label
State 3 label | Libellé de l'état 3 | State 3 label | Etiqueta de estado 3 | Etiqueta de estado 3 | Состояние 3 метки | State 3 label
State 4 label | Libellé de l'état 4 | State 4 label | Etiqueta de estado 4 | Etiqueta de estado 4 | Состояние 4 метки | State 4 label
State 5 label | Libellé de l'état 5 | State 5 label | Etiqueta de estado 5 | Etiqueta de estado 5 | Состояние 5 метки | State 5 label
State 6 label | Libellé de l'état 6 | State 6 label | Etiqueta de estado 6 | Etiqueta de estado 6 | Состояние 6 метки | State 6 label
State 7 label | Libellé de l'état 7 | State 7 label | Etiqueta de estado 7 | Etiqueta de estado 7 | Состояние 7 метки | State 7 label
State 8 label | Libellé de l'état 8 | State 8 label | Etiqueta de estado 8 | Etiqueta de estado 8 | Состояние 8 метки | State 8 label
State 9 label | Libellé de l'état 9 | State 9 label | Etiqueta de estado 9 | Etiqueta de estado 9 | Состояние 9 метки | State 9 label
State 10 label | Libellé de l'état 10 | State 10 label | Etiqueta de estado 10 | Etiqueta de estado 10 | Состояние 10 метки | State 10 label
State 11 label | Libellé de l'état 11 | State 11 label | Etiqueta de estado 11 | Etiqueta de estado 11 | Состояние 11 метки | State 11 label
State 12 label | Libellé de l'état 12 | State 12 label | Etiqueta de estado 12 | Etiqueta de estado 12 | Состояние 12 метки | State 12 label
State 13 label | Libellé de l'état 13 | State 13 label | Etiqueta de estado 13 | Etiqueta de estado 13 | Состояние 13 метки | State 13 label
State 14 label | Libellé de l'état 14 | State 14 label | Etiqueta de estado 14 | Etiqueta de estado 14 | Состояние 14 метки | State 14 label
State 15 label | Libellé de l'état 15 | State 15 label | Etiqueta de estado 15 | Etiqueta de estado 15 | Состояние 15 метки | State 15 label
Undefined state label | Libellé de l'état indéfini | Undefined state label | Etiqueta de estado Indefinido | Etiqueta de estado Indefinido | Метка статуса Undefined | Undefined state label
Toggling state label | Libellé de l'état de basculement | Toggling state label | Etiqueta de estado en curso | Etiqueta de estado em Curso | Метка статуса Toggling | Toggling state label
SelfCheckFault state label | Libellé de l'état d'auto vérification du défaut | SelfCheckFault state label | Etiqueta de estado FallaAutoChequeo | Etiqueta de estado FalhaAutoCheque | Метка статуса SelfCheckFault | SelfCheckFault state label
Unknown state label | Libellé de l'état inconnu | Unknown state label | Etiqueta de estado desconocido | Etiqueta de estado Desconhecido | Метка статуса Unknown | Unknown state label
Suppressed state label | Libellé de l'état supprimé | Suppressed state label | Etiqueta de estado suprimido | Etiqueta de estado Suprimido | Метка статуса Suppressed | Suppressed state label
Forced state label | Libellé de l'état forcé | Forced state label | Etiqueta de estado forzado | Etiqueta de estado Forçado | Метка статуса Forced | Forced state label
Substituted state label | Libellé de l'état substitué | Substituted state label | Etiqueta de estado sustituido | Etiqueta de estado Substituído | Метка статуса Substituted | Substituted state label
Treatment on state 0 | Traitement sur l'état 0 | Treatment on state 0 | Manipulación en estado 0 | Manipulação em estado 0 | Обработка статуса 0 | Treatment on state 0
Treatment on state 1 | Traitement sur l'état 1 | Treatment on state 1 | Manipulación en estado 1 | Manipulação em estado 1 | Обработка статуса 1 | Treatment on state 1
Treatment on state 2 | Traitement sur l'état 2 | Treatment on state 2 | Manipulación en estado 2 | Manipulação em estado 2 | Обработка статуса 2 | Treatment on state 2
Treatment on state 3 | Traitement sur l'état 3 | Treatment on state 3 | Manipulación en estado 3 | Manipulação em estado 3 | Обработка статуса 3 | Treatment on state 3
Treatment on state 4 | Traitement sur l'état 4 | Treatment on state 4 | Manipulación en estado 4 | Manipulação em estado 4 | Обработка статуса 4 | Treatment on state 4
Treatment on state 5 | Traitement sur l'état 5 | Treatment on state 5 | Manipulación en estado 5 | Manipulação em estado 5 | Обработка статуса 5 | Treatment on state 5
Treatment on state 6 | Traitement sur l'état 6 | Treatment on state 6 | Manipulación en estado 6 | Manipulação em estado 6 | Обработка статуса 6 | Treatment on state 6
Treatment on state 7 | Traitement sur l'état 7 | Treatment on state 7 | Manipulación en estado 7 | Manipulação em estado 7 | Обработка статуса 7 | Treatment on state 7
Treatment on state 8 | Traitement sur l'état 8 | Treatment on state 8 | Manipulación en estado 8 | Manipulação em estado 8 | Обработка статуса 8 | Treatment on state 8
Treatment on state 9 | Traitement sur l'état 9 | Treatment on state 9 | Manipulación en estado 9 | Manipulação em estado 9 | Обработка статуса 9 | Treatment on state 9
Treatment on state 10 | Traitement sur l'état 10 | Treatment on state 10 | Manipulación en estado 10 | Manipulação em estado 10 | Обработка статуса 10 | Treatment on state 10
Treatment on state 11 | Traitement sur l'état 11 | Treatment on state 11 | Manipulación en estado 11 | Manipulação em estado 11 | Обработка статуса 11 | Treatment on state 11
Treatment on state 12 | Traitement sur l'état 12 | Treatment on state 12 | Manipulación en estado 12 | Manipulação em estado 12 | Обработка статуса 12 | Treatment on state 12
Treatment on state 13 | Traitement sur l'état 13 | Treatment on state 13 | Manipulación en estado 13 | Manipulação em estado 13 | Обработка статуса 13 | Treatment on state 13
Treatment on state 14 | Traitement sur l'état 14 | Treatment on state 14 | Manipulación en estado 14 | Manipulação em estado 14 | Обработка статуса 14 | Treatment on state 14
Treatment on state 15 | Traitement sur l'état 15 | Treatment on state 15 | Manipulación en estado 15 | Manipulação em estado 15 | Обработка статуса 15 | Treatment on state 15
Treatment on Undefined state | Traitement sur l'état indéfini | Treatment on Undefined state | Manipulación en estado Indefinido | Manipulação em estado Indefinido | Обработка статуса Undefined | Treatment on Undefined state
Treatment on Toggling state | Traitement sur l'état de basculement | Treatment on Toggling state | Manipulación en estado en curso | Manipulação em estado em Curso | Обработка статуса Toggling | Treatment on Toggling state
Treatment on SelfCheckFault state | Traitement sur l'état d'auto vérification du défaut | Treatment on SelfCheckFault state | Manipulación en estado FallaAutoChequeo | Manipulação em estado FalhaAutoCheque | Обработка статуса SelfCheckFault | Treatment on SelfCheckFault state
Treatment on Unknown state | Traitement sur l'état inconnu | Treatment on Unknown state | Manipulación en estado Desconocido | Manipulação em estado Desconhecido | Обрабока статуса Unknown | Treatment on Unknown state
Treatment on Suppressed state | Traitement sur l'état supprimé | Treatment on Suppressed state | Manipulación en estado Suprimido | Manipulação em estado Suprimido | Обработка статуса Suppressed | Treatment on Suppressed state
Treatment on Forced state | Traitement sur l'état forcé | Treatment on Forced state | Manipulación en estado Forzado | Manipulação em estado Forçado | Обработка статуса Forced | Treatment on Forced state
Treatment on Substituted state | Traitement sur l'état substitué | Treatment on Substituted state | Manipulación en estado sustituido | Manipulação em estado Substituído | Обработка статуса Substituted | Treatment on Substituted state
Treatment on Forcing state | Traitement sur l'état de forçage | Treatment on Forcing state | Manipulación en estado Forzando | Manipulação em estado Forzando | Обработка статуса Forcing | Treatment on Forcing state
Treatment on Substitution state | Traitement sur l'état de substitution | Treatment on Substitution state | Manipulación en estado por sustitución | Manipulação em estado por Substituição | Обработка статуса Substitution | Treatment on Substitution state
Treatment on Suppression state | Traitement sur l'état de suppression | Treatment on Suppression state | Manipulación en estado por supresión | Manipulação em estado por Supressão | Обработка статуса Suppression | Treatment on Suppression state
Alarm and Gravity on state 0 | Gravité d'alarme sur l'état 0 | Alarm and Gravity on state 0 | Alarma y gravedad en estado 0 | Alarme e gravidade em estado 0 | Тревога и важность статуса 0 | Alarm and Gravity on state 0
Alarm and Gravity on state 1 | Gravité d'alarme sur l'état 1 | Alarm and Gravity on state 1 | Alarma y gravedad en estado 1 | Alarme e gravidade em estado 1 | Тревога и важность статуса 1 | Alarm and Gravity on state 1
Alarm and Gravity on state 2 | Gravité d'alarme sur l'état 2 | Alarm and Gravity on state 2 | Alarma y gravedad en estado 2 | Alarme e gravidade em estado 2 | Тревога и важность статуса 2 | Alarm and Gravity on state 2
Alarm and Gravity on state 3 | Gravité d'alarme sur l'état 3 | Alarm and Gravity on state 3 | Alarma y gravedad en estado 3 | Alarme e gravidade em estado 3 | Тревога и важность статуса 3 | Alarm and Gravity on state 3
Alarm and Gravity on state 4 | Gravité d'alarme sur l'état 4 | Alarm and Gravity on state 4 | Alarma y gravedad en estado 4 | Alarme e gravidade em estado 4 | Тревога и важность статуса 4 | Alarm and Gravity on state 4
Alarm and Gravity on state 5 | Gravité d'alarme sur l'état 5 | Alarm and Gravity on state 5 | Alarma y gravedad en estado 5 | Alarme e gravidade em estado 5 | Тревога и важность статуса 5 | Alarm and Gravity on state 5
Alarm and Gravity on state 6 | Gravité d'alarme sur l'état 6 | Alarm and Gravity on state 6 | Alarma y gravedad en estado 6 | Alarme e gravidade em estado 6 | Тревога и важность статуса 6 | Alarm and Gravity on state 6
Alarm and Gravity on state 7 | Gravité d'alarme sur l'état 7 | Alarm and Gravity on state 7 | Alarma y gravedad en estado 7 | Alarme e gravidade em estado 7 | Тревога и важность статуса 7 | Alarm and Gravity on state 7
Alarm and Gravity on state 8 | Gravité d'alarme sur l'état 8 | Alarm and Gravity on state 8 | Alarma y gravedad en estado 8 | Alarme e gravidade em estado 8 | Тревога и важность статуса 8 | Alarm and Gravity on state 8
Alarm and Gravity on state 9 | Gravité d'alarme sur l'état 9 | Alarm and Gravity on state 9 | Alarma y gravedad en estado 9 | Alarme e gravidade em estado 9 | Тревога и важность статуса 9 | Alarm and Gravity on state 9
Alarm and Gravity on state 10 | Gravité d'alarme sur l'état 10 | Alarm and Gravity on state 10 | Alarma y gravedad en estado 10 | Alarme e gravidade em estado 10 | Тревога и важность статуса 10 | Alarm and Gravity on state 10
Alarm and Gravity on state 11 | Gravité d'alarme sur l'état 11 | Alarm and Gravity on state 11 | Alarma y gravedad en estado 11 | Alarme e gravidade em estado 11 | Тревога и важность статуса 11 | Alarm and Gravity on state 11
Alarm and Gravity on state 12 | Gravité d'alarme sur l'état 12 | Alarm and Gravity on state 12 | Alarma y gravedad en estado 12 | Alarme e gravidade em estado 12 | Тревога и важность статуса 12 | Alarm and Gravity on state 12
Alarm and Gravity on state 13 | Gravité d'alarme sur l'état 13 | Alarm and Gravity on state 13 | Alarma y gravedad en estado 13 | Alarme e gravidade em estado 13 | Тревога и важность статуса 13 | Alarm and Gravity on state 13
Alarm and Gravity on state 14 | Gravité d'alarme sur l'état 14 | Alarm and Gravity on state 14 | Alarma y gravedad en estado 14 | Alarme e gravidade em estado 14 | Тревога и важность статуса 14 | Alarm and Gravity on state 14
Alarm and Gravity on state 15 | Gravité d'alarme sur l'état 15 | Alarm and Gravity on state 15 | Alarma y gravedad en estado 15 | Alarme e gravidade em estado 15 | Тревога и важность статуса 15 | Alarm and Gravity on state 15
Alarm and Gravity on Undefined state | Gravité d'alarme sur l'état indéfini | Alarm and Gravity on Undefined state | Alarma y gravedad en estado Indefinido | Alarme e gravidade em estado Indefinido | Тревога и важность статуса Undefined | Alarm and Gravity on Undefined state
Alarm and Gravity on Toggling state | Gravité d'alarme sur l'état de basculement | Alarm and Gravity on Toggling state | Alarma y gravedad en estado en curso | Alarme e gravidade em estado em Curso | Тревога и важность статуса Toggling | Alarm and Gravity on Toggling state
Alarm and Gravity on SelfCheckFault state | Gravité d'alarme sur l'état d'auto vérification du défaut | Alarm and Gravity on SelfCheckFault state | Alarma y gravedad en estado FallaAutoChequeo | Alarme e gravidade em estado FalhaAutoCheque | Тревога и важность статуса SelfCheckFault | Alarm and Gravity on SelfCheckFault state
Alarm and Gravity on Unknown state | Gravité d'alarme sur l'état inconnu | Alarm and Gravity on Unknown state | Alarma y gravedad en estado desconocido | Alarme e gravidade em estado Desconhecido | Тревога и важность статуса Unknown | Alarm and Gravity on Unknown state
Alarm and Gravity on Suppressed state | Gravité d'alarme sur l'état supprimé | Alarm and Gravity on Suppressed state | Alarma y gravedad en estado Suprimido | Alarme e gravidade em estado Suprimido | Тревога и важность статуса Suppressed | Alarm and Gravity on Suppressed state
Alarm and Gravity on Forced state | Gravité d'alarme sur l'état forcé | Alarm and Gravity on Forced state | Alarma y gravedad en estado forzado | Alarme e gravidade em estado Forçado | Тревога и важность статуса Forced | Alarm and Gravity on Forced state
Alarm and Gravity on Substituted state | Gravité d'alarme sur l'état substitué | Alarm and Gravity on Substituted state | Alarma y gravedad en estado Sustituido | Alarme e gravidade em estado Substituído | Тревога и важность статуса Substituted | Alarm and Gravity on Substituted state
Masking due to control | Masqué dû à la commande | Masking due to control | Enmascarar debido al control | Mascarar devido ao controle | Masking due to control | Masking due to control
SBMC dependant | Dépendance SBMC | SBMC dependant | SBMC dependiente | SBMC dependente | SBMC иждивенца | SBMC unterhaltsberechtigte
Suppressed interlock value | Valeur de l'interverrouillage supprimé | Suppressed interlock value | Valor de enclavamiento suprimido | Valor de Intertravamento Suprimido | Значение блокировки Suppressed | Suppressed interlock value
Unknown interlock value | Valeur de l'interverrouillage inconnu | Unknown interlock value | Valor de enclavamiento desconocido | Valor de Intertravamento Desconhecido | Значение блокировки Unknown | Unknown interlock value
Toggling interlock value | Valeur de l'interverrouillage de basculement | Toggling interlock value | Valor de enclavamiento curso | Valor de Intertravamento Curso | Значение блокировки Toggling | Toggling interlock value
SelfCheckFault interlock value | Valeur de l'interverrouillage sur l'auto vérification du défaut | SelfCheckFault interlock value | Valor de enclavamiento FallaAutoChequeo | Valor de Intertravamento FalhaAutoCheque | Значение блокировки SelfCheckFaul | SelfCheckFault interlock value
Undefined interlock value | Valeur de l'interverrouillage indéfini | Undefined interlock value | Valor de enclavamiento indefinido | Valor de Intertravamento Indefinido | Значение блокировки Undefined | Undefined interlock value
Enable FSS (forcing / substituting / suppressing) | Activer le FSS (forçage / substitution / suppression) | Enable FSS (forcing / substituting / suppressing) | Permitir FSS (forcing / substituting / suppressing) | Permitir FSS (forcing / substituting / suppressing) | позволить FSS (forcing / substituting / suppressing) | Enable FSS (forcing / substituting / suppressing)
Single Digital Outputs Profiles | Profils sorties numériques simples (SPC) | Single Digital Outputs Profiles | Perfiles de salidas digitales sencillas | Perfis de saidas Digitais Únicas | Профили одинарных DO | Single Digital Outputs Profiles
Single System Digital Outputs Profiles | Profils sorties numériques systèmes simples (SPC) | Single System Digital Outputs Profiles | Perfiles de systema de salidas digitales sencillas | Perfis de Systema de saidas Digitais Únicas | Профили одинарных системных DO | Single System Digital Outputs Profiles
Function Name | Nom de la fonction | Function Name | Nombre de función | Nome da Função | Функция Name | Function Name
SCE Name (13 char) | Nom dans le SCE (13 char) | SCE Name (13 char) | Nombre SCE (13 caract) | Nome SCE (13 caract) | Имя SCE (13 символов) | SCE Name (13 char)
SPC General Parameters | Paramètres généraux de la SPC | SPC General Parameters | Parámetros generales SPC | Parâmetros Geração SPC | Основные параметры SPC | SPC General Parameters
Activation Mode | Mode d'activation | Activation Mode | Modo de activación | Modo de Ativação | Режим активации | Activation Mode
SBO Mode | Mode de sélection avant opération | SBO Mode | Modo SBO | Modo SBO | Режим SBO | SBO Mode
SBO Timeout [0-600s] | Temps d'expiration pour la sélection avant opération [0-600s] | SBO Timeout [0-600s] | Tiempo fuera SBO [0-600s] | Falha SBO [0-600s] | Задержка SBO [0-600 с] | SBO Timeout [0-600s]
Execution timeout (if any) [0..6000000] (x100ms) | Temps d'expiration de l'exécution (si présent) [0..6000000] (x100ms) | Execution timeout (if any) [0..6000000] (x100ms) | Tiempo fuera de ejecución (si existe) [0..6000000] (x100ms) | Falha de execução (se existe) [0..6000000] (x100ms) | Задержка выполнения (если есть) [0..6000000] (х100 мс) | Execution timeout (if any) [0..6000000] (x100ms)
NACK Alarm Parameters | Paramètres NACK d'alarme | NACK Alarm Parameters | Parámetros de alarmas NACK | Parâmetros de Alarmes NACK | Параметры тревоги NACK | NACK Alarm Parameters
Alarmed on Negative Ack state | Etat de l'alarme sur réception négative | Alarmed on Negative Ack state | Alarmado en estado de adquisición negativo | Alarme em estado de aquisição negativo | Сигнализация на неподтвержденный статус | Alarmed on Negative Ack state
Treatment on Negative Ack state | Etat du Traitement sur réception Négative | Treatment on Negative Ack state | Manipulación en estado adquisición negativo | Manipulação em estado de aquisição negativo | Обработка неподтверденного статуса | Treatment on Negative Ack state
Audible Alarm | Alarme audible | Audible Alarm | Alarma audible | Alarme Auditível | Звуковая тревога | Audible Alarm
Clearing Mode | Mode d'effacement | Clearing Mode | Modo Clearing | Modo de Limpeza | Режим очистки | Clearing Mode
Alarm appearance delay (0-120 s) | Retard d'apparition de l'alarme (0-120 s) | Alarm appearance delay (0-120 s) | Retardo de aparición de Alarma (0-120 s) | Retardo de aparição de Alarme (0-120 s) | Задержка появления тревоги (0-120 с) | Alarm appearance delay (0-120 s)
Usage Parameters | Paramètres d'Utilisation | Usage Parameters | Parámetros del Uso | Parâmetros do Uso | Параметры Usage | Usage Parameters
Off Usage | Valeur "Off" d'utilisation | Off Usage | Valor uso 'Off' | Valor Uso 'Off' | Значение Usage Off | Off Usage
On Usage | Valeur "On" d'utilisation | On Usage | Valor uso 'On' | Valor Uso 'On' | Значения Usage On | On Usage
Interlocking Parameters | Paramètres d'Interverrouillage | Interlocking Parameters | Parámetros de enclavamiento | Parâmetros de Intertravamento | Параметры блокировки | Interlocking Parameters
Off Interlock Value | Valeur "Off" de l'interverrouillage | Off Interlock Value | Valor enclavamiento 'Off' | Valor Intertravamento 'Off' | Значение блокировки Off | Off Interlock Value
On Interlock Value | Valeur "On" de l'interverrouillage | On Interlock Value | Valor enclavamiento 'On' | Valor Intertravamento 'On' | Значение блокировки On | On Interlock Value
Order on duration (ms) | Durée de l'ordre (ms) | Order on duration (ms) | Duración de 'Order on' (ms) | Duração de 'Order on' (ms) | Продолжительность 'Order on' (mc) | Order on duration (ms)
Hold duration (ms) | Durée de maintien (ms) | Hold duration (ms) | Duración de 'Hold' (ms) | Duração de 'Hold' (ms) | Продолжительность 'Hold' (mc) | Hold duration (ms)
SPC Printing Parameters | Paramètres d'impression de la SPC | SPC Printing Parameters | Parámetros de impresión SPC | Parâmetros de Impressão SPC | Параметры печати SPC | SPC Printing Parameters
Printed on Sequence Of Events SOE 1 : | Imprimer sur l'imprimante Fil de l'eau 1 : | Printed on Sequence Of Events SOE 1 : | Impreso en SOE 1 : | Impresso em SOE 1 : | Вывод на SOE 1 : | Printed on Sequence Of Events SOE 1 :
Printed on Sequence Of Events SOE 2 : | Imprimer sur l'imprimante Fil de l'eau 2 : | Printed on Sequence Of Events SOE 2 : | Impreso en SOE 2 : | Impresso em SOE 1 : | Вывод на SOE 2 : | Printed on Sequence Of Events SOE 2 :
Printed on Logbook LB 1 : | Imprimer sur l'imprimante Journal de Bord 1 : | Printed on Logbook LB 1 : | Impreso en LB 1 : | Impresso em LB 1 : | Вывод на LB 1 : | Printed on Logbook LB 1 :
Printed on Logbook LB 2 : | Imprimer sur l'imprimante Journal de Bord 2 : | Printed on Logbook LB 2 : | Impreso en LB 2 : | Impresso em LB 2 : | Вывод на LB 2 : | Printed on Logbook LB 2 :
Default State labels | Valeurs par défaut des Etats électriques | Default State labels | Por defecto las etiquetas de estado | Estado padrão rótulos | По умолчанию состояние этикетки | Default State labels
Default Text at electrical state = 1 (16 char) | Texte par défaut à l'état électrique = 1 (16 car) | Default Text at electrical state = 1 (16 char) | Texto predeterminado en estado eléctrico = 1 (16 caract) | Texto padrão em estado Elétrico = 1 (16 caract) | умолчанию текст электрического состояния = 1 (16 символов) | Default Text at electrical state = 1 (16 char)
Default Text at electrical state = 0 (16 char) | Texte par défaut à l'état électrique = 0 (16 car) | Default Text at electrical state = 0 (16 char) | Texto predeterminado en estado eléctrico = 0 (16 caract) | Texto padrão em estado Elétrico = 0 (16 caract) | умолчанию текст электрического состояния = 0 (16 символов) | Default Text at electrical state = 0 (16 char)
Double Digital Outputs Profiles | Profils des sorties numériques doubles (DPC) | Double Digital Outputs Profiles | Perfiles de salidas digitales dobles | Perfis de saidas Digitais Duplas | Профили двоичных DO | Double Digital Outputs Profiles
Double System Digital Outputs Profiles | Profils des sorties numériques systèmes doubles (DPC) | Double System Digital Outputs Profiles | Perfiles de systema de salidas digitales dobles | Perfis de Systema de saidas Digitais Duplas | Профили двоичных системных DO | Double System Digital Outputs Profiles
Default State labels | Valeurs par défaut des Etats électriques | Default State labels | Por defecto las etiquetas de estado | Estado padrão rótulos | По умолчанию состояние этикетки | Default State labels
Default Text at electrical state = 10 (16 char) | Texte par défaut à l'état électrique = 10 (16 car) | Default Text at electrical state = 10 (16 char) | Texto predeterminado en estado eléctrico = 10 (16 caract) | Texto padrão em estado Elétrico = 10 (16 caract) | умолчанию текст электрического состояния = 10 (16 символов) | Default Text at electrical state = 10 (16 char)
Default Text at electrical state = 01 (16 char) | Texte par défaut à l'état électrique = 01 (16 car) | Default Text at electrical state = 01 (16 char) | Texto predeterminado en estado eléctrico = 01 (16 caract) | Texto padrão em estado Elétrico = 01 (16 caract) | умолчанию текст электрического состояния = 01 (16 символов) | Default Text at electrical state = 01 (16 char)
DPC Printing Parameters | Paramètres d'impression de la DPC | DPC Printing Parameters | Parámetros de impresión DPC | Parâmetros de Impressão DPC | Параметры печати DPC | DPC Printing Parameters
Printed on Sequence Of Events SOE 1 : | Imprimer sur l'imprimante Fil de l'eau 1 : | Printed on Sequence Of Events SOE 1 : | Impreso en SOE 1 : | Impresso em SOE 1 : | Вывод на SOE 1 : | Printed on Sequence Of Events SOE 1 :
Printed on Sequence Of Events SOE 2 : | Imprimer sur l'imprimante Fil de l'eau 2 : | Printed on Sequence Of Events SOE 2 : | Impreso en SOE 2 : | Impresso em SOE 1 : | Вывод на SOE 2 : | Printed on Sequence Of Events SOE 2 :
Printed on Logbook LB 1 : | Imprimer sur l'imprimante Journal de Bord 1 : | Printed on Logbook LB 1 : | Impreso en LB 1 : | Impresso em LB 1 : | Вывод на LB 1 : | Printed on Logbook LB 1 :
Printed on Logbook LB 2 : | Imprimer sur l'imprimante Journal de Bord 2 : | Printed on Logbook LB 2 : | Impreso en LB 2 : | Impresso em LB 2 : | Вывод на LB 2 : | Printed on Logbook LB 2 :
Open duration (ms) | Durée d'ouverture (ms) | Open duration (ms) | Duración de 'Open' (ms) | Duração de 'Open' (ms) | Продолжительность 'Open' (mc) | Open duration (ms)
Close duration (ms) | Durée de fermeture (ms) | Close duration (ms) | Duración de 'Close' (ms) | Duração de 'Close' (ms) | Продолжительность 'Close' (mc) | Close duration (ms)
Hold duration (ms) | Durée de maintien (ms) | Hold duration (ms) | Duración de 'Hold' (ms) | Duração de 'Hold' (ms) | Продолжительность 'Hold' (mc) | Hold duration (ms)
Usage Parameters | Paramètres d'Utilisation | Usage Parameters | Parámetros del Uso | Parâmetros do Uso | Параметры Usage | Usage Parameters
Open Usage 01 | Valeur "Ouvert" d'utilisation 01 | Open Usage 01 | Valor uso 'Open' 01 | Valor Uso 'Open' 01 | Значение Usage 'Open' 01 | Open Usage 01
Close Usage 10 | Valeur "Fermé" d'utilisation 10 | Close Usage 10 | Valor uso 'Close' 10 | Valor Uso 'Close' 10 | Значения Usage 'Close' 10 | Close Usage 10
Interlocking Parameters | Paramètres d'Interverrouillage | Interlocking Parameters | Parámetros de enclavamiento | Parâmetros de Intertravamento | Параметры блокировки | Interlocking Parameters
Open Interlock Value 01 | Valeur "Ouvert" de l'interverrouillage 01 | Open Interlock Value 01 | Valor enclavamiento 'Open' 01 | Valor Intertravamento 'Open' 01 | Значение блокировки 'Open' 01 | Open Interlock Value 01
Close Interlock Value 10 | Valeur "Fermé" de l'interverrouillage 10 | Close Interlock Value 10 | Valor enclavamiento 'Close' 10 | Valor Intertravamento 'Close' 10 | Значение блокировки 'Close' 10 | Close Interlock Value 10
Function Name | Nom de la fonction | Function Name | Nombre de función | Nome da Função | Функция Name | Function Name
SCE Name (13 char) | Nom dans le SCE (13 char) | SCE Name (13 char) | Nombre SCE (13 caract) | Nome SCE (13 caract) | Имя SCE (13 символов) | SCE Name (13 char)
DPC General Parameters | Paramètres généraux de la DPC | DPC General Parameters | Parámetros generales DPC | Parâmetros Geração DPC | Основные параметры DPC | DPC General Parameters
Activation Mode | Mode d'activation | Activation Mode | Modo de activación | Modo de Ativação | Режим активации | Activation Mode
SBO Mode | Mode de sélection avant opération | SBO Mode | Modo SBO | Modo SBO | Режим SBO | SBO Mode
SBO Timeout [0-600s] | Temps d'expiration pour la sélection avant opération [0-600s] | SBO Timeout [0-600s] | Tiempo fuera SBO [0-600s] | Falha SBO [0-600s] | Задержка SBO [0-600 с] | SBO Timeout [0-600s]
Execution timeout (if any) [0..6000000] (x100ms) | Temps d'expiration de l'exécution (si présent) [0..6000000] (x100ms) | Execution timeout (if any) [0..6000000] (x100ms) | Tiempo fuera de ejecución (si existe) [0..6000000] (x100ms) | Falha de execução (se existe) [0..6000000] (x100ms) | Задержка выполнения (если есть) [0..6000000] (х100 мс) | Execution timeout (if any) [0..6000000] (x100ms)
NACK Alarm Parameters | Paramètres NACK d'alarme | NACK Alarm Parameters | Parámetros de alarmas NACK | Parâmetros de Alarmes NACK | Параметры тревоги NACK | NACK Alarm Parameters
Alarmed on Negative Ack state | Etat de l'alarme sur réception négative | Alarmed on Negative Ack state | Alarmado en estado de adquisición negativo | Alarme em estado de aquisição negativo | Сигнализация на неподтвержденный статус | Alarmed on Negative Ack state
Treatment on Negative Ack state | Etat du Traitement sur réception Négative | Treatment on Negative Ack state | Manipulación en estado adquisición negativo | Manipulação em estado de aquisição negativo | Обработка неподтверденного статуса | Treatment on Negative Ack state
Audible Alarm | Alarme audible | Audible Alarm | Alarma audible | Alarme Auditível | Звуковая тревога | Audible Alarm
Clearing Mode | Mode d'effacement | Clearing Mode | Modo Clearing | Modo de Limpeza | Режим очистки | Clearing Mode
Alarm appearance delay (0-120 s) | Retard d'apparition de l'alarme (0-120 s) | Alarm appearance delay (0-120 s) | Retardo de aparición de Alarma (0-120 s) | Retardo de aparição de Alarme (0-120 s) | Задержка появления тревоги (0-120 с) | Alarm appearance delay (0-120 s)
System SetPoint Profiles | Profils SetPoint systèmes | System SetPoint Profiles | Perfiles de systema de SetPoint | Perfis de Systema de SetPoint | Профили системных SetPoint | System SetPoint Profiles
SetPoint Profiles | Profils SetPoint | SetPoint Profiles | Perfiles de SetPoint | Perfis de SetPoint | Профили SetPoint | SetPoint Profiles
SetPoint Printing Parameters | Paramètres d'impression de la SetPoint | SetPoint Printing Parameters | Parámetros de impresión SetPoint | Parâmetros de Impressão SetPoint | Параметры печати SetPoint | SetPoint Printing Parameters
Function Name | Nom de la fonction | Function Name | Nombre de función | Nome da Função | Функция Name | Function Name
SCE Name (13 char) | Nom dans le SCE (13 char) | SCE Name (13 char) | Nombre SCE (13 caract) | Nome SCE (13 caract) | Имя SCE (13 символов) | SCE Name (13 char)
SetPoint General Parameters | Paramètres généraux du SetPoint | SetPoint General Parameters | Parámetros generales SetPoint | Parâmetros Geração SetPoint | Основные параметры SetPoint | SetPoint General Parameters
Activation Mode | Mode d'activation | Activation Mode | Modo de activación | Modo de Ativação | Режим активации | Activation Mode
SBO Mode | Mode de sélection avant opération | SBO Mode | Modo SBO | Modo SBO | Режим SBO | SBO Mode
SBO Timeout [0-600s] | Temps d'expiration pour la sélection avant opération [0-600s] | SBO Timeout [0-600s] | Tiempo fuera SBO [0-600s] | Falha SBO [0-600s] | Задержка SBO [0-600 с] | SBO Timeout [0-600s]
Execution timeout (if any) [0..6000000] (x100ms) | Temps d'expiration de l'exécution (si présent) [0..6000000] (x100ms) | Execution timeout (if any) [0..6000000] (x100ms) | Tiempo fuera de ejecución (si existe) [0..6000000] (x100ms) | Falha de execução (se existe) [0..6000000] (x100ms) | Задержка выполнения (если есть) [0..6000000] (х100 мс) | Execution timeout (if any) [0..6000000] (x100ms)
NACK Alarm Parameters | Paramètres NACK d'alarme | NACK Alarm Parameters | Parámetros de alarmas NACK | Parâmetros de Alarmes NACK | Параметры тревоги NACK | NACK Alarm Parameters
Alarmed on Negative Ack state | Etat de l'alarme sur réception négative | Alarmed on Negative Ack state | Alarmado en estado de adquisición negativo | Alarme em estado de aquisição negativo | Сигнализация на неподтвержденный статус | Alarmed on Negative Ack state
Treatment on Negative Ack state | Etat du Traitement sur réception Négative | Treatment on Negative Ack state | Manipulación en estado adquisición negativo | Manipulação em estado de aquisição negativo | Обработка неподтверденного статуса | Treatment on Negative Ack state
Audible Alarm | Alarme audible | Audible Alarm | Alarma audible | Alarme Auditível | Звуковая тревога | Audible Alarm
Clearing Mode | Mode d'effacement | Clearing Mode | Modo Clearing | Modo de Limpeza | Режим очистки | Clearing Mode
Alarm appearance delay (0-120 s) | Retard d'apparition de l'alarme (0-120 s) | Alarm appearance delay (0-120 s) | Retardo de aparición de Alarma (0-120 s) | Retardo de aparição de Alarme (0-120 s) | Задержка появления тревоги (0-120 с) | Alarm appearance delay (0-120 s)
Printed on Logbook LB 1 : | Imprimer sur l'imprimante Journal de Bord 1 : | Printed on Logbook LB 1 : | Impreso en LB 1 : | Impresso em LB 1 : | Вывод на LB 1 : | Printed on Logbook LB 1 :
Printed on Logbook LB 2 : | Imprimer sur l'imprimante Journal de Bord 2 : | Printed on Logbook LB 2 : | Impreso en LB 2 : | Impresso em LB 2 : | Вывод на LB 2 : | Printed on Logbook LB 2 :
Measurement Profiles | Profils analogiques | Measurement Profiles | Perfiles de mediciones | Perfis de Medições | Профили измерений | Measurement Profiles
Measurement System Profiles | Profils systèmes analogiques | Measurement System Profiles | Perfiles de systema de mediciones | Perfis de Systema de Medições | Профили системных измерений | Measurement System Profiles
Function Name | Nom de la fonction | Function Name | Nombre de función | Nome da Função | Функция Name | Function Name
SCE Name (13 char) | Nom dans le SCE (13 char) | SCE Name (13 char) | Nombre SCE (13 caract) | Nome SCE (13 caract) | Имя SCE (13 символов) | SCE Name (13 char)
MV General Parameters | Paramètres généraux de la MV | MV General Parameters | Parámetros generales MV | Parâmetros Geração MV | Основные параметры MV | MV General Parameters
Number of decimal for display [0-4] | Nombre de décimales pour l'affichage [0-4] | Number of decimal for display [0-4] | Número de decimales para pantalla [0-4] | Número de decimaoes para Display [0-4] | Количество цифр на дисплее [0-4] | Number of decimal for display [0-4]
Short Acquisition period (ms) [100 … 1000] step 100 | Période d'acquisition courte (ms) [100 … 1000] pas de 100 | Short Acquisition period (ms) [100 … 1000] step 100 | Periodo de adquisición corto (ms) [100 … 1000] escalón 100 | Periodo de aquisição Curto (ms) [100 … 1000] Escala 100 | Короткий период опроса (мс) [100 … 1000] с шагом 100 | Short Acquisition period (ms) [100 … 1000] step 100
Long Acquisition period (ms) [500 … 10000] step 500 | Période d'acquisition longue (ms) [500 … 10000] pas de 500 | Long Acquisition period (ms) [500 … 10000] step 500 | Periodo de adquisición largo (ms) [500 … 10000] escalón 500 | Periodo de aquisição Longo (ms) [500 … 10000] Escala 500 | Длинный период опроса (мс) [500 … 10000] с шагом 500 | Long Acquisition period (ms) [500 … 10000] step 500
3rd Low Threshold (no or % of full scale) | 3eme seuil bas (non ou % de la pleine échelle) | 3rd Low Threshold (no or % of full scale) | 3er Umbral bajo (no o % de la escala completa) | 3ro Limite Baixo (Nãoo % da escala completa) | Третий нижний предел (отсутствует или % от полной шкалы) | 3rd Low Threshold (no or % der Skalenendwerts)
2nd Low Threshold (no or % of full scale) | 2eme seuil bas (non ou % de la pleine échelle) | 2nd Low Threshold (no or % of full scale) | 2do Umbral bajo (no o % de la escala completa) | 2do Limite Baixo (Nãoo % da escala completa) | Второй нижний предел (отсутствует или % от полной шкалы) | 2nd Low Threshold (no or % der Skalenendwerts)
1st Low Threshold (no or % of full scale) | 1er seuil bas (non ou % de la pleine échelle) | 1st Low Threshold (no or % of full scale) | 1er Umbral bajo (no o % de la escala completa) | 1ro Limite Baixo (Nãoo % da escala completa) | Первый нижний предел (отсутствует или % от полной шкалы) | 1st Low Threshold (no or % der Skalenendwerts)
1st High Threshold (no or % of full scale) | 1er seuil haut (non ou % de la pleine échelle) | 1st High Threshold (no or % of full scale) | 1er Umbral alto (no o % de la escala completa) | 1ro Limite Alto (Nãoo % da escala completa) | Первый верхний предел (отсутствует или % от полной шкалы) | 1st High Threshold (no or % der Skalenendwerts)
2nd High Threshold (no or % of full scale) | 2em seuil haut (non ou % de la pleine échelle) | 2nd High Threshold (no or % of full scale) | 2do Umbral alto (no o % de la escala completa) | 2do Limite Alto (Nãoo % da escala completa) | Второй верхний предел (отсутствует или % от полной шкалы) | 2nd High Threshold (no or % der Skalenendwerts)
3rd High Threshold (no or % of full scale) | 3eme seuil haut(non ou % de la pleine échelle) | 3rd High Threshold (no or % of full scale) | 3er Umbral alto (no o % de la escala completa) | 3ro Limite Alto (Nãoo % da escala completa) | Третий верхний предел (отсутствует или % от полной шкалы) | 3rd High Threshold (no or % der Skalenendwerts)
Scaling | Graduation | Scaling | Escala | Graduação | Шкалирование | Scaling
Number of Slopes [1-20] | Nombres de pentes [1-20] | Number of Slopes [1-20] | Número de escalones [1-20] | Número de Escala [1-20] | Количество кривых c разным наклоном [1-20] | Number of Slopes [1-20]
Associated Alarm Parameters | Paramètres d'alarme associés à la MV | Associated Alarm Parameters | Associated Alarm Parameters | Associated aoarm Parameters | Параметры тревоги | Associated Alarm Parameters
Generation Condition | Condition de la Génération | Generation Condition | Condición de generación | Condição de Geração | Основное условие | Generation Condition
Audible Alarm | Alarme audible | Audible Alarm | Alarma audible | Alarme Auditível | Звуковая тревога | Audible Alarm
Clearing Mode | Mode d'effacement | Clearing Mode | Modo Clearing | Modo de Limpeza | Режим очистки | Clearing Mode
Alarm appearance delay (0-120 s) | Retard d'apparition de l'alarme (0-120 s) | Alarm appearance delay (0-120 s) | Retardo de aparición de Alarma (0-120 s) | Retardo de aparição de Alarme (0-120 s) | Задержка появления тревоги (0-120 с) | Alarm appearance delay (0-120 s)
MV Processing Parameters | Paramètres de traitement de la MV | MV Processing Parameters | Parámetros de procesamiento MV | Parâmetros de Processamento MV | Пораметры обработки MV | MV Processing Parameters
Valid state label | Libellé de l'état valide | Valid state label | Etiqueta de estado válido | Etiqueta de estado válido | Метка статуса Valid | Valid state label
SelfCheckFault state label | Libellé de l'état d'auto vérification du défaut | SelfCheckFault state label | Etiqueta de estado FallaAutoChequeo | Etiqueta de estado FalhaAutoCheque | Метка статуса SelfCheckFault | SelfCheckFault state label
Unknown state label | Libellé de l'état inconnu | Unknown state label | Etiqueta de estado desconocido | Etiqueta de estado Desconhecido | Метка статуса Unknown | Unknown state label
Suppressed state label | Libellé de l'état supprimé | Suppressed state label | Etiqueta de estado suprimido | Etiqueta de estado Suprimido | Метка статуса Suppressed | Suppressed state label
Forced state label | Libellé de l'état forcé | Forced state label | Etiqueta de estado forzado | Etiqueta de estado Forçado | Метка статуса Forced | Forced state label
Substituted state label | Libellé de l'état substitué | Substituted state label | Etiqueta de estado sustituido | Etiqueta de estado Substituído | Метка статуса Substituted | Substituted state label
OverRange state label | Libellé de l'état au-dessus de l'échelle | OverRange state label | Etiqueta de estado fuera de rango | Etiqueta de estado fora de Range | Метка статуса OverRange | OverRange state label
Undefined state label | Libellé de l'état indéfini | Undefined state label | Etiqueta de estado Indefinido | Etiqueta de estado Indefinido | Метка статуса Undefined | Undefined state label
OpenCircuit state label | Libellé de l'état circuit ouvert | OpenCircuit state label | Etiqueta de estado circuito abierto | Etiqueta de estado circuito Aberto | Метка статуса OpenCircuit | OpenCircuit state label
LLL Threshold state label | Libellé de l'état seuil LLL | LLL Threshold state label | Etiqueta de estado umbral LLL | Etiqueta de estado Limite LLL | Метка статуса LLL Threshold | LLL Threshold state label
LL Threshold state label | Libellé de l'état seuil LL | LL Threshold state label | Etiqueta de estado umbral LL | Etiqueta de estado Limite LL | Метка статуса LL Threshold | LL Threshold state label
L Threshold state label | Libellé de l'état seuil L | L Threshold state label | Etiqueta de estado umbral L | Etiqueta de estado Limite L | Метка статуса L Threshold | L Threshold state label
H Threshold state label | Libellé de l'état seuil H | H Threshold state label | Etiqueta de estado umbral H | Etiqueta de estado Limite H | Метка статуса H Threshold | H Threshold state label
HH Threshold state label | Libellé de l'état seuil HH | HH Threshold state label | Etiqueta de estado umbral HH | Etiqueta de estado Limite HH | Метка статуса HH Threshold | HH Threshold state label
HHH Threshold state label | Libellé de l'état seuil HHH | HHH Threshold state label | Etiqueta de estado umbral HHH | Etiqueta de estado Limite HHH | Метка статуса HHH Threshold | HHH Threshold state label
Treatment on Valid state | Traitement sur l'état valide | Treatment on Valid state | Manipulación en estado válido | Manipulação em estado válido | Обработка статуса Valid | Treatment on Valid state
Treatment on SelfCheckFault state | Traitement sur l'état d'auto vérification du défaut | Treatment on SelfCheckFault state | Manipulación en estado FallaAutoChequeo | Manipulação em estado FalhaAutoCheque | Обработка статуса SelfCheckFault | Treatment on SelfCheckFault state
Treatment on Unknown state | Traitement sur l'état inconnu | Treatment on Unknown state | Manipulación en estado Desconocido | Manipulação em estado Desconhecido | Обрабока статуса Unknown | Treatment on Unknown state
Treatment on Suppressed state | Traitement sur l'état supprimé | Treatment on Suppressed state | Manipulación en estado Suprimido | Manipulação em estado Suprimido | Обработка статуса Suppressed | Treatment on Suppressed state
Treatment on Forced state | Traitement sur l'état forcé | Treatment on Forced state | Manipulación en estado Forzado | Manipulação em estado Forçado | Обработка статуса Forced | Treatment on Forced state
Treatment on Substituted state | Traitement sur l'état substitué | Treatment on Substituted state | Manipulación en estado sustituido | Manipulação em estado Substituído | Обработка статуса Substituted | Treatment on Substituted state
Treatment on OverRange state | Traitement sur l'état au-dessus de l'échelle | Treatment on OverRange state | Manipulación en estado fuera de rango | Manipulação em estado fora de Range | Обработка статуса OverRange | Treatment on OverRange state
Treatment on Undefined state | Traitement sur l'état indéfini | Treatment on Undefined state | Manipulación en estado Indefinido | Manipulação em estado Indefinido | Обработка статуса Undefined | Treatment on Undefined state
Treatment on OpenCircuit state | Traitement sur l'état circuit ouvert | Treatment on OpenCircuit state | Manipulación de estado en Circuito Abierto | Manipulação de estado em Circuito Aberto | Обработка статуса OpenCircuit | Treatment on OpenCircuit state
Treatment on LLL Threshold state | Traitement sur l'état LLL seuil | Treatment on LLL Threshold state | Manipualción de estado en umbral LLL | Manipuaoción de estado em Limite LLL | Обработка статуса LLL Threshold | Treatment on LLL Threshold state
Treatment on LL Threshold state | Traitement sur l'état LL seuil | Treatment on LL Threshold state | Manipulación de estado en umbral LL | Manipulação de estado em Limite LL | Обработка статуса LL Threshold | Treatment on LL Threshold state
Treatment on L Threshold state | Traitement sur l'état L seuil | Treatment on L Threshold state | Manipulación de estado en umbral L | Manipulação de estado em Limite L | Обработка статуса L Threshold | Treatment on L Threshold state
Treatment on H Threshold state | Traitement sur l'état H seuil | Treatment on H Threshold state | Manipulación de estado en umbral H | Manipulação de estado em Limite H | Обработка статуса Н Threshold | Treatment on H Threshold state
Treatment on HH Threshold state | Traitement sur l'état HH seuil | Treatment on HH Threshold state | Manipulación de estado en umbral HH | Manipulação de estado em Limite HH | Обработка статуса HH Threshold | Treatment on HH Threshold state
Treatment on HHH Threshold state | Traitement sur l'état HHH seuil | Treatment on HHH Threshold state | Manipulación de estado en umbral HHH | Manipulação de estado em Limite HHH | Обработка статуса HHH Threshold | Treatment on HHH Threshold state
Valid interlock value | Valeur de l'interverrouillage valide | Valid interlock value | Valor de enclavamiento válido | Valor de Intertravamento válido | Значение блокировки Valid | Valid interlock value
SelfCheckFault interlock value | Valeur de l'interverrouillage sur l'auto vérification du défaut | SelfCheckFault interlock value | Valor de enclavamiento FallaAutoChequeo | Valor de Intertravamento FalhaAutoCheque | Значение блокировки SelfCheckFaul | SelfCheckFault interlock value
Unknown interlock value | Valeur de l'interverrouillage inconnu | Unknown interlock value | Valor de enclavamiento desconocido | Valor de Intertravamento Desconhecido | Значение блокировки Unknown | Unknown interlock value
Suppressed interlock value | Valeur de l'interverrouillage supprimé | Suppressed interlock value | Valor de enclavamiento suprimido | Valor de Intertravamento Suprimido | Значение блокировки Suppressed | Suppressed interlock value
Forced interlock value | Valeur de l'interverrouillage forcé | Forced interlock value | Valor de enclavamiento forzado | Valor de Intertravamento Forçado | Значение блокировки Forced | Forced interlock value
Substituted interlock value | Valeur de l'interverrouillage substitué | Substituted interlock value | Valor de enclavamiento sustituido | Valor de Intertravamento Substituído | Значение блокировки Substituted | Substituted interlock value
OverRange interlock value | Valeur de l'interverrouillage au-dessus de l'échelle | OverRange interlock value | Valor de enclavamiento fuera de rango | Valor de Intertravamento fora de Range | Значение блокировки OverRange | OverRange interlock value
Undefined interlock value | Valeur de l'interverrouillage indéfini | Undefined interlock value | Valor de enclavamiento indefinido | Valor de Intertravamento Indefinido | Значение блокировки Undefined | Undefined interlock value
OpenCircuit interlock value | Valeur de l'interverrouillage circuit ouvert | OpenCircuit interlock value | Valor de enclavamiento Circuito Abierto | Valor de Intertravamento Circuito Aberto | Значение блокировки OpenCircuit | OpenCircuit interlock value
LLL Threshold interlock value | Valeur de l'interverrouillage seuil LLL | LLL Threshold interlock value | Valor de enclavamiento umbral LLL | Valor de Intertravamento Limite LLL | Значение блокировки LLL Threshold | LLL Threshold interlock value
LL Threshold interlock value | Valeur de l'interverrouillage seuil LL | LL Threshold interlock value | Valor de enclavamiento umbral LL | Valor de Intertravamento Limite LL | Значение блокировки LL Threshold | LL Threshold interlock value
L Threshold interlock value | Valeur de l'interverrouillage seuil L | L Threshold interlock value | Valor de enclavamiento umbral L | Valor de Intertravamento Limite L | Значение блокировки L Threshold | L Threshold interlock value
H Threshold interlock value | Valeur de l'interverrouillage seuil H | H Threshold interlock value | Valor de enclavamiento umbral H | Valor de Intertravamento Limite H | Значение блокировки H Threshold | H Threshold interlock value
HH Threshold interlock value | Valeur de l'interverrouillage seuil HH | HH Threshold interlock value | Valor de enclavamiento umbral HH | Valor de Intertravamento Limite HH | Значение блокировки HH Threshold | HH Threshold interlock value
HHH Threshold interlock value | Valeur de l'interverrouillage seuil HHH | HHH Threshold interlock value | Valor de enclavamiento umbral HHH | Valor de Intertravamento Limite HHH | Значение блокировки HHH Threshold | HHH Threshold interlock value
Alarm and Gravity on Valid state | Gravité d'alarme sur l'état valide | Alarm and Gravity on Valid state | Alarma y gravedad en estado valido | Alarme e gravidade em estado vaoido | Тревога и важность статуса Valid | Alarm and Gravity on Valid state
Alarm and Gravity on SelfCheckFault state | Gravité d'alarme sur l'état d'auto vérification du défaut | Alarm and Gravity on SelfCheckFault state | Alarma y gravedad en estado FallaAutoChequeo | Alarme e gravidade em estado FalhaAutoCheque | Тревога и важность статуса SelfCheckFault | Alarm and Gravity on SelfCheckFault state
Alarm and Gravity on Unknown state | Gravité d'alarme sur l'état inconnu | Alarm and Gravity on Unknown state | Alarma y gravedad en estado desconocido | Alarme e gravidade em estado Desconhecido | Тревога и важность статуса Unknown | Alarm and Gravity on Unknown state
Alarm and Gravity on Suppressed state | Gravité d'alarme sur l'état supprimé | Alarm and Gravity on Suppressed state | Alarma y gravedad en estado Suprimido | Alarme e gravidade em estado Suprimido | Тревога и важность статуса Suppressed | Alarm and Gravity on Suppressed state
Alarm and Gravity on Forced state | Gravité d'alarme sur l'état forcé | Alarm and Gravity on Forced state | Alarma y gravedad en estado forzado | Alarme e gravidade em estado Forçado | Тревога и важность статуса Forced | Alarm and Gravity on Forced state
Alarm and Gravity on Substituted state | Gravité d'alarme sur l'état substitué | Alarm and Gravity on Substituted state | Alarma y gravedad en estado Sustituido | Alarme e gravidade em estado Substituído | Тревога и важность статуса Substituted | Alarm and Gravity on Substituted state
Alarm and Gravity on OverRange state | Gravité d'alarme sur l'état au-dessus de l'échelle | Alarm and Gravity on OverRange state | Alarma y gravedad en estado fuera de rango | Alarme e gravidade em estado fora de Range | Тревога и важность статуса OverRange | Alarm and Gravity on OverRange state
Alarm and Gravity on Undefined state | Gravité d'alarme sur l'état indéfini | Alarm and Gravity on Undefined state | Alarma y gravedad en estado Indefinido | Alarme e gravidade em estado Indefinido | Тревога и важность статуса Undefined | Alarm and Gravity on Undefined state
Alarm and Gravity on OpenCircuit state | Gravité d'alarme sur l'état circuit ouvert | Alarm and Gravity on OpenCircuit state | Alarma y gravedad en estado circuito abierto | Alarme e gravidade em estado Circuito Aberto | Тревога и важность статуса OpenCircuit | Alarm and Gravity on OpenCircuit state
Alarm and Gravity on LLL Threshold state | Gravité d'alarme sur l'état de seuil LLL | Alarm and Gravity on LLL Threshold state | Alarma y gravedad en estado umbral LLL | Alarme e gravidade em estado Limite LLL | Тревога и важность статуса LLL Threshold | Alarm and Gravity on LLL Threshold state
Alarm and Gravity on LL Threshold state | Gravité d'alarme sur l'état de seuil LL | Alarm and Gravity on LL Threshold state | Alarma y gravedad en estado umbral LL | Alarme e gravidade em estado Limite LL | Тревога и важность статуса LL Threshold | Alarm and Gravity on LL Threshold state
Alarm and Gravity on L Threshold state | Gravité d'alarme sur l'état de seuil L | Alarm and Gravity on L Threshold state | Alarma y gravedad en estado umbral L | Alarme e gravidade em estado Limite L | Тревога и важность статуса L Threshold | Alarm and Gravity on L Threshold state
Alarm and Gravity on H Threshold state | Gravité d'alarme sur l'état de seuil H | Alarm and Gravity on H Threshold state | Alarma y gravedad en estado umbral H | Alarme e gravidade em estado Limite H | Тревога и важность статуса H Threshold | Alarm and Gravity on H Threshold state
Alarm and Gravity on HH Threshold state | Gravité d'alarme sur l'état de seuil HH | Alarm and Gravity on HH Threshold state | Alarma y gravedad en estado umbral HH | Alarme e gravidade em estado Limite HH | Тревога и важность статуса HH Threshold | Alarm and Gravity on HH Threshold state
Alarm and Gravity on HHH Threshold state | Gravité d'alarme sur l'état de seuil HHH | Alarm and Gravity on HHH Threshold state | Alarma y gravedad en estado umbral HHH | Alarme e gravidade em estado Limite HHH | Тревога и важность статуса HHH Threshold | Alarm and Gravity on HHH Threshold state
Computation | Calculé | Computation | Cómputación | Computação | Вычисление | Computation
SBMC dependant | Dépendance SBMC | SBMC dependant | SBMC dependiente | SBMC dependente | SBMC иждивенца | SBMC unterhaltsberechtigte
Graphical Default Format | Format graphique par défaut | Graphical Default Format | Formato gráfico del defecto | Formato gráfico do defeito | Стандартный графический формат | Graphical Default Format
Transmission on Event | Transmission sur événement | Transmission on Event | Transmisión en acontecimiento | Transmissão no evento | Передача события | Transmission on Event
Deadband | Bande morte | Deadband | Venda muerta | Faixa muerta | Порог чувствительности | Deadband
MV Printing Parameters | Paramètres d'impression de la MV | MV Printing Parameters | Parámetros de impresión MV | Parâmetros de Impressão MV | Параметры печати MV | MV Printing Parameters
Printed on Logbook LB 1 : | Imprimer sur l'imprimante Journal de Bord 1 : | Printed on Logbook LB 1 : | Impreso en LB 1 : | Impresso em LB 1 : | Вывод на LB 1 : | Printed on Logbook LB 1 :
Printed on Logbook LB 2 : | Imprimer sur l'imprimante Journal de Bord 2 : | Printed on Logbook LB 2 : | Impreso en LB 2 : | Impresso em LB 2 : | Вывод на LB 2 : | Printed on Logbook LB 2 :
Enable FSS (forcing / substituting / suppressing) | Activer le FSS (forçage / substitution / suppression) | Enable FSS (forcing / substituting / suppressing) | Permitir FSS (forcing / substituting / suppressing) | Permitir FSS (forcing / substituting / suppressing) | позволить FSS (forcing / substituting / suppressing) | Enable FSS (forcing / substituting / suppressing)
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : System Information | SHEET : Informations Systemes | SHEET : System Information | SHEET : System Information | SHEET : System Information | SHEET : Системная информация | SHEET : System Information
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
SYSTEM INFORMATION DATA DESCRIPTION | INFORMATION SYSTEME DESCRIPTION | SYSTEM INFORMATION DATA DESCRIPTION | SYSTEM INFORMATION DATA DESCRIPTION | SYSTEM INFORMATION DATA DESCRIPTION | ОПИСАНИЕ СИСТЕМНОЙ ИНФОРМАЦИИ | SYSTEM INFORMATION DATA DESCRIPTION
Gateway | Passerelle | Gateway | UTR | UTR | Шлюз | Gateway
Port used (on gateway) | Ports utilisés (sur la passerelle) | Port used (on gateway) | Puerto utilizado (en UTR) | Porta utilizada (em UTR) | Используемый порт (на шлюз) | benutzter Port (Gateway)
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
SCADA 1 | SCADA 1 | SCADA 1 | SCADA 1 | SCADA 1 | SCADA 1 | SCADA 1
GE Reserved | Réservé à GE | GE Grid | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
SCADA 2 | SCADA 2 | SCADA 2 | SCADA 2 | SCADA 2 | SCADA 2 | SCADA 2
Auto generated | Génération automatique | Auto generated | Auto generado | Auto Geração | Автоматически сгенерировано | Auto generated
SCADA 3 | SCADA 3 | SCADA 3 | SCADA 3 | SCADA 3 | SCADA 3 | SCADA 3
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
SCADA 4 | SCADA 4 | SCADA 4 | SCADA 4 | SCADA 4 | SCADA 4 | SCADA 4
SYSTEM INFORMATION DATA DESCRIPTION | INFORMATION SYSTEME DESCRIPTION | SYSTEM INFORMATION DATA DESCRIPTION | SYSTEM INFORMATION DATA DESCRIPTION | SYSTEM INFORMATION DATA DESCRIPTION | ОПИСАНИЕ СИСТЕМНОЙ ИНФОРМАЦИИ | SYSTEM INFORMATION DATA DESCRIPTION
BAY OI Name : | Nom de la BAIE OI : | BAY OI Name : | BAY OI Name : | BAY OI Name : | Имя BAY OI : | BAY OI Name :
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels / States | Libellés/Etats | Labels / States | Etiquetas/Estados | Etiquetas/Estados | Метки / Состояния | Labels / States
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Groups | Groupes | Groups | Grupos | Grupos | Группы | Gruppen
Local Display | Affichage Local | Local Display | Despliegue Local | Display Local | Локальный дисплей | Local Display
HMI | HMI | HMI | IHM | IHM | HMI | HMI
Special | Spécial | Special | Especial | Especial | Специальный | Special
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC 61850 Name : | Nom de l'IEC 61850 : | IEC 61850 Name : | IEC 61850 Name : | IEC 61850 Name : | Имя IEC 61850 : | IEC 61850 Name :
UCA2 IED Name : | Nom de l'UCA2 IED : | UCA2 IED Name : | UCA2 IED Name : | UCA2 IED Name : | Имя UCA2 IED : | UCA2 IED Name :
SERVER OI Name : | Nom du SERVEUR d'E/S : | SERVER OI Name : | SERVER OI Name : | SERVER OI Name : | Имя сервера OI : | SERVER OI Name :
CLIENT OI Name : | Nom du CLIENT d'E/S : | CLIENT OI Name : | CLIENT OI Name : | CLIENT OI Name : | Имя клиента OI : | CLIENT OI Name :
MiCOM C264 Name : | Nom du MiCOM C264 : | MiCOM C264 Name : | MiCOM C264 Name : | MiCOM C264 Name : | Имя MiCOM C264 : | MiCOM C264 Name :
GATEWAY Name : | Nom de la PASSERELLE : | GATEWAY Name : | GATEWAY Name : | GATEWAY Name : | Имя шлюза : | GATEWAY Name :
MiCOM C364 Name : | Nom du MiCOM C364 : | MiCOM C364 Name : | MiCOM C364 Name : | MiCOM C364 Name : | Имя MiCOM C364 : | MiCOM C364 Name :
SYSTEM INFORMATION GATEWAY | INFORMATION SYSTEME PASSERELLE | SYSTEM INFORMATION GATEWAY | SYSTEM INFORMATION GATEWAY | SYSTEM INFORMATION GATEWAY | СИСТЕМНАЯ ИНФОРМАЦИЯ ПО ШЛЮЗУ | SYSTEM INFORMATION GATEWAY
SYSTEM INFORMATION MiCOM C264 | INFORMATION SYSTEME MiCOM C264 | SYSTEM INFORMATION MiCOM C264 | SYSTEM INFORMATION MiCOM C264 | SYSTEM INFORMATION MiCOM C264 | СИСТЕМНАЯ ИНФОРМАЦИЯ ПО MiCOM C264 | SYSTEM INFORMATION MiCOM C264
SYSTEM INFORMATION MiCOM C364 | INFORMATION SYSTEME MiCOM C364 | SYSTEM INFORMATION MiCOM C364 | SYSTEM INFORMATION MiCOM C364 | SYSTEM INFORMATION MiCOM C364 | СИСТЕМНАЯ ИНФОРМАЦИЯ ПО MiCOM C364 | SYSTEM INFORMATION MiCOM C364
SYSTEM INFORMATION CLIENT OI | INFORMATION SYSTEME CLIENT E/S | SYSTEM INFORMATION CLIENT OI | SYSTEM INFORMATION CLIENT OI | SYSTEM INFORMATION CLIENT OI | СИСТЕМНАЯ ИНФОРМАЦИЯ ПО КЛИЕНТУ OI | SYSTEM INFORMATION CLIENT OI
SYSTEM INFORMATION SERVER OI | INFORMATION SYSTEME SERVER E/S | SYSTEM INFORMATION SERVER OI | SYSTEM INFORMATION SERVER OI | SYSTEM INFORMATION SERVER OI | СИСТЕМНАЯ ИНФОРМАЦИЯ ПО СЕРВЕРУ OI | SYSTEM INFORMATION SERVER OI
SYSTEM INFORMATION UCA2 IED | INFORMATION SYSTEME UCA2 IED | SYSTEM INFORMATION UCA2 IED | SYSTEM INFORMATION UCA2 IED | SYSTEM INFORMATION UCA2 IED | СИСТЕМНАЯ ИНФОРМАЦИЯ ПО UCA2 IED | SYSTEM INFORMATION UCA2 IED
SYSTEM INFORMATION IEC 61850 | INFORMATION SYSTEME IEC 61850 | SYSTEM INFORMATION IEC 61850 | SYSTEM INFORMATION IEC 61850 | SYSTEM INFORMATION IEC 61850 | СИСТЕМНАЯ ИНФОРМАЦИЯ ПО IEC 61850 | SYSTEM INFORMATION IEC 61850
SYSTEM INFORMATION BAY OI | INFORMATION SYSTEME BAIE OI | SYSTEM INFORMATION BAY OI | SYSTEM INFORMATION BAY OI | SYSTEM INFORMATION BAY OI | СИСТЕМНАЯ ИНФОРМАЦИЯ ПО BAY OI | SYSTEM INFORMATION BAY OI
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Equipment Link | Lien Equipement | Equipment Link | Acoplamiento del equipo | Ligação do equipamento | Оборудование связи | Equipment Link
Function | Fonction | Function | Función | Função | Функция | Function
Type | Type | Type | Type | Type | Type | Type
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Simple : Texte à l'état électrique = 1 Double : Texte à l'état électrique = 10 Multiple : pas utilisé MV : pas utilisé (16 car) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char) | Одиночный : Обозначение электрического состояния = 1 Двойной : Обозначение электрического состояния = 10 Множественный: не используется MV : Не используется (16 символов) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 Multiple : Not used MV : Not used (16 char)
Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Simple : Texte à l'état électrique = 0 Double : Texte à l'état électrique =01 Multiple : pas utilisé MV : pas utilisé (16 car) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char) | Одиночный : Обозначение электрического состояния = 0 Двойной : Обозначение электрического состояния = 01 Множественный: не используется MV : Не используется (16 символов) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 Multiple : Not used MV : Not used (16 char)
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
Computers Groups (separator ";") | Groupes de calculateur (séparateur ";") | Computers Groups (separator ";") | Grupos de Computadoras (separador ";") | Grupos de Computadores (separador ";") | Группы контроллеров (разделитель ";") | Computers Gruppen (separator ";")
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
LED MV : Not used | LED MV : Non utilisé | LED MV : Not used | LED MV : Not used | LED MV : Not used | Индикатор MV : Не используется | LED MV : Not used
xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : Affichage LCD xPC : Contrôle LCD MV : Affichage LCD | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : LCD Display xPC : LCD Control MV : LCD Display | xPS : LCD Дисплей xPC : Управление LCD MV : LCD Дисплей | xPS : LCD Display xPC : LCD Control MV : LCD Display
xPS : HMI Display xPC : HMI Control MV : HMI Display | xPS : Affichage HMI xPC : Contrôle HMI MV : Affichage HMI | xPS : HMI Display xPC : HMI Control MV : HMI Display | xPS : HMI Display xPC : HMI Control MV : HMI Display | xPS : HMI Display xPC : HMI Control MV : HMI Display | xPS : HMI Дисплей xPC : Управление HMI MV : HMI Дисплей | xPS : HMI Display xPC : HMI Control MV : HMI Display
xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | xPS : Est un retour de position xPC xPC : Est activé par xPS MV : Archivé | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer | xPS : активируется с помощью xPC xPC : активируется с помощью xPS MV : Просмотр кривых | xPS : Acts on xPC xPC : Is activated by xPS MV : Trend Viewer
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used | xPS, MV : Est utilisé par la distribution automatique (GOOSE) xPC : Non utilisé | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used | xPS, MV : Используется распределенной автоматикой (GOOSE) xPC : Не используется | xPS, MV : Is used by distributed Automation (GOOSE) xPC : Not used
Datapoint Name (in SCE Template) | Nom du Point de Donnée (dans le modèle du SCE) | Datapoint Name (in SCE Template) | Nombre del dato (en plantilla SCE) | Nome do Dado (em Panilha SCE) | Имя точки данных (в SCE шаблоне) | Datapoint Name (in SCE Template)
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
Agency status | Etat agence | Agency status | Agency status | Agency status | Agency status | Agency status
Auto archiving | Archivage auto | Auto archiving | Auto archiving | Auto archiving | Auto archiving | Auto archiving
AIU status | AIU statut | AIU status | AIU status | AIU status | AIU status | AIU status
AIU status | AIU statut | AIU status | AIU status | AIU status | AIU status | AIU status
Backup printer status | Etat imprimante backup | Backup printer status | Backup printer status | Backup printer status | Backup printer status | Backup printer status
BIU status | BIU statut | BIU status | BIU status | BIU status | BIU status | BIU status
CCU status | CCU statut | CCU status | CCU status | CCU status | CCU status | CCU status
Central archive | Archive centrale | Central archive | Central archive | Central archive | Central archive | Central archive
Device link | Lien équipement | Device link | Device link | Device link | Device link | Device link
SPS Communication with the IED | SPS de communication avec l'IED | SPS Communication with the IED | SPS Communication with the IED | SPS Communication with the IED | SPS Communication with the IED | SPS Communication with the IED
OI client link | Lien client OI | OI client link | OI client link | OI client link | OI client link | OI client link
Communication SPS with the SCADA | SPS de communication avec le SCADA | Communication SPS with the SCADA | Communication SPS with the SCADA | Communication SPS with the SCADA | Communication SPS with the SCADA | Communication SPS with the SCADA
Counter Top | Top compteur | Counter Top | Counter Top | Counter Top | Counter Top | Counter Top
UCA2 Coupling | Couplage UCA2 | UCA2 Coupling | UCA2 Coupling | UCA2 Coupling | UCA2 Coupling | UCA2 Coupling
DB incohency SPS | SPS DB incohérente | DB incohency SPS | DB incohency SPS | DB incohency SPS | DB incohency SPS | DB incohency SPS
DB switch control | contrôle basculement BD | DB switch control | DB switch control | DB switch control | DB switch control | DB switch control
DI acquisition stopped | Acquisition DI arrêtée | DI acquisition stopped | DI acquisition stopped | DI acquisition stopped | DI acquisition stopped | DI acquisition stopped
SPS disturbance file ready | SPS fichier de perturbo prête | SPS disturbance file ready | SPS disturbance file ready | SPS disturbance file ready | SPS disturbance file ready | SPS disturbance file ready
SPS disturbance file ready | SPS fichier de perturbo prête | SPS disturbance file ready | SPS disturbance file ready | SPS disturbance file ready | SPS disturbance file ready | SPS disturbance file ready
DIU status | DIU statut | DIU status | DIU status | DIU status | DIU status | DIU status
DOU status | DOU statut | DOU status | DOU status | DOU status | DOU status | DOU status
External clock status | Etat horloge external | External clock status | External clock status | External clock status | External clock status | External clock status
GHU status | GHU statut | GHU status | GHU status | GHU status | GHU status | GHU status
ISAGRAF status | Etat ISAGRAF | ISAGRAF status | ISAGRAF status | ISAGRAF status | ISAGRAF status | ISAGRAF status
Local/remote DPS | DPS local/distant | Local/remote DPS | Local/remote DPS | Local/remote DPS | Local/remote DPS | Local/remote DPS
Local/remote controlDPC | DPC de contrôle Local/distant | Local/remote controlDPC | Local/remote controlDPC | Local/remote controlDPC | Local/remote controlDPC | Local/remote controlDPC
Local/remote SPS | SPS loc/distant | Local/remote SPS | Local/remote SPS | Local/remote SPS | Local/remote SPS | Local/remote SPS
Log Queue | File du log | Log Queue | Log Queue | Log Queue | Log Queue | Log Queue
Main computer status MV | MV état calculateur principal | Main computer status MV | Main computer status MV | Main computer status MV | Main computer status MV | Main computer status MV
Device mode | Mode équip. | Device mode | Device mode | Device mode | Device mode | Device mode
Mode control DPC | DPC de contrôle du mode | Mode control DPC | Mode control DPC | Mode control DPC | Mode control DPC | Mode control DPC
Operating mode | Mode exploitation | Operating mode | Operating mode | Operating mode | Operating mode | Operating mode
Printer status | DPS état imprimante | Printer status | Printer status | Printer status | Printer status | Printer status
Redundancy change mode control | contrôle changement mode redondance | Redundancy change mode control | Redundancy change mode control | Redundancy change mode control | Redundancy change mode control | Redundancy change mode control
Redundancy change status | Statut changt redondance | Redundancy change status | Redundancy change status | Redundancy change status | Redundancy change status | Redundancy change status
Redundancy change status control | Contrôle changement statut redond. | Redundancy change status control | Redundancy change status control | Redundancy change status control | Redundancy change status control | Redundancy change status control
Redundancy mode | Mode redondance | Redundancy mode | Redundancy mode | Redundancy mode | Redundancy mode | Redundancy mode
Redundancy SPS | SPS de Redondance | Redundancy SPS | Redundancy SPS | Redundancy SPS | Redundancy SPS | Redundancy SPS
OI client | Client OI | OI client | OI client | OI client | OI client | OI client
Software error SPS | SPS erreur logicielle | Software error SPS | Software error SPS | Software error SPS | Software error SPS | Software error SPS
Synchronisation | Synchronisation | Synchronisation | Synchronisation | Synchronisation | Synchronisation | Synchronisation
IED SPS Synchronisation | SPS de Synchronisation de l'IED | IED SPS Synchronisation | IED SPS Synchronisation | IED SPS Synchronisation | IED SPS Synchronisation | IED SPS Synchronisation
Test control DPC | DPC de control de test | Test control DPC | Test control DPC | Test control DPC | Test control DPC | Test control DPC
TMU status | TMU statut | TMU status | TMU status | TMU status | TMU status | TMU status
Watchdog error SPS | SPS erreur watchdog | Watchdog error SPS | Watchdog error SPS | Watchdog error SPS | Watchdog error SPS | Watchdog error SPS
HBU status | HBU statut | HBU status | HBU status | HBU status | HBU status | HBU status
Agency status | Etat agence | Agency status | Agency status | Agency status | Agency status | Agency status
AIU status | AIU statut | AIU status | AIU status | AIU status | AIU status | AIU status
AIU status | AIU statut | AIU status | AIU status | AIU status | AIU status | AIU status
Auto archiving | Archivage auto | Auto archiving | Auto archiving | Auto archiving | Auto archiving | Auto archiving
BackupPrint stat | Etat imp. backup | BackupPrint stat | BackupPrint stat | BackupPrint stat | BackupPrint stat | BackupPrint stat
BIU status | BIU statut | BIU status | BIU status | BIU status | BIU status | BIU status
DREC ready | Perturbo prête | DREC ready | DREC ready | DREC ready | DREC ready | DREC ready
CCU status | CCU statut | CCU status | CCU status | CCU status | CCU status | CCU status
Central archive | Archive centrale | Central archive | Central archive | Central archive | Central archive | Central archive
Counter Top | Top compteur | Counter Top | Counter Top | Counter Top | Counter Top | Counter Top
DB incoh. SPS | SPS DB incoh. | DB incoh. SPS | DB incoh. SPS | DB incoh. SPS | DB incoh. SPS | DB incoh. SPS
DB switch ctrl | ctrl bascul. BD | DB switch ctrl | DB switch ctrl | DB switch ctrl | DB switch ctrl | DB switch ctrl
Device link | Lien équipement | Device link | Device link | Device link | Device link | Device link
Device mode | Mode équip. | Device mode | Device mode | Device mode | Device mode | Device mode
DI acq stopped | Acq DI arrêtée | DI acq stopped | DI acq stopped | DI acq stopped | DI acq stopped | DI acq stopped
DIU status | DIU statut | DIU status | DIU status | DIU status | DIU status | DIU status
DOU status | DOU statut | DOU status | DOU status | DOU status | DOU status | DOU status
Ext clock status | Etat horloge ext | Ext clock status | Ext clock status | Ext clock status | Ext clock status | Ext clock status
GHU status | GHU statut | GHU status | GHU status | GHU status | GHU status | GHU status
IED DREC ready | IED pert. prête | IED DREC ready | IED DREC ready | IED DREC ready | IED DREC ready | IED DREC ready
IED SPS com. | SPS com. IED | IED SPS com. | IED SPS com. | IED SPS com. | IED SPS com. | IED SPS com.
IED SPS Synchro. | SPS Synchro. IED | IED SPS Synchro. | IED SPS Synchro. | IED SPS Synchro. | IED SPS Synchro. | IED SPS Synchro.
ISAGRAF status | Etat ISAGRAF | ISAGRAF status | ISAGRAF status | ISAGRAF status | ISAGRAF status | ISAGRAF status
ISAGRAF status | Etat ISAGRAF | ISAGRAF status | ISAGRAF status | ISAGRAF status | ISAGRAF status | ISAGRAF status
Loc/rem ctrl DPC | DPC ctrl Loc/dis | Loc/rem ctrl DPC | Loc/rem ctrl DPC | Loc/rem ctrl DPC | Loc/rem ctrl DPC | Loc/rem ctrl DPC
Local/remote DPS | DPS local/distant | Local/remote DPS | Local/remote DPS | Local/remote DPS | Local/remote DPS | Local/remote DPS
Local/remote SPS | SPS loc/distant | Local/remote SPS | Local/remote SPS | Local/remote SPS | Local/remote SPS | Local/remote SPS
Log Queue | File du log | Log Queue | Log Queue | Log Queue | Log Queue | Log Queue
Main status MV | MV état princ. | Main status MV | Main status MV | Main status MV | Main status MV | Main status MV
Mode control DPC | DPC de contrôle du mode | Mode control DPC | Mode control DPC | Mode control DPC | Mode control DPC | Mode control DPC
OI client link | Lien client OI | OI client link | OI client link | OI client link | OI client link | OI client link
Operating mode | Mode exploitation | Operating mode | Operating mode | Operating mode | Operating mode | Operating mode
Printer status | DPS état imprimante | Printer status | Printer status | Printer status | Printer status | Printer status
Red mode ctrl | ctrl mode red | Red mode ctrl | Red mode ctrl | Red mode ctrl | Red mode ctrl | Red mode ctrl
Red Status ctrl | ctrl statut red | Red Status ctrl | Red Status ctrl | Red Status ctrl | Red Status ctrl | Red Status ctrl
Red. change stat | Stat changt red. | Red. change stat | Red. change stat | Red. change stat | Red. change stat | Red. change stat
Redundancy mode | Mode redondance | Redundancy mode | Redundancy mode | Redundancy mode | Redundancy mode | Redundancy mode
Redundancy SPS | SPS de Redondance | Redundancy SPS | Redundancy SPS | Redundancy SPS | Redundancy SPS | Redundancy SPS
SCADA SPS com. | SPS com. SCADA | SCADA SPS com. | SCADA SPS com. | SCADA SPS com. | SCADA SPS com. | SCADA SPS com.
Soft. error SPS | SPS erreur soft. | Soft. error SPS | Soft. error SPS | Soft. error SPS | Soft. error SPS | Soft. error SPS
Synchronisation | Synchronisation | Synchronisation | Synchronisation | Synchronisation | Synchronisation | Synchronisation
Test control DPC | DPC de control de test | Test control DPC | Test control DPC | Test control DPC | Test control DPC | Test control DPC
TMU status | TMU statut | TMU status | TMU status | TMU status | TMU status | TMU status
HBU status | HBU statut | HBU status | HBU status | HBU status | HBU status | HBU status
UCA2 Coupling | Couplage UCA2 | UCA2 Coupling | UCA2 Coupling | UCA2 Coupling | UCA2 Coupling | UCA2 Coupling
Watchdog SPS | SPS Watchdog | Watchdog SPS | Watchdog SPS | Watchdog SPS | Watchdog SPS | Watchdog SPS
Board status DPS | DPS état carte | Board status DPS | Board status DPS | Board status DPS | Board status DPS | Board status DPS
Red. change mode | Mode changt red. | Red. change mode | Red. change mode | Red. change mode | Red. change mode | Red. change mode
LD DREC ready | LD DREC prêt | LD DREC ready | LD DREC ready | LD DREC ready | LD DREC ready | LD DREC ready
AOU status | AOU statut | AOU status | AOU status | AOU status | AOU status | AOU status
Buff Ov Gtw 1 | Buff Ov Gtw 1 | Buff Ov Gtw 1 | Buff Ov Gtw 1 | Buff Ov Gtw 1 | Buff Ov Gtw 1 | Buff Ov Gtw 1
Buff Ov Gtw 2 | Buff Ov Gtw 2 | Buff Ov Gtw 2 | Buff Ov Gtw 2 | Buff Ov Gtw 2 | Buff Ov Gtw 2 | Buff Ov Gtw 2
Buff Ov OI | Buff Ov OI | Buff Ov OI | Buff Ov OI | Buff Ov OI | Buff Ov OI | Buff Ov OI
Buff Ov OI Bck | Buff Ov OI Bck | Buff Ov OI Bck | Buff Ov OI Bck | Buff Ov OI Bck | Buff Ov OI Bck | Buff Ov OI Bck
All IED status | All IED status | All IED status | All IED status | All IED status | All IED status | All IED status
All rack status | All rack status | All rack status | All rack status | All rack status | All rack status | All rack status
Local alarm ack | Local alarm ack | Local alarm ack | Local alarm ack | Local alarm ack | Local alarm ack | Local alarm ack
Setting done | Setting done | Setting done | Setting done | Setting done | Setting done | Setting done
Setting disc. | Setting disc. | Setting disc. | Setting disc. | Setting disc. | Setting disc. | Setting disc.
Setting in prog. | Setting in prog. | Setting in prog. | Setting in prog. | Setting in prog. | Setting in prog. | Setting in prog.
Setting incoher. | Setting incoher. | Setting incoher. | Setting incoher. | Setting incoher. | Setting incoher. | Setting incoher.
Rack link status | Rack link status | Rack link status | Rack link status | Rack link status | Rack link status | Rack link status
Red.Status | Red.Status | Red.Status | Red.Status | Red.Status | Red.Status | Red.Status
IEC61850 gen SPS | IEC61850 gen SPS | IEC61850 gen SPS | IEC61850 gen SPS | IEC61850 gen SPS | IEC61850 gen SPS | IEC61850 gen SPS
IEC61850 gen DPS | IEC61850 gen DPS | IEC61850 gen DPS | IEC61850 gen DPS | IEC61850 gen DPS | IEC61850 gen DPS | IEC61850 gen DPS
IEC61850 gen MPS | IEC61850 gen MPS | IEC61850 gen MPS | IEC61850 gen MPS | IEC61850 gen MPS | IEC61850 gen MPS | IEC61850 gen MPS
IEC61850 gen SPC | IEC61850 gen SPC | IEC61850 gen SPC | IEC61850 gen SPC | IEC61850 gen SPC | IEC61850 gen SPC | IEC61850 gen SPC
IEC61850 gen DPC | IEC61850 gen DPC | IEC61850 gen DPC | IEC61850 gen DPC | IEC61850 gen DPC | IEC61850 gen DPC | IEC61850 gen DPC
IEC61850 gen MV | IEC61850 gen MV | IEC61850 gen MV | IEC61850 gen MV | IEC61850 gen MV | IEC61850 gen MV | IEC61850 gen MV
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : System Functions | SHEET : Fonctions Systèmes | SHEET : System Functions | SHEET : System Functions | SHEET : System Functions | SHEET : Функции системы | SHEET : System Functions
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
SYSTEM PROFILES | PROFILS SYSTEMES | SYSTEM PROFILES | SYSTEM PROFILES | SYSTEM PROFILES | Профили системы | SYSTEM PROFILES
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : SystemInformation_Template | SHEET : SystemInformation_Template | SHEET : SystemInformation_Template | SHEET : SystemInformation_Template | SHEET : SystemInformation_Template | SHEET : SystemInformation_Template | SHEET : SystemInformation_Template
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
SYSTEM INFORMATION DATA DESCRIPTION | INFORMATION SYSTEME DESCRIPTION | SYSTEM INFORMATION DATA DESCRIPTION | SYSTEM INFORMATION DATA DESCRIPTION | SYSTEM INFORMATION DATA DESCRIPTION | ОПИСАНИЕ СИСТЕМНОЙ ИНФОРМАЦИИ | SYSTEM INFORMATION DATA DESCRIPTION
Gateway | Passerelle | Gateway | UTR | UTR | Шлюз | Gateway
Port used (on gateway) | Ports utilisés (sur la passerelle) | Port used (on gateway) | Puerto utilizado (en UTR) | Porta utilizada (em UTR) | Используемый порт (на шлюз) | benutzter Port (Gateway)
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
SCADA 1 | SCADA 1 | SCADA 1 | SCADA 1 | SCADA 1 | SCADA 1 | SCADA 1
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
SCADA 2 | SCADA 2 | SCADA 2 | SCADA 2 | SCADA 2 | SCADA 2 | SCADA 2
Auto generated | Génération automatique | Auto generated | Auto generado | Auto Geração | Автоматически сгенерировано | Auto generated
SCADA 3 | SCADA 3 | SCADA 3 | SCADA 3 | SCADA 3 | SCADA 3 | SCADA 3
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
SCADA 4 | SCADA 4 | SCADA 4 | SCADA 4 | SCADA 4 | SCADA 4 | SCADA 4
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : List of bays | SHEET : Liste des Tranches | SHEET : List of bays | SHEET : Lista de bahías | SHEET : Lista de Bays | SHEET : Список ячеек | SHEET : List of bays
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
BAY INFORMATION | INFORMATIONS SUR LES TRANCHES | BAY INFORMATION | INFORMACION DE BAHIAS | Informação de Bays | ИНФОРМАЦИЯ ПО ЯЧЕЙКЕ | BAY INFORMATION
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
Bay Name | Nom de la Tranche | Bay Name | Nombre de bahía | Nome do Painel | Имя ячейки | Bay Name
Bay Type | Type de Tranche | Bay Type | Tipo de bahía | Tipo de Painel | Тип ячейки | Bay Type
Computer | Calculateur | Computer | Computador | Computador | Компьютер | Computer
Redundant Computer | Calculateur Redondant | Redundant Computer | Computador Redundante | Computador Redundante | Резервный компьютер | Redundant Computer
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : T101 Model | SHEET : Modèles T101 | SHEET : T101 Model | SHEET : Modelo T101 | SHEET : Modo T101 | SHEET : Модель T101 | SHEET : T101 Model
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
BEGIN SCADA T101 | DEBUT SCADA T101 | BEGIN SCADA T101 | COMIENZA SCADA T101 | INÍCIO SCADA T101 | НАЧАЛО ОПИСАНИЯ SCADA T101 | BEGIN SCADA T101
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Grid
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
SCADA Protocol Name | Nom de protocole SCADA | SCADA Protocol Name | Nombre de Protocolo SCADA | Nome do Protocolo SCADA | SCADA ИМЯ Протокола | SCADA Protocol Name
Scada short name (16 char) | Nom court du SCADA (16 char) | Scada short name (16 char) | Nombre corto Scada (16 caract) | Nome Curto Scada (16 caract) | Сокращенное имя SCADA (16 символов) | Scada short name (16 char)
Protocol General Parameters | Paramètres généraux du Protocole | Protocol General Parameters | Parámetros generales del protocolo | Parâmetros Geração do Protocolo | Основные параметры протокола | Protocol General Parameters
Main communication channel | Voie de communication principale | Main communication channel | Canal de comunicación principal | Canal de Comunicação Principal | Основной канал связи | Main communication channel
Auxiliary Communication channel | Voie de communication auxiliaire | Auxiliary Communication channel | Canal de comunciación auxiliar | Canal de Comunicação auxiliar | Запасной канал связи | Auxiliary Communication channel
Baud rate (bit/s) | Vitesse de transmission (bit/s) | Baud rate (bit/s) | Baudios (bit/s) | Baud Rate (bit/s) | Скорость в бодах (бит/с) | Baud rate (bit/s)
Time Reference | Temps de référence | Time Reference | Tiempo de referencia | Tempo de referência | Время ссылку | Zeitplan
Redundancy type | Type de redondance | Redundancy type | Tipo de redundancia | Redundância tipo | Избыточность типа | Redundanz Typ
Link Address | Adresse du lien | Link Address | Dirección del vínculo | Endereço do Link | Адрес связи | Link Address
Redundant Link Address | Adresse du lien redondant | Redundant Link Address | Dirección redundante del vínculo | Endereço redundante do Vínculo | Резервный адрес связи | Redundant Link Address
Link Address Length | Longueur de l'adresse du lien | Link Address Length | Longitud de la dirección del vínculo | Tamanho do Endereço do Link | Длина адреса связи | Link Address Length
Common address of ASDU | Adresse commune de l'ASDU | Common address of ASDU | Dirección común ASDU | Endereço comum ASDU | Общий адрес ASDU | Common address of ASDU
Common address of ASDU Length | Longueur de l'adresse commune de l'ASDU | Common address of ASDU Length | Longitud de la dirección común ASDU | Tamanho do Endereço comum ASDU | Длина общего адреса ASDU | Common address of ASDU Length
Object structure | Structure d'objet | Object structure | Estructura del objeto | Estrutura do objeto | Структура объекта | Object structure
Frame max length | Longueur maximale de la vue | Frame max length | Longitud máx de la trama | Tamanho máx do frame | Максимальная длина кадра | Frame max length
Cause of Transmission Length | Cause de longueur de transmission | Cause of Transmission Length | Longitud de la causa de transmisión | Tamanho da causa de Transmissão | Длина Cause of Transmission | Cause of Transmission Length
Measurement periodic cycle | Cycle Périodique de Mesure | Measurement periodic cycle | Ciclo de medición periódico | Ciclo periódico de Medição | Периодический цикл измерений | Measurement periodic cycle
Binary Time Size | Taille de Temps binaire | Binary Time Size | Tamaño de tiempo binario | Tamanho Binário do Tempo | Размер двоичной кодировки времени | Binary Time Size
Background scan cycle | Cycle de balayage | Background scan cycle | Ciclo "background scan" | Ciclo "background scan" | Фоновый цикл сканирования | Background scan cycle
Type of link | Type de lien | Type of link | Tipo de enlace | Tipo de ligação | Вид ссылки | Art der Verknüpfung
Test frame timeout (T3) | Expriration de la trame de test (T3) | Test frame timeout (T3) | Marco de tiempo de prueba (T3) | Teste moldura Timeout (T3) | Тест кадр тайм (T3) | Prüfung Timeout (T3)
SBO timeout | Temps d'expiration pour la sélection avant opération | SBO timeout | Tiempo fuera SBO | Falha SBO | Задержка SBO | SBO Timeout
Inter frame duration | Durée inter trame | Inter frame duration | Duración entre 2 fotogramas | Duração entre 2 frames | Продолжительность от 2 кадров | Inter frame duration
Quality Value for 'Jammed' state | Valeur de Qualité de l'état 'Jammed' | Quality Value for 'Jammed' state | Valor de calidad 'atascado' estado | Qualidade Valor para 'emperrado' estado | Качество стоимость для 'застряла' состояния | Qualitäts für "gestaute" Zustand
Quality Value for toggling xPS | Valeur de Qualité de bascule xPS | Quality Value for toggling xPS | Valor de calidad para alternar XPS | Qualidade Valor para alternar xps | Качество стоимость для переключения XPS | Qualitäts für Makeln XPS
Quality Value for 'Unknown' state | Valeur de Qualité de l'état 'Inconnu' | Quality Value for 'Unknown' state | Valor de calidad 'Desconocido' estado | Qualidade Valor para 'Desconhecido' estado | Качество стоимость для 'Неизвестное' состояние | Qualitäts für "unbekannt" Zustand
SOE file support | Support de fichier SOE | SOE file support | Archivo de apoyo SOE | Arquivo apoio SOE | файл поддержки SOE | SOE file support
SOE file address | Adresse de fichier SOE | SOE file address | Archivo dirección SOE | Arquivo endereço SOE | файл адрес SOE | SOE file address
SOE file format | Format de fichier SOE | SOE file format | Formato de archivo SOE | Formato de arquivo SOE | файл формата SOE | SOE file format
SOE file nb of events | Nb d'évenements dans le fichier SOE | SOE file nb of events | Número de expediente de hechos SOE | Arquivo número de eventos SOE | файл ряд мероприятий SOE | SOE file nb of events
Nb max of SOE files | Nombre maximum de fichiers SOE | Nb max of SOE files | número máximo de archivos de SOE | Número máximo de arquivos SOE | Максимальное количество SOE файлы | Nb max of SOE files
Full SOE file nb of events | Nb d'évenements dans le fichier SOE plein | Full SOE file nb of events | Completa número de expediente de hechos SOE | Arquivo completo conjunto de eventos SOE | полный файл SOE ряд мероприятий | Full SOE file nb of events
Disturbance file support | Support du fichier de Perturbographie | Disturbance file support | Perturbación archivo de apoyo | Perturbação arquivo apoio | Нарушение файл поддержки | Disturbance-Unterstützung
Disturbance file address | Adresse du fichier de Perturbographie | Disturbance file address | Perturbación archivo dirección | Perturbação arquivo endereço | Нарушение файл адрес | Disturbance-Adresse
Disturbance file address for T103 | Adresse du fichier de Perturbographie T103 | Disturbance file address for T103 | Perturbación archivo dirección T103 | Perturbação arquivo endereço T103 | Нарушение файл адрес T103 | Disturbance-Adresse T103
Disturbance file address for S20 | Adresse du fichier de Perturbographie S20 | Disturbance file address for S20 | Perturbación archivo dirección S20 | Perturbação arquivo endereço S20 | Нарушение файл адрес S20 | Disturbance-Adresse S20
Disturbance file address for M300 | Adresse du fichier de Perturbographie M300 | Disturbance file address for M300 | Perturbación archivo dirección M300 | Perturbação arquivo endereço M300 | Нарушение файл адрес M300 | Disturbance-Adresse M300
Disturbance file address for SlowWave | Adresse du fichier de Perturbographie SlowWave | Disturbance file address for SlowWave | Perturbación archivo dirección SlowWave | Perturbação arquivo endereço SlowWave | Нарушение файл адрес SlowWave | Disturbance-Adresse SlowWave
Disturbance file address for FastWave | Adresse du fichier de Perturbographie FastWave | Disturbance file address for FastWave | Perturbación archivo dirección FastWave | Perturbação arquivo endereço FastWave | Нарушение файл адрес FastWave | Disturbance-Adresse FastWave
Nb max of Disturbance files | Nombre maximum de fichiers de perturbographie | Nb max of Disturbance files | número máximo de archivos de perturbación | Número máximo de arquivos Perturbação | Максимальное количество нарушений файлы | maximale Anzahl von Dateien Disturbance
Buffer Overflow file support | Support du fichier de débordement de tampon | Buffer Overflow file support | Desbordamiento de búfer de archivo de apoyo | Buffer overflow arquivo apoio | Переполнение буфера файл поддержки | Buffer Overflow-Unterstützung
Buffer Overflow file address | Adresse du fichier de débordement de tampon | Buffer Overflow file address | Desbordamiento de búfer de archivo dirección | Buffer overflow arquivo endereço | Переполнение буфера файла адрес | Buffer Overflow-Datei-Adresse
Buffer Overflow empty condition | Condition vide de débordement de tampon | Buffer Overflow empty condition | Condición vacío de desbordamiento de búfer | Buffer overflow vazio condição | Переполнение буфера пустого состояния | Buffer Overflow leeren Zustand
Balanced mode | Mode balancé | Balanced mode | Modo Balanced | Modo Balanced | Сбалансированный режим | Balanced mode
Balanced mode retry number | Mode balancé nb d'essais | Balanced mode retry number | Modo Balanced el número de reintentos | Modo Balanced número do reintentos | Сбалансированный режим повтора номера | Balanced mode retry Zahl
Balanced mode link timeout | Expiration du mode balancé | Balanced mode link timeout | Tiempo de modo Balanced enlace | Falha do modo Balanced | Сбалансированный режим ссылку тайм | Balanced mode link timeout
Sequence of Information value for TS | Séquence d'Information valeur de TS | Sequence of Information value for TS | Secuencia de la información de valor para el TS | Sequência de Informação valor para TS | Последовательность Информация значение для ТП | Sequence of Information value for TS
Sequence of Information value for TM | Séquence d'Information valeur de TM | Sequence of Information value for TM | Secuencia de la información de valor para TM | Sequência de Informação valor para TM | Последовательность Информация значение для TM | Sequence of Information value for TM
Sequence of Information value for Counter | Séquence d'Information valeur de Compteur | Sequence of Information value for Counter | Secuencia de la información de valor para Counter | Sequência de Informação valor para Counter | Последовательность Информация значение для борьбы | Sequence of Information value for Counter
Sequence of Information Gap address to split | Séquence d'Information écart d'adresse de séparation | Sequence of Information Gap address to split | Secuencia de la Información Brecha dirección para dividir | Sequência de Informação Gap endereço para dividir | Последовательность информационных пробелов адрес разделить | Sequence of Information Gap address to split
SPS Data Type | SPS Donnée de Type | SPS Data Type | SPS Datos tipo | SPS Dados tipo | SPS Тип данных | SPS Data Type
Event transmission | Transmission d'évènements | Event transmission | Transmisión de eventos | Transmissão de Eventos | Событие передачи | Event transmission
Group [0-16] (0=no) | Groupes [0-16] (0=non) | Group [0-16] (0=no) | Grupo [0-16] (0=no) | Grupo [0-16] (0=não) | Группа [0-16] (0=no) | Gruppe [0-16] (0=no)
Priority [1-255] | Prioritée [1-255] | Priority [1-255] | Prioridad [1-255] | Prioridade[1-255] | Приоритет [1-255] | Priority [1-255]
Inverted state | Etat Inversé | Inverted state | Estado invertido | Estado invertido | Инвертированное состояние | Inverted state
Background scan | Balayage de fond | Background scan | Background scan | Background scan | Сканирование в фоновом режиме | Background scan
Event Record | Enregistrement d'évènement | Event Record | Registro de eventos | Registro de Eventos | Запись события | Event Record
DPS Data Type | DPS Donnée de Type | DPS Data Type | DPS Datos tipo | DPS Dados tipo | DPS Тип данных | DPS Data Type
Event transmission | Transmission d'évènements | Event transmission | Transmisión de eventos | Transmissão de Eventos | Событие передачи | Event transmission
Group [0-16] (0=no) | Groupes [0-16] (0=non) | Group [0-16] (0=no) | Grupo [0-16] (0=no) | Grupo [0-16] (0=não) | Группа [0-16] (0=no) | Gruppe [0-16] (0=no)
Priority [1-255] | Prioritée [1-255] | Priority [1-255] | Prioridad [1-255] | Prioridade[1-255] | Приоритет [1-255] | Priority [1-255]
Inverted state | Etat Inversé | Inverted state | Estado invertido | Estado invertido | Инвертированное состояние | Inverted state
Background scan | Balayage de fond | Background scan | Background scan | Background scan | Сканирование в фоновом режиме | Background scan
Event Record | Enregistrement d'évènement | Event Record | Registro de eventos | Registro de Eventos | Запись события | Event Record
MPS Data Type | MPS Donnée de Type | MPS Data Type | MPS Datos tipo | MPS Dados tipo | MPS Тип данных | MPS Data Type
Event transmission | Transmission d'évènements | Event transmission | Transmisión de eventos | Transmissão de Eventos | Событие передачи | Event transmission
Group [0-16] (0=no) | Groupes [0-16] (0=non) | Group [0-16] (0=no) | Grupo [0-16] (0=no) | Grupo [0-16] (0=não) | Группа [0-16] (0=no) | Gruppe [0-16] (0=no)
Priority [1-255] | Prioritée [1-255] | Priority [1-255] | Prioridad [1-255] | Prioridade[1-255] | Приоритет [1-255] | Priority [1-255]
Bitstring usage | Utilisation du Bistring | Bitstring usage | Bitstring uso | Estado invertido | Bitstring использования | Bitstring Nutzung
Background scan | Balayage de fond | Background scan | Background scan | Background scan | Сканирование в фоновом режиме | Background scan
Event Record | Enregistrement d'évènement | Event Record | Registro de eventos | Registro de Eventos | Запись события | Event Record
SPC Data Type | SPC Donnée de Type | SPC Data Type | SPC Datos tipo | SPC Dados tipo | SPC Тип данных | SPC Data Type
SCADA order type | Type de commande SCADA | SCADA order type | Tipo de orden SCADA | Tipo de Ordem SCADA | Тип команды SCADA | SCADA order type
SBO timeout [0-65535 s] | Temps d'expiration pour la sélection avant opération [0-65535 s] | SBO timeout [0-65535 s] | SBO tiempo fuera [0-65535 s] | Tempo Limite SBO[0-65535 s] | Задерка SBO [0-65535 с] | SBO timeout [0-65535 s]
DPC Data Type | DPC Donnée de Type | DPC Data Type | DPC Datos tipo | DPC Dados tipo | DPC Тип данных | DPC Data Type
SCADA order type | Type de commande SCADA | SCADA order type | Tipo de orden SCADA | Tipo de Ordem SCADA | Тип команды SCADA | SCADA order type
SBO timeout [0-65535 s] | Temps d'expiration pour la sélection avant opération [0-65535 s] | SBO timeout [0-65535 s] | SBO tiempo fuera [0-65535 s] | Tempo Limite SBO[0-65535 s] | Задерка SBO [0-65535 с] | SBO timeout [0-65535 s]
MV Data Type | MV Donnée de Type | MV Data Type | MV Datos tipo | MV Dados tipo | MV Тип данных | MV Data Type
Event transmission | Transmission d'évènements | Event transmission | Transmisión de eventos | Transmissão de Eventos | Событие передачи | Event transmission
Group [0-16] (0=no) | Groupes [0-16] (0=non) | Group [0-16] (0=no) | Grupo [0-16] (0=no) | Grupo [0-16] (0=não) | Группа [0-16] (0=no) | Gruppe [0-16] (0=no)
Priority [1-255] | Prioritée [1-255] | Priority [1-255] | Prioridad [1-255] | Prioridade[1-255] | Приоритет [1-255] | Priority [1-255]
Format | Format | Format | Formato | Formato | Формат | Format
Cycle Type | Type de Cycle | Cycle Type | Tipo de ciclo | Tipo de Ciclo | Тип цикла | Cycle Type
Event Record | Enregistrement d'évènement | Event Record | Registro de eventos | Registro de Eventos | Запись события | Event Record
Minimum value | Valeur Min | Minimum value | Valor al mínimo | Valor ao Mínimo | Значение минимуму | Minimum value
Maximum value | Valeur Max | Maximum value | Valor al Máximo | Valor ao Máximo | Значение максимуму | Maximum value
Setpoint Data Type | SetPoint Donnée de Type | Setpoint Data Type | SetPoint Datos tipo | SetPoint Dados tipo | SetPoint Тип данных | Setpoint Data Type
SCADA order type | Type de commande SCADA | SCADA order type | Tipo de orden SCADA | Tipo de Ordem SCADA | Тип команды SCADA | SCADA order type
Format | Format | Format | Formato | Formato | Формат | Format
Minimum value | Valeur Min | Minimum value | Valor al mínimo | Valor ao Mínimo | Значение минимуму | Minimum value
Maximum value | Valeur Max | Maximum value | Valor al Máximo | Valor ao Máximo | Значение максимуму | Maximum value
SBO timeout [0-65535 s] | Temps d'expiration pour la sélection avant opération [0-65535 s] | SBO timeout [0-65535 s] | SBO tiempo fuera [0-65535 s] | Tempo Limite SBO[0-65535 s] | Задерка SBO [0-65535 с] | SBO timeout [0-65535 s]
Counter Data Type | Compteur de Donnée de Type | Counter Data Type | Counter Datos tipo | Contador de Dados tipo | Counter Тип данных | Counter Data Type
Event transmission | Transmission d'évènements | Event transmission | Transmisión de eventos | Transmissão de Eventos | Событие передачи | Event transmission
Group [0-4] (0=no) | Groupes [0-4] (0=non) | Group [0-4] (0=no) | Grupo [0-4] (0=no) | Grupo [0-4] (0=não) | Группа [0-4] (0=no) | Gruppe [0-4] (0=no)
Priority [1-255] | Prioritée [1-255] | Priority [1-255] | Prioridad [1-255] | Prioridade[1-255] | Приоритет [1-255] | Priority [1-255]
Event Record | Enregistrement d'évènement | Event Record | Registro de eventos | Registro de Eventos | Запись события | Event Record
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : DNP3 Model | SHEET : Modèles DNP3 | SHEET : DNP3 Model | SHEET : Modelo DNP3 | SHEET : Modo DNP3 | SHEET : Модель DNP3 | SHEET : DNP3 Model
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
BEGIN SCADA DNP3 | DEBUT SCADA DNP3 | BEGIN SCADA DNP3 | COMIENZA SCADA DNP3 | INÍCIO SCADA DNP3 | НАЧАЛО ОПИСАНИЯ SCADA ПРОТОКОЛА DNP3 | BEGIN SCADA DNP3
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
SCADA Protocol Name | Nom de protocole SCADA | SCADA Protocol Name | Nombre de Protocolo SCADA | Nome do Protocolo SCADA | SCADA ИМЯ Протокола | SCADA Protocol Name
Scada short name (16 char) | Nom court du SCADA (16 char) | Scada short name (16 char) | Nombre corto Scada (16 caract) | Nome Curto Scada (16 caract) | Сокращенное имя SCADA (16 символов) | Scada short name (16 char)
Protocol General Parameters | Paramètres généraux du Protocole | Protocol General Parameters | Parámetros generales del protocolo | Parâmetros Geração do Protocolo | Основные параметры протокола | Protocol General Parameters
Main communication channel | Voie de communication principale | Main communication channel | Canal de comunicación principal | Canal de Comunicação Principal | Основной канал связи | Main communication channel
Auxiliary Communication channel | Voie de communication auxiliaire | Auxiliary Communication channel | Canal de comunciación auxiliar | Canal de Comunicação auxiliar | Запасной канал связи | Auxiliary Communication channel
Baud rate (bit/s) | Vitesse de transmission (bit/s) | Baud rate (bit/s) | Baudios (bit/s) | Baud Rate (bit/s) | Скорость в бодах (бит/с) | Baud rate (bit/s)
Time Reference | Temps de référence | Time Reference | Tiempo de referencia | Tempo de referência | Время ссылку | Zeitplan
TCP/IP usage | Utilise TCP/IP | TCP/IP usage | Uso de TCP/IP | Usos de TCP/IP | использование TCP/IP | TCP/IP usage
TCP/IP Address | Adresse TCP/IP | TCP/IP Address | TCP/IP Dirección | TCP/IP Endereço | TCP/IP Адрес | TCP/IP Address
Link Address | Adresse du lien | Link Address | Dirección del vínculo | Endereço do Link | Адрес связи | Link Address
Digital information class | Classe d'information numérique | Digital information class | Clase de información digital | Classe de Informação Digital | Тип цифровой информации | Digital information class
Measurement values class | Classe de valeur de mesure | Measurement values class | Clase de valores de medición | Classe de Valores de Medição | Тип измеряемых величин | Measurement values class
Counter class | Classe de compteur | Counter class | Clase de contadores | Classe de contadores | Тип счетчика | Counter class
Measurement format | Format de mesure | Measurement format | El formato de medición | Medição formato | Измерение формате | Messung format
Static Measurement | Mesure statique | Static Measurement | Medida estática | Static Medição | Статические измерения | Statische Messung
Event Measurement | Mesure évènementielle | Event Measurement | Medida eventa | Evento Medição | Событие измерения | Event-Messung
Counter format | Format de compteur | Counter format | Contador el formato | Contador formato | Счетчик формате | Counter-Format
Static Counter | Compteur statique | Static Counter | Contador estática | Static Contador | Статические Счетчик | Statische Counter
Event Counter | Compteur évènementielle | Event Counter | Contador eventa | Evento Contador | Событие Счетчик | Event Counter
Inter frame duration | Durée inter trame | Inter frame duration | Duración entre 2 fotogramas | Duração entre 2 frames | Продолжительность от 2 кадров | Inter frame duration
SBO timeout | Temps d'expiration pour la sélection avant opération | SBO timeout | Tiempo fuera SBO | Falha SBO | Задержка SBO | SBO Timeout
Spontaneous message enabled | Message spontané actif | Spontaneous message enabled | Espontáneo mensaje habilitado | Espontâneas mensagem ativado | Спонтанные сообщения позволили | Spontan Nachricht aktiviert
Spontaneous message class | Classe de message spontané | Spontaneous message class | Espontánea clase de mensaje | Espontâneas mensagem classe | Спонтанное сообщение класс | Spontan Nachrichtenklasse
SOE file support | Support de fichier SOE | SOE file support | Archivo de apoyo SOE | Arquivo apoio SOE | файл поддержки SOE | SOE file support
SOE file address | Adresse de fichier SOE | SOE file address | Archivo dirección SOE | Arquivo endereço SOE | файл адрес SOE | SOE file address
SOE file format | Format de fichier SOE | SOE file format | Formato de archivo SOE | Formato de arquivo SOE | файл формата SOE | SOE file format
SOE file nb of events | Nb d'évenements dans le fichier SOE | SOE file nb of events | Número de expediente de hechos SOE | Arquivo número de eventos SOE | файл ряд мероприятий SOE | SOE file nb of events
Full SOE file nb of events | Nb d'évenements dans le fichier SOE plein | Full SOE file nb of events | Completa número de expediente de hechos SOE | Arquivo completo conjunto de eventos SOE | полный файл SOE ряд мероприятий | Full SOE file nb of events
SPS Data Type | SPS Donnée de Type | SPS Data Type | SPS Datos tipo | SPS Dados tipo | SPS Тип данных | SPS Data Type
Event transmission | Transmission d'évènements | Event transmission | Transmisión de eventos | Transmissão de Eventos | Событие передачи | Event transmission
Inverted state | Etat Inversé | Inverted state | Estado invertido | Estado invertido | Инвертированное состояние | Inverted state
DPS Data Type | DPS Donnée de Type | DPS Data Type | DPS Datos tipo | DPS Dados tipo | DPS Тип данных | DPS Data Type
Event transmission | Transmission d'évènements | Event transmission | Transmisión de eventos | Transmissão de Eventos | Событие передачи | Event transmission
Inverted state | Etat Inversé | Inverted state | Estado invertido | Estado invertido | Инвертированное состояние | Inverted state
MPS Data Type | MPS Donnée de Type | MPS Data Type | MPS Datos tipo | MPS Dados tipo | MPS Тип данных | MPS Data Type
Event transmission | Transmission d'évènements | Event transmission | Transmisión de eventos | Transmissão de Eventos | Событие передачи | Event transmission
Bitstring usage | Utilisation du Bistring | Bitstring usage | Bitstring uso | Estado invertido | Bitstring использования | Bitstring Nutzung
SPC Data Type | SPC Donnée de Type | SPC Data Type | SPC Datos tipo | SPC Dados tipo | SPC Тип данных | SPC Data Type
SCADA order type | Type de commande SCADA | SCADA order type | Tipo de orden SCADA | Tipo de Ordem SCADA | Тип команды SCADA | SCADA order type
DPC Data Type | DPC Donnée de Type | DPC Data Type | DPC Datos tipo | DPC Dados tipo | DPC Тип данных | DPC Data Type
SCADA order type | Type de commande SCADA | SCADA order type | Tipo de orden SCADA | Tipo de Ordem SCADA | Тип команды SCADA | SCADA order type
MV Data Type | MV Donnée de Type | MV Data Type | MV Datos tipo | MV Dados tipo | MV Тип данных | MV Data Type
Event transmission | Transmission d'évènements | Event transmission | Transmisión de eventos | Transmissão de Eventos | Событие передачи | Event transmission
Format | Format | Format | Formato | Formato | Формат | Format
Minimum value | Valeur Min | Minimum value | Valor al mínimo | Valor ao Mínimo | Значение минимуму | Minimum value
Maximum value | Valeur Max | Maximum value | Valor al Máximo | Valor ao Máximo | Значение максимуму | Maximum value
Defined as counter | Défini comme compteur | Defined as counter | Definido como contador | Definido como contador | Определяется как борьба | Definiert als Zähler
Setpoint Data Type | SetPoint Donnée de Type | Setpoint Data Type | SetPoint Datos tipo | SetPoint Dados tipo | SetPoint Тип данных | Setpoint Data Type
SCADA order type | Type de commande SCADA | SCADA order type | Tipo de orden SCADA | Tipo de Ordem SCADA | Тип команды SCADA | SCADA order type
Format | Format | Format | Formato | Formato | Формат | Format
Minimum value | Valeur Min | Minimum value | Valor al mínimo | Valor ao Mínimo | Значение минимуму | Minimum value
Maximum value | Valeur Max | Maximum value | Valor al Máximo | Valor ao Máximo | Значение максимуму | Maximum value
Counter Data Type | Compteur de Donnée de Type | Counter Data Type | Counter Datos tipo | Contador de Dados tipo | Counter Тип данных | Counter Data Type
Event transmission | Transmission d'évènements | Event transmission | Transmisión de eventos | Transmissão de Eventos | Событие передачи | Event transmission
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : T104 Model | SHEET : Modèles T104 | SHEET : T104 Model | SHEET : Modelo T104 | SHEET : Modo T104 | SHEET : Модель T104 | SHEET : T104 Model
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
BEGIN SCADA T104 | DEBUT SCADA T104 | BEGIN SCADA T104 | COMIENZA SCADA T104 | INÍCIO SCADA T104 | НАЧАЛО ОПИСАНИЯ SCADA T104 | BEGIN SCADA T104
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
SCADA Protocol Name | Nom de protocole SCADA | SCADA Protocol Name | Nombre de Protocolo SCADA | Nome do Protocolo SCADA | SCADA ИМЯ Протокола | SCADA Protocol Name
Scada short name (16 char) | Nom court du SCADA (16 char) | Scada short name (16 char) | Nombre corto Scada (16 caract) | Nome Curto Scada (16 caract) | Сокращенное имя SCADA (16 символов) | Scada short name (16 char)
Protocol General Parameters | Paramètres généraux du Protocole | Protocol General Parameters | Parámetros generales del protocolo | Parâmetros Geração do Protocolo | Основные параметры протокола | Protocol General Parameters
Time Reference | Temps de référence | Time Reference | Tiempo de referencia | Tempo de referência | Время ссылку | Zeitplan
TCP/IP Address | Adresse TCP/IP | TCP/IP Address | TCP/IP Dirección | TCP/IP Endereço | TCP/IP Адрес | TCP/IP Address
Common address of ASDU | Adresse commune de l'ASDU | Common address of ASDU | Dirección común ASDU | Endereço comum ASDU | Общий адрес ASDU | Common address of ASDU
Address structure | Structure de l'adresse | Address structure | Estructura de la dirección | Estrutura do endereço | Структура решения | Struktur der Adresse
Frame max length | Longueur maximale de la vue | Frame max length | Longitud máx de la trama | Tamanho máx do frame | Максимальная длина кадра | Frame max length
Measurement periodic cycle | Cycle Périodique de Mesure | Measurement periodic cycle | Ciclo de medición periódico | Ciclo periódico de Medição | Периодический цикл измерений | Measurement periodic cycle
Binary Time Size | Taille de Temps binaire | Binary Time Size | Tamaño de tiempo binario | Tamanho Binário do Tempo | Размер двоичной кодировки времени | Binary Time Size
Background scan cycle | Cycle de balayage | Background scan cycle | Ciclo "background scan" | Ciclo "background scan" | Фоновый цикл сканирования | Background scan cycle
Connection timeout (T0) | Expiration de la Connexion (T0) | Connection timeout (T0) | Connection tiempo fuera (T0) | Falha de Conexão (T0) | Задержка соединения (T0) | Connection timeout (T0)
APDU timeout (T1) | Expiration de l'APDU (T1) | APDU timeout (T1) | APDU tiempo fuera (T1) | Falha APDU (T1) | Задержка APDU (T1) | APDU timeout (T1)
Acknowledgement timeout (T2) | Expiration de la Réception (T2) | Acknowledgement timeout (T2) | Acknowledgement tiempo fuera (T2) | Falha de Reconhecimento (T2) | Задержка подтвердения (T2) | Acknowledgement timeout (T2)
Test frame timeout (T3) | Expriration de la trame de test (T3) | Test frame timeout (T3) | Marco de tiempo de prueba (T3) | Teste moldura Timeout (T3) | Тест кадр тайм (T3) | Prüfung Timeout (T3)
Sent unack. Frames window size (K) | Taille de la fenêtre d'envoi d'acquis négatif | Sent unack. Frames window size (K) | Tamaño de ventana de tramas enviadas no reconocidas (K) | Tamanho de janelas de frames enviadas Não reconhecidas (K) | Sent unack. Frames window size (K) | Sent unack. Frames window size (K)
Ack. Received frames window size (W) | Taille de la fenêtre de réception d'acquis positif | Ack. Received frames window size (W) | Tamaño de ventana de tramas recibidas y reconocidas (W) | Tamanho de janelas de frames recebidas e reconhecidas (W) | Ack. Received frames window size (W) | Ack. Received frames window size (W)
Max command delay | Délai maximum de la Commande | Max command delay | Retardo de comando Máx | Retardo de comando Máx | Max command delay | Max command delay
Socket IP #1 | Socket IP #1 | Socket IP #1 | Socket IP #1 | Socket IP #1 | Socket IP #1 | Socket IP #1
Socket IP #2 | Socket IP #2 | Socket IP #2 | Socket IP #2 | Socket IP #2 | Socket IP #2 | Socket IP #2
Socket IP #3 | Socket IP #3 | Socket IP #3 | Socket IP #3 | Socket IP #3 | Socket IP #3 | Socket IP #3
Socket IP #4 | Socket IP #4 | Socket IP #4 | Socket IP #4 | Socket IP #4 | Socket IP #4 | Socket IP #4
SBO timeout | Temps d'expiration pour la sélection avant opération | SBO timeout | Tiempo fuera SBO | Falha SBO | Задержка SBO | SBO Timeout
Quality Value for 'Jammed' state | Valeur de Qualité de l'état 'Jammed' | Quality Value for 'Jammed' state | Valor de calidad 'atascado' estado | Qualidade Valor para 'emperrado' estado | Качество стоимость для 'застряла' состояния | Qualitäts für "gestaute" Zustand
Quality Value for toggling xPS | Valeur de Qualité de bascule xPS | Quality Value for toggling xPS | Valor de calidad para alternar XPS | Qualidade Valor para alternar xps | Качество стоимость для переключения XPS | Qualitäts für Makeln XPS
Quality Value for 'Unknown' state | Valeur de Qualité de l'état 'Inconnu' | Quality Value for 'Unknown' state | Valor de calidad 'Desconocido' estado | Qualidade Valor para 'Desconhecido' estado | Качество стоимость для 'Неизвестное' состояние | Qualitäts für "unbekannt" Zustand
Switchover | Switchover | Switchover | Switchover | Switchover | Switchover | Switchover
SOE file support | Support de fichier SOE | SOE file support | Archivo de apoyo SOE | Arquivo apoio SOE | файл поддержки SOE | SOE file support
SOE file address | Adresse de fichier SOE | SOE file address | Archivo dirección SOE | Arquivo endereço SOE | файл адрес SOE | SOE file address
SOE file format | Format de fichier SOE | SOE file format | Formato de archivo SOE | Formato de arquivo SOE | файл формата SOE | SOE file format
SOE file nb of events | Nb d'évenements dans le fichier SOE | SOE file nb of events | Número de expediente de hechos SOE | Arquivo número de eventos SOE | файл ряд мероприятий SOE | SOE file nb of events
Nb max of SOE files | Nombre maximum de fichiers SOE | Nb max of SOE files | número máximo de archivos de SOE | Número máximo de arquivos SOE | Максимальное количество SOE файлы | Nb max of SOE files
Full SOE file nb of events | Nb d'évenements dans le fichier SOE plein | Full SOE file nb of events | Completa número de expediente de hechos SOE | Arquivo completo conjunto de eventos SOE | полный файл SOE ряд мероприятий | Full SOE file nb of events
Disturbance file support | Support du fichier de Perturbographie | Disturbance file support | Perturbación archivo de apoyo | Perturbação arquivo apoio | Нарушение файл поддержки | Disturbance-Unterstützung
Disturbance file address | Adresse du fichier de Perturbographie | Disturbance file address | Perturbación archivo dirección | Perturbação arquivo endereço | Нарушение файл адрес | Disturbance-Adresse
Disturbance file address for T103 | Adresse du fichier de Perturbographie T103 | Disturbance file address for T103 | Perturbación archivo dirección T103 | Perturbação arquivo endereço T103 | Нарушение файл адрес T103 | Disturbance-Adresse T103
Disturbance file address for S20 | Adresse du fichier de Perturbographie S20 | Disturbance file address for S20 | Perturbación archivo dirección S20 | Perturbação arquivo endereço S20 | Нарушение файл адрес S20 | Disturbance-Adresse S20
Disturbance file address for M300 | Adresse du fichier de Perturbographie M300 | Disturbance file address for M300 | Perturbación archivo dirección M300 | Perturbação arquivo endereço M300 | Нарушение файл адрес M300 | Disturbance-Adresse M300
Disturbance file address for SlowWave | Adresse du fichier de Perturbographie SlowWave | Disturbance file address for SlowWave | Perturbación archivo dirección SlowWave | Perturbação arquivo endereço SlowWave | Нарушение файл адрес SlowWave | Disturbance-Adresse SlowWave
Disturbance file address for FastWave | Adresse du fichier de Perturbographie FastWave | Disturbance file address for FastWave | Perturbación archivo dirección FastWave | Perturbação arquivo endereço FastWave | Нарушение файл адрес FastWave | Disturbance-Adresse FastWave
Nb max of Disturbance files | Nombre maximum de fichiers de perturbographie | Nb max of Disturbance files | número máximo de archivos de perturbación | Número máximo de arquivos Perturbação | Максимальное количество нарушений файлы | maximale Anzahl von Dateien Disturbance
Buffer Overflow file support | Support du fichier de débordement de tampon | Buffer Overflow file support | Desbordamiento de búfer de archivo de apoyo | Buffer overflow arquivo apoio | Переполнение буфера файл поддержки | Buffer Overflow-Unterstützung
Buffer Overflow file address | Adresse du fichier de débordement de tampon | Buffer Overflow file address | Desbordamiento de búfer de archivo dirección | Buffer overflow arquivo endereço | Переполнение буфера файла адрес | Buffer Overflow-Datei-Adresse
Buffer Overflow empty condition | Condition vide de débordement de tampon | Buffer Overflow empty condition | Condición vacío de desbordamiento de búfer | Buffer overflow vazio condição | Переполнение буфера пустого состояния | Buffer Overflow leeren Zustand
SPS Data Type | SPS Donnée de Type | SPS Data Type | SPS Datos tipo | SPS Dados tipo | SPS Тип данных | SPS Data Type
Event transmission | Transmission d'évènements | Event transmission | Transmisión de eventos | Transmissão de Eventos | Событие передачи | Event transmission
Group [0-16] (0=no) | Groupes [0-16] (0=non) | Group [0-16] (0=no) | Grupo [0-16] (0=no) | Grupo [0-16] (0=não) | Группа [0-16] (0=no) | Gruppe [0-16] (0=no)
Priority | Prioritée | Priority | Prioridad | Prioridade[1-255] | Приоритет | Priority
Inverted state | Etat Inversé | Inverted state | Estado invertido | Estado invertido | Инвертированное состояние | Inverted state
Background scan | Balayage de fond | Background scan | Background scan | Background scan | Сканирование в фоновом режиме | Background scan
Event Record | Enregistrement d'évènement | Event Record | Registro de eventos | Registro de Eventos | Запись события | Event Record
DPS Data Type | DPS Donnée de Type | DPS Data Type | DPS Datos tipo | DPS Dados tipo | DPS Тип данных | DPS Data Type
Event transmission | Transmission d'évènements | Event transmission | Transmisión de eventos | Transmissão de Eventos | Событие передачи | Event transmission
Group [0-16] (0=no) | Groupes [0-16] (0=non) | Group [0-16] (0=no) | Grupo [0-16] (0=no) | Grupo [0-16] (0=não) | Группа [0-16] (0=no) | Gruppe [0-16] (0=no)
Priority | Prioritée | Priority | Prioridad | Prioridade[1-255] | Приоритет | Priority
Inverted state | Etat Inversé | Inverted state | Estado invertido | Estado invertido | Инвертированное состояние | Inverted state
Background scan | Balayage de fond | Background scan | Background scan | Background scan | Сканирование в фоновом режиме | Background scan
Event Record | Enregistrement d'évènement | Event Record | Registro de eventos | Registro de Eventos | Запись события | Event Record
MPS Data Type | MPS Donnée de Type | MPS Data Type | MPS Datos tipo | MPS Dados tipo | MPS Тип данных | MPS Data Type
Event transmission | Transmission d'évènements | Event transmission | Transmisión de eventos | Transmissão de Eventos | Событие передачи | Event transmission
Group [0-16] (0=no) | Groupes [0-16] (0=non) | Group [0-16] (0=no) | Grupo [0-16] (0=no) | Grupo [0-16] (0=não) | Группа [0-16] (0=no) | Gruppe [0-16] (0=no)
Priority | Prioritée | Priority | Prioridad | Prioridade[1-255] | Приоритет | Priority
Bitstring usage | Utilisation du Bistring | Bitstring usage | Bitstring uso | Estado invertido | Bitstring использования | Bitstring Nutzung
Background scan | Balayage de fond | Background scan | Background scan | Background scan | Сканирование в фоновом режиме | Background scan
Event Record | Enregistrement d'évènement | Event Record | Registro de eventos | Registro de Eventos | Запись события | Event Record
SPC Data Type | SPC Donnée de Type | SPC Data Type | SPC Datos tipo | SPC Dados tipo | SPC Тип данных | SPC Data Type
SCADA order type | Type de commande SCADA | SCADA order type | Tipo de orden SCADA | Tipo de Ordem SCADA | Тип команды SCADA | SCADA order type
SBO timeout [0-65535 s] | Temps d'expiration pour la sélection avant opération [0-65535 s] | SBO timeout [0-65535 s] | SBO tiempo fuera [0-65535 s] | Tempo Limite SBO[0-65535 s] | Задерка SBO [0-65535 с] | SBO timeout [0-65535 s]
DPC Data Type | DPC Donnée de Type | DPC Data Type | DPC Datos tipo | DPC Dados tipo | DPC Тип данных | DPC Data Type
SCADA order type | Type de commande SCADA | SCADA order type | Tipo de orden SCADA | Tipo de Ordem SCADA | Тип команды SCADA | SCADA order type
SBO timeout [0-65535 s] | Temps d'expiration pour la sélection avant opération [0-65535 s] | SBO timeout [0-65535 s] | SBO tiempo fuera [0-65535 s] | Tempo Limite SBO[0-65535 s] | Задерка SBO [0-65535 с] | SBO timeout [0-65535 s]
MV Data Type | MV Donnée de Type | MV Data Type | MV Datos tipo | MV Dados tipo | MV Тип данных | MV Data Type
Event transmission | Transmission d'évènements | Event transmission | Transmisión de eventos | Transmissão de Eventos | Событие передачи | Event transmission
Group [0-16] (0=no) | Groupes [0-16] (0=non) | Group [0-16] (0=no) | Grupo [0-16] (0=no) | Grupo [0-16] (0=não) | Группа [0-16] (0=no) | Gruppe [0-16] (0=no)
Priority | Prioritée | Priority | Prioridad | Prioridade[1-255] | Приоритет | Priority
Format | Format | Format | Formato | Formato | Формат | Format
Cycle Type | Type de Cycle | Cycle Type | Tipo de ciclo | Tipo de Ciclo | Тип цикла | Cycle Type
Event Record | Enregistrement d'évènement | Event Record | Registro de eventos | Registro de Eventos | Запись события | Event Record
Minimum value | Valeur Min | Minimum value | Valor al mínimo | Valor ao Mínimo | Значение минимуму | Minimum value
Maximum value | Valeur Max | Maximum value | Valor al Máximo | Valor ao Máximo | Значение максимуму | Maximum value
Setpoint Data Type | SetPoint Donnée de Type | Setpoint Data Type | SetPoint Datos tipo | SetPoint Dados tipo | SetPoint Тип данных | Setpoint Data Type
SCADA order type | Type de commande SCADA | SCADA order type | Tipo de orden SCADA | Tipo de Ordem SCADA | Тип команды SCADA | SCADA order type
Format | Format | Format | Formato | Formato | Формат | Format
Minimum value | Valeur Min | Minimum value | Valor al mínimo | Valor ao Mínimo | Значение минимуму | Minimum value
Maximum value | Valeur Max | Maximum value | Valor al Máximo | Valor ao Máximo | Значение максимуму | Maximum value
SBO timeout [0-65535 s] | Temps d'expiration pour la sélection avant opération [0-65535 s] | SBO timeout [0-65535 s] | SBO tiempo fuera [0-65535 s] | Tempo Limite SBO[0-65535 s] | Задерка SBO [0-65535 с] | SBO timeout [0-65535 s]
Counter Data Type | Compteur de Donnée de Type | Counter Data Type | Counter Datos tipo | Contador de Dados tipo | Counter Тип данных | Counter Data Type
Event transmission | Transmission d'évènements | Event transmission | Transmisión de eventos | Transmissão de Eventos | Событие передачи | Event transmission
Group [0-4] (0=no) | Groupes [0-4] (0=non) | Group [0-4] (0=no) | Grupo [0-4] (0=no) | Grupo [0-4] (0=não) | Группа [0-4] (0=no) | Gruppe [0-4] (0=no)
Priority | Prioritée | Priority | Prioridad | Prioridade[1-255] | Приоритет | Priority
Event Record | Enregistrement d'évènement | Event Record | Registro de eventos | Registro de Eventos | Запись события | Event Record
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : MODBUS Model | SHEET : Modèles MODBUS | SHEET : MODBUS Model | SHEET : Modelo MODBUS | SHEET : Modo MODBUS | SHEET : Модель MODBUS | SHEET : MODBUS Model
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
BEGIN SCADA MODBUS | DEBUT SCADA MODBUS | BEGIN SCADA MODBUS | COMIENZA SCADA MODBUS | INÍCIO SCADA MODBUS | НАЧАЛО ОПИСАНИЯ ПРОТОКОЛА SCADA MODBUS | BEGIN SCADA MODBUS
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
SCADA Protocol Name | Nom de protocole SCADA | SCADA Protocol Name | Nombre de Protocolo SCADA | Nome do Protocolo SCADA | SCADA ИМЯ Протокола | SCADA Protocol Name
Scada short name (16 char) | Nom court du SCADA (16 char) | Scada short name (16 char) | Nombre corto Scada (16 caract) | Nome Curto Scada (16 caract) | Сокращенное имя SCADA (16 символов) | Scada short name (16 char)
Protocol General Parameters | Paramètres généraux du Protocole | Protocol General Parameters | Parámetros generales del protocolo | Parâmetros Geração do Protocolo | Основные параметры протокола | Protocol General Parameters
Main communication channel | Voie de communication principale | Main communication channel | Canal de comunicación principal | Canal de Comunicação Principal | Основной канал связи | Main communication channel
Auxiliary Communication channel | Voie de communication auxiliaire | Auxiliary Communication channel | Canal de comunciación auxiliar | Canal de Comunicação auxiliar | Запасной канал связи | Auxiliary Communication channel
Baud rate (bit/s) | Vitesse de transmission (bit/s) | Baud rate (bit/s) | Baudios (bit/s) | Baud Rate (bit/s) | Скорость в бодах (бит/с) | Baud rate (bit/s)
TCP/IP usage | Utilise TCP/IP | TCP/IP usage | Uso de TCP/IP | Usos de TCP/IP | использование TCP/IP | TCP/IP usage
Link Address | Adresse du lien | Link Address | Dirección del vínculo | Endereço do Link | Адрес связи | Link Address
Inter frame duration | Durée inter trame | Inter frame duration | Duración entre 2 fotogramas | Duração entre 2 frames | Продолжительность от 2 кадров | Inter frame duration
Parity | Parité | Parity | Paridad | Paridade | Четность | Parity
SOE file support | Support de fichier SOE | SOE file support | Archivo de apoyo SOE | Arquivo apoio SOE | файл поддержки SOE | SOE file support
SOE file address | Adresse de fichier SOE | SOE file address | Archivo dirección SOE | Arquivo endereço SOE | файл адрес SOE | SOE file address
SOE file format | Format de fichier SOE | SOE file format | Formato de archivo SOE | Formato de arquivo SOE | файл формата SOE | SOE file format
SOE file nb of events | Nb d'évenements dans le fichier SOE | SOE file nb of events | Número de expediente de hechos SOE | Arquivo número de eventos SOE | файл ряд мероприятий SOE | SOE file nb of events
Full SOE file nb of events | Nb d'évenements dans le fichier SOE plein | Full SOE file nb of events | Completa número de expediente de hechos SOE | Arquivo completo conjunto de eventos SOE | полный файл SOE ряд мероприятий | Full SOE file nb of events
SPS Data Type | SPS Donnée de Type | SPS Data Type | SPS Datos tipo | SPS Dados tipo | SPS Тип данных | SPS Data Type
Inversion | Inversion | Inversion | Inversion | Inversão | Инверсия | Inversion
DPS Data Type | DPS Donnée de Type | DPS Data Type | DPS Datos tipo | DPS Dados tipo | DPS Тип данных | DPS Data Type
Double Address usage | Utilisation du Double Adressage | Double Address usage | Doble dirección de uso | Endereço duplo uso | адрес двойного использования | Double Address usage
Inversion | Inversion | Inversion | Inversion | Inversão | Инверсия | Inversion
MV Data Type | MV Donnée de Type | MV Data Type | MV Datos tipo | MV Dados tipo | MV Тип данных | MV Data Type
Format | Format | Format | Formato | Formato | Формат | Format
Precision [8-16] | Précision [8-16] | Precision [8-16] | Precisión [8-16] | Precisão [8-16] | Точность [8-16] | Precision [8-16]
Minimum value | Valeur Min | Minimum value | Valor al mínimo | Valor ao Mínimo | Значение минимуму | Minimum value
Maximum value | Valeur Max | Maximum value | Valor al Máximo | Valor ao Máximo | Значение максимуму | Maximum value
Setpoint Data Type | SetPoint Donnée de Type | Setpoint Data Type | SetPoint Datos tipo | SetPoint Dados tipo | SetPoint Тип данных | Setpoint Data Type
Format | Format | Format | Formato | Formato | Формат | Format
Counter Data Type | Compteur de Donnée de Type | Counter Data Type | Counter Datos tipo | Contador de Dados tipo | Counter Тип данных | Counter Data Type
Format | Format | Format | Formato | Formato | Формат | Format
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : OPC Model | SHEET : Modèles OPC | SHEET : OPC Model | SHEET : Modelo OPC | SHEET : Modo OPC | SHEET : Модель OPC | SHEET : OPC Model
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
BEGIN SCADA OPC | DEBUT SCADA OPC | BEGIN SCADA OPC | COMIENZA SCADA OPC | INÍCIO SCADA OPC | НАЧАЛО ОПИСАНИЯ SCADA OPC | BEGIN SCADA OPC
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
SCADA Protocol Name | Nom de protocole SCADA | SCADA Protocol Name | Nombre de Protocolo SCADA | Nome do Protocolo SCADA | SCADA ИМЯ Протокола | SCADA Protocol Name
Scada short name (16 char) | Nom court du SCADA (16 char) | Scada short name (16 char) | Nombre corto Scada (16 caract) | Nome Curto Scada (16 caract) | Сокращенное имя SCADA (16 символов) | Scada short name (16 char)
Protocol General Parameters | Paramètres généraux du Protocole | Protocol General Parameters | Parámetros generales del protocolo | Parâmetros Geração do Protocolo | Основные параметры протокола | Protocol General Parameters
OPC value for 'Reset' | OPC valeur pour 'Reset' | OPC value for 'Reset' | Valor OPC de 'Reajuste' | Valor OPC de 'Reajuste' | Значение OPC для статуса 'Reset' | OPC value for 'Reset'
OPC value for 'Set' | OPC valeur pour 'Set' | OPC value for 'Set' | Valor OPC de 'Ajuste' | Valor OPC de 'Ajuste' | Значение OPC для статуса 'Set' | OPC value for 'Set'
OPC value for 'Jammed' | OPC valeur pour 'Jammed' | OPC value for 'Jammed' | Valor OPC de 'Bloqueado' | Valor OPC de 'bloqueado' | Значение OPC для статуса 'Jammed' | OPC value for 'Jammed'
OPC value for 'Open' | OPC valeur pour 'Open' | OPC value for 'Open' | Valor OPC de 'Abierto' | Valor OPC de 'Aberto' | Значение OPC для статуса 'Open' | OPC value for 'Open'
OPC value for 'Closed' | OPC valeur pour 'Closed' | OPC value for 'Closed' | Valor OPC de 'Cerrado' | Valor OPC de 'Fechado' | Значение OPC для статуса 'Closed' | OPC value for 'Closed'
OPC value for 'Undefined' | OPC valeur pour 'Undefined' | OPC value for 'Undefined' | Valor OPC de 'Indefinido' | Valor OPC de 'Indefinido' | Значение OPC для статуса 'Undefined' | OPC value for 'Undefined'
OPC value for 'Order Open' (set to 01) | OPC valeur pour 'Order Open' (set to 01) | OPC value for 'Order Open' (set to 01) | Valor OPC de 'Orden de abierto' (estado 01) | Valor OPC de 'Ordem de Aberto' (estado 01) | Значение OPC для статуса 'Order Open' (установка в 01) | OPC value for 'Order Open' (set to 01)
OPC value for 'Order Close' (set to 10) | OPC valeur pour 'Order Close' (set to 10) | OPC value for 'Order Close' (set to 10) | Valor OPC de 'Orden de cerrado' (estado 10) | Valor OPC de 'Ordem de Fechado' (estado 10) | Значение OPC для статуса 'Order Close' (установка в 10) | OPC value for 'Order Close' (set to 10)
OPC value for 'Order Reset' | OPC valeur pour 'Order Reset' | OPC value for 'Order Reset' | Valor OPC de 'Order Reset' | Valor OPC de 'Order Reset' | Значение OPC для статуса 'Order Reset' | OPC value for 'Order Reset'
OPC value for 'Order Set' | OPC valeur pour 'Order Set' | OPC value for 'Order Set' | Valor OPC de 'Order Set' | Valor OPC de 'Order Set' | Значение OPC для статуса 'Order Set' | OPC value for 'Order Set'
OPC Bool value for 'Reset' | OPC Bool valeur pour 'Reset' | OPC Bool value for 'Reset' | Valor booleano OPC de 'Reset' | Valor booleano OPC de 'Reset' | OPC булево значение для 'Reset' | OPC Bool value for 'Reset'
OPC Bool value for 'Set' | OPC Bool valeur pour 'Set' | OPC Bool value for 'Set' | Valor booleano OPC de 'Set' | Valor booleano OPC de 'Set' | OPC булево значение для 'Set' | OPC Bool value for 'Set'
OPC Bool value for 'Jammed' | OPC Bool valeur pour 'Jammed' | OPC Bool value for 'Jammed' | Valor booleano OPC de 'Jammed' | Valor booleano OPC de 'Jammed' | OPC булево значение для 'Jammed' | OPC Bool value for 'Jammed'
OPC Bool value for 'Open' | OPC Bool valeur pour 'Open' | OPC Bool value for 'Open' | Valor booleano OPC de 'Open' | Valor booleano OPC de 'Open' | OPC булево значение для 'Open' | OPC Bool value for 'Open'
OPC Bool value for 'Closed' | OPC Bool valeur pour 'Closed' | OPC Bool value for 'Closed' | Valor booleano OPC de 'Closed' | Valor booleano OPC de 'Closed' | OPC булево значение для 'Closed' | OPC Bool value for 'Closed'
OPC Bool value for 'Undefined' | OPC Bool valeur pour 'Undefined' | OPC Bool value for 'Undefined' | Valor booleano OPC de 'Undefined' | Valor booleano OPC de 'Undefined' | OPC булево значение для 'Undefined' | OPC Bool value for 'Undefined'
OPC Bool value for 'Order Open' (set to 01) | OPC Bool valeur pour 'Order Open' (set to 01) | OPC Bool value for 'Order Open' (set to 01) | Valor booleano OPC de 'Order Open' (set to 01) | Valor booleano OPC de 'Order Open' (set to 01) | OPC булево значение для 'Order Open' (set to 01) | OPC Bool value for 'Order Open' (set to 01)
OPC Bool value for 'Order Close' (set to 10) | OPC Bool valeur pour 'Order Close' (set to 10) | OPC Bool value for 'Order Close' (set to 10) | Valor booleano OPC de 'Order Close' (set to 10) | Valor booleano OPC de 'Order Close' (set to 10) | OPC булево значение для 'Order Close' (set to 10) | OPC Bool value for 'Order Close' (set to 10)
OPC Bool value for 'Order Reset' | OPC Bool valeur pour 'Order Reset' | OPC Bool value for 'Order Reset' | Valor booleano OPC de 'Order Reset' | Valor booleano OPC de 'Order Reset' | OPC булево значение для 'Order Reset' | OPC Bool value for 'Order Reset'
OPC Bool value for 'Order Set' | OPC Bool valeur pour 'Order Set' | OPC Bool value for 'Order Set' | Valor booleano OPC de 'Order Set' | Valor booleano OPC de 'Order Set' | OPC булево значение для 'Order Set' | OPC Bool value for 'Order Set'
OPC quality for 'SelfCheckFault' | OPC qualité pour 'SelfCheckFault' | OPC quality for 'SelfCheckFault' | Calidad OPC de 'SelfCheckFault' | Qualidade OPC de 'SelfCheckFault' | OPC качество 'SelfCheckFault' | OPC quality for 'SelfCheckFault'
OPC quality for 'Unknown' | OPC qualité pour 'Unknown' | OPC quality for 'Unknown' | Calidad OPC de 'Unknown' | Qualidade OPC de 'Unknown' | OPC качество 'Unknown' | OPC quality for 'Unknown'
OPC quality for 'Toggling' | OPC qualité pour 'Toggling' | OPC quality for 'Toggling' | Calidad OPC de 'Toggling' | Qualidade OPC de 'Toggling' | OPC качество 'Toggling' | OPC quality for 'Toggling'
OPC quality for 'Suppressed' | OPC qualité pour 'Suppressed' | OPC quality for 'Suppressed' | Calidad OPC de 'Suppressed' | Qualidade OPC de 'Suppressed' | OPC качество 'Suppressed' | OPC quality for 'Suppressed'
OPC quality for 'Forced' | OPC qualité pour 'Forced' | OPC quality for 'Forced' | Calidad OPC de 'Forced' | Qualidade OPC de 'Forced' | OPC качество 'Forced' | OPC quality for 'Forced'
OPC quality for 'Substituted' | OPC qualité pour 'Substituted' | OPC quality for 'Substituted' | Calidad OPC de 'Substituted' | Qualidade OPC de 'Substituted' | OPC качество 'Substituted' | OPC quality for 'Substituted'
OPC quality for 'Undefined' MPS MV Counter | OPC qualité pour 'Undefined' MPS MV Compteur | OPC quality for 'Undefined' MPS MV Counter | Calidad OPC de 'Undefined' MPS MV Counter | Qualidade OPC de 'Undefined' MPS MV Counter | OPC качество 'Undefined' MPS MV Counter | OPC quality for 'Undefined' MPS MV Counter
OPC quality for 'OverRange' MPS MV Counter | OPC qualité pour 'OverRange' MPS MV Compteur | OPC quality for 'OverRange' MPS MV Counter | Calidad OPC de 'OverRange' MPS MV Counter | Qualidade OPC de 'OverRange' MPS MV Counter | OPC качество 'OverRange' MPS MV Counter | OPC quality for 'OverRange' MPS MV Counter
OPC quality for 'OpenCircuit' MPS MV Counter | OPC qualité pour 'OpenCircuit' MPS MV Compteur | OPC quality for 'OpenCircuit' MPS MV Counter | Calidad OPC de 'OpenCircuit' MPS MV Counter | Qualidade OPC de 'OpenCircuit' MPS MV Counter | OPC качество 'OpenCircuit' MPS MV Counter | OPC quality for 'OpenCircuit' MPS MV Counter
OPC quality for 'LLLThreshold' | OPC qualité pour 'LLLThreshold' | OPC quality for 'LLLThreshold' | Calidad OPC de 'LLLThreshold' | Qualidade OPC de 'LLLThreshold' | OPC качество 'LLLThreshold' | OPC quality for 'LLLThreshold'
OPC quality for 'LLThreshold' | OPC qualité pour 'LLThreshold' | OPC quality for 'LLThreshold' | Calidad OPC de 'LLThreshold' | Qualidade OPC de 'LLThreshold' | OPC качество 'LLThreshold' | OPC quality for 'LLThreshold'
OPC quality for 'LThreshold' | OPC qualité pour 'LThreshold' | OPC quality for 'LThreshold' | Calidad OPC de 'LThreshold' | Qualidade OPC de 'LThreshold' | OPC качество 'LThreshold' | OPC quality for 'LThreshold'
OPC quality for 'HThreshold' | OPC qualité pour 'HThreshold' | OPC quality for 'HThreshold' | Calidad OPC de 'HThreshold' | Qualidade OPC de 'HThreshold' | OPC качество 'HThreshold' | OPC quality for 'HThreshold'
OPC quality for 'HHThreshold' | OPC qualité pour 'HHThreshold' | OPC quality for 'HHThreshold' | Calidad OPC de 'HHThreshold' | Qualidade OPC de 'HHThreshold' | OPC качество 'HHThreshold' | OPC quality for 'HHThreshold'
OPC quality for 'HHHThreshold' | OPC qualité pour 'HHHThreshold' | OPC quality for 'HHHThreshold' | Calidad OPC de 'HHHThreshold' | Qualidade OPC de 'HHHThreshold' | OPC качество 'HHHThreshold' | OPC quality for 'HHHThreshold'
OPC quality for 'Jammed' DPS | OPC qualité pour 'Jammed' DPS | OPC quality for 'Jammed' DPS | Calidad OPC de 'Jammed' DPS | Qualidade OPC de 'Jammed' DPS | OPC качество 'Jammed' DPS | OPC quality for 'Jammed' DPS
OPC quality for 'Undefined' DPS | OPC qualité pour 'Undefined' DPS | OPC quality for 'Undefined' DPS | Calidad OPC de 'Undefined' DPS | Qualidade OPC de 'Undefined' DPS | OPC качество 'Undefined' DPS | OPC quality for 'Undefined' DPS
OPC quality for 'Valid Set/Closed' | OPC qualité pour 'Valid Set/Closed' | OPC quality for 'Valid Set/Closed' | Calidad OPC de 'Valid Set/Closed' | Qualidade OPC de 'Valid Set/Closed' | OPC качество 'Valid Set/Closed' | OPC quality for 'Valid Set/Closed'
OPC quality for 'Valid Reset/Open' | OPC qualité pour 'Valid Reset/Open' | OPC quality for 'Valid Reset/Open' | Calidad OPC de 'Valid Reset/Open' | Qualidade OPC de 'Valid Reset/Open' | OPC качество 'Valid Reset/Open' | OPC quality for 'Valid Reset/Open'
SPS Data Type | SPS Donnée de Type | SPS Data Type | SPS Datos tipo | SPS Dados tipo | SPS Тип данных | SPS Data Type
Historization | Historisation | Historization | Histórico | Histórico | исторический | Historischen
Format | Format | Format | Formato | Formato | Формат | Format
Inverted state | Etat Inversé | Inverted state | Estado invertido | Estado invertido | Инвертированное состояние | Inverted state
DPS Data Type | DPS Donnée de Type | DPS Data Type | DPS Datos tipo | DPS Dados tipo | DPS Тип данных | DPS Data Type
Double Address usage | Utilisation du Double Adressage | Double Address usage | Doble dirección de uso | Endereço duplo uso | адрес двойного использования | Double Address usage
Historization | Historisation | Historization | Histórico | Histórico | исторический | Historischen
Format | Format | Format | Formato | Formato | Формат | Format
Inverted state | Etat Inversé | Inverted state | Estado invertido | Estado invertido | Инвертированное состояние | Inverted state
MPS Data Type | MPS Donnée de Type | MPS Data Type | MPS Datos tipo | MPS Dados tipo | MPS Тип данных | MPS Data Type
Historization | Historisation | Historization | Histórico | Histórico | исторический | Historischen
SPC Data Type | SPC Donnée de Type | SPC Data Type | SPC Datos tipo | SPC Dados tipo | SPC Тип данных | SPC Data Type
Format | Format | Format | Formato | Formato | Формат | Format
DPC Data Type | DPC Donnée de Type | DPC Data Type | DPC Datos tipo | DPC Dados tipo | DPC Тип данных | DPC Data Type
Format | Format | Format | Formato | Formato | Формат | Format
Double Address usage | Utilisation du Double Adressage | Double Address usage | Doble dirección de uso | Endereço duplo uso | адрес двойного использования | Double Address usage
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : Connections | SHEET : Connectique | SHEET : Connections | SHEET : Conexiones | SHEET : Conexões | SHEET : Связи | SHEET : Connections
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
BEGIN DATA | DEBUT DES DONNEES | BEGIN DATA | INICIO DE DATOS | INICIO DOS DADOS | НАЧАЛО ДАННЫХ | BEGIN DATA
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : Column Presence Checking | SHEET : Présence des Colonnes | SHEET : Column Presence Checking | SHEET : Columna de verificación | SHEET : Checkup Coluna de Presença | SHEET : Графа проведения проверки | SHEET : Column Presence Checking
This sheet is to be used to indicate the cells/columns that are : | Cette FEUILLE est utilisée pour indiquer les cellules/colonnes qui sont : | This sheet is to be used to indicate the cells/columns that are : | Esta hoja se utiliza para indicar las celdas/columnas que están : | Esta Ficha se utiliza para indicar as céluas/colunas que estão : | Этот лист используется для выделения ячеек/колонок, которые : | This sheet is to be used to indicate the cells/columns that are :
- P : present in all corresponding sheets but the contents shall not be used by automatic tools | - P : présentes dans toute les FEUILLES mais dont le contenu ne sera pas employé par les outils automatiques | - P : present in all corresponding sheets but the contents shall not be used by automatic tools | - P : presentes en todas las hojas correspondientes pero los contenidos no se deben utilizar por herramientas automáticas | - P : Presentes em todas as Fichas correspondentes mas o conteúdo não podem ser utilizados por Ferramentas Automáticas | -P : представлены во всех соответствующих листах, но содержание м.б. не использовано автоматич. Утилитами | - P : present in all corresponding sheets but the contents shall not be used by automatic tools
- U : present in all corresponding sheets and shall be used by automatic tools | - U : présentes dans toutes les FEUILLES et seront employées par les outils automatiques | - U : present in all corresponding sheets and shall be used by automatic tools | - U : presentes en todas las hojas correspondientes y se deben utilizar por herramientas automáticas | - U : Presentes em todas as Fichas correspondentes e devem se utilizar por Ferramentas Automáticas | -U : представлены во всех соответствующих листах и м.б. использованы автоматич. Утилитами | - U : present in all corresponding sheets and shall be used by automatic tools
- A : not present in corresponding sheets | - A : Absentes des FEUILLES | - A : not present in corresponding sheets | - A : no presentes en las hojas correspondientes | - A : Não Presentes nas Fichas correspondentes | -A : не представлены во всех соответствующих листах | - A : not present in corresponding sheets
- PH : hide in all corresponding sheets but the contents shall not be used by automatic tools | - PH :cachées dans toute les FEUILLES mais le contenu ne sera pas employée par les outils automatiques | - PH : hide in all corresponding sheets but the contents shall not be used by automatic tools | - PH : ocultas en todas las hojas correspondientes pero los contenidos no se deben utilizar por herramientas automáticas | - PH : Ocultas em todas as Fichas correspondentes mas o conteúdo não podem ser utilizados por Ferramentas Automáticas | -PH : скрыты во всех соответствующих листах, но содержание м.б. не использовано автоматич. Утилитами | - PH : hide in all corresponding sheets but the contents shall not be used by automatic tools
- UH : hide in all corresponding sheets and shall be used by automatic tools | - UH :cachées dans toutes les FEUILLES et seront employées par les outils automatiques | - UH : hide in all corresponding sheets and shall be used by automatic tools | - UH : ocultas en todas las hojas correspondientes y se deben utilizar por herramientas automáticas | - UH : Ocultas em todas as Fichas correspondentes e devem se utilizar por Ferramentas Automáticas | -UH : скрыты во всех соответствующих листах и м.б. использованы автоматич. Утилитами | - UH : hide in all corresponding sheets and shall be used by automatic tools
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
MiCOM CXXX DESCRIPTION | MiCOM CXXX DESCRIPTION | MiCOM CXXX DESCRIPTION | Descripción MiCOM CXXX | Descrição MiCOM CXXX | ОПИСАНИЕ MiCOM CXXX | MiCOM CXXX DESCRIPTION
DI GROUPS | GROUPES DES ENTREES NUMERIQUES | DI GROUPS | Grupos DI | Grupos DI | Группы DI | DI GROUPS
SELF GENERATED DIGITAL INFORMATION | ENTREES NUMERIQUES AUTOMATIQUES | SELF GENERATED DIGITAL INFORMATION | INFORMACION DIGITAL AUTO GENERADA | Informação Digital Auto Gerada | ЦИФРОВАЯ ИНФОРМАЦИЯ, СГЕНЕРИРОВАННАЯ | SELBSTGENERIERTE DIGITAL INFORMATION
SELF GENERATED DIGITAL OUTPUT INFORMATION | SORTIES NUMERIQUES AUTOMATIQUES | SELF GENERATED DIGITAL OUTPUT INFORMATION | INFORMACION DE SALIDAS DIGITALES AUTO GENERADAS | Informação de saidas Digitais Auto Geradas | ИНФОРМАЦИЯ, СГЕНЕРИРОВАННАЯ ЦИФРОВЫМИ ВЫХОДАМИ | SELBSTGENERIERTE DIGITAL OUTPUT INFORMATION
SELF GENERATED ANALOG INFORMATION | ENTREES ANALOGIQUES AUTOMATIQUES | SELF GENERATED ANALOG INFORMATION | INFORMACION ANALOGICA AUTO GENERADA | Informação Analógica Auto Gerada | АНАЛОГОВАЯ ИНФОРМАЦИЯ, СГЕНЕРИРОВАННАЯ | SELBSTGENERIERTE ANALOG INFORMATION
SHEET : Column Default Value | SHEET : Valeurs par Défaut | SHEET : Column Default Value | SHEET : Valor por defecto de columna | SHEET : Valor padrão da Coluna | SHEET : Графа стандартных величин | SHEET : Column Default Value
This sheet is used to set default parameter value for each data. | Cette FEUILLE est employée pour remplacer des valeurs par de nouvelles. | This sheet is used to set default parameter value for each data. | Esta hoja se utiliza para ajustar el parámetro por defecto para cada dato | Esta Ficha se utiliza para ajustar os parâmetros de defeitos para cada dado. | Этот лист применяется при установке стандартного значения параметра для каждого данного | This sheet is used to set default parameter value for each data.
- set the Old parameter value to change in the "Old Value" line | - placez l'ancienne valeur de paramètre dans la ligne "Ancienne valeur" | - set the Old parameter value to change in the "Old Value" line | - Ajusta el valor del parámetro anterior que se va a cambiar en la línea: "Valor anterior" | - Ajusta o Valor do parâmetro anterior usado para Sobrescrever na linha: "Valor anterior" | - установите старые значения параметров, выбрав строку "Old Value" | - set the Old parameter value to change in the "Old Value" line
- set the New parameter value used to overwrite Old one in the "New Value" line | - placez la nouvelle valeur du paramètre dans la ligne "Nouvelle valeur" | - set the New parameter value used to overwrite Old one in the "New Value" line | - Ajusta el valor del parámetro anterior que se va a cambiar en la línea: "Valor nuevo" | - Ajusta o Valor do parámetro anterior usado para Sobrescrever na linha: "Valor novo" | - установите новые значения параметров, перезаписав старые значения в строке "New Value" | - set the New parameter value used to overwrite Old one in the "New Value" line
- It is possible to use regular expressions as 'Old value' to locate data by using: | - Il est possible d'employer des expressions régulières pour filtrer les "Anciennes valeurs". | - It is possible to use regular expressions as 'Old value' to locate data by using: | - Es posible utilizar expresiones regulares como 'Valor anterior' para localozar datos utilizando: | - É possível utilizar expressões regulares como 'Valor anterior' para localizar Dados utilizando: | - Возможно использование определ. значения в линии "Old Value" для группы данных путем использования: | - It is possible to use regular expressions as 'Old value' to locate data by using:
? Any single character. | ? Tout caractère simple. | ? Any single character. | ? Cualquier caracter sencillo. | ? qualquer caracter Simples. | знака "?" для любого одиночного символа | ? Any single character.
* Zero or more characters. | * Zéro caractère ou plus. | * Zero or more characters. | * Cero o más caracteres. | * Zero ou mais Caracteres. | знака "*" для обозначения большего количества символов или не использования символов | * Zero or more characters.
# Any single digit (0-9). | # Tout chiffre simple (0-9). | # Any single digit (0-9). | # Cuaquier dígito sencillo (0-9). | # Qualquer dígito Simples (0-9). | знака "#" для обозначения любой цифры (0-9) | # Any single digit (0-9).
[charlist] Any single character in charlist. | [charlist] Tout caractère simple dans charlist. | [charlist] Any single character in charlist. | [caractlist] Cualquier caracter simple en la lista de caracteres. | [caractlist] qualquer caracter Simples da Lista de caracteres. | [charlist] Любой единичный символ из charlist | [charlist] Any single character in charlist.
[!charlist] Any single character not in charlist. | [!charlist] Tout caractère simple non compris dans charlist. | [!charlist] Any single character not in charlist. | [!caractlist] Cualquier caracter simple no incluido en la lista de caracteres. | [!caractlist] qualquer caracter Simples não incluido na Lista de caracteres. | [!charlist] Любой единичный символ не из charlist | [!charlist] Any single character not in charlist.
- A group of one or more characters (charlist) enclosed in brackets ([ ]) can be used to | - un groupes d'un ou plusieurs caractères (charlist) inclus entre crochets ([ ]) peut être employé à | - A group of one or more characters (charlist) enclosed in brackets ([ ]) can be used to | - Un grupo de uno o más caracteres (lista de caracteres) entre corchetes ([ ]) se puede utilizar para | - Um grupo de um o mais caracteres (Lista de caracteres) entre colchetes ([ ]) pode-se utilizar para | Группа из одного или нескольких символов (charlist), заключенная в квадратные скобки ([ ]), м.б. Использована | - A group of one or more characters (charlist) enclosed in brackets ([ ]) can be used to
match any single character in string and can include almost any character code, | partir de n'importe quel caractère simple dans la chaine et pouvant inclure presque n'importe quel code de caractère, | match any single character in string and can include almost any character code, | enlazar cualquier caracter sencillo en cadena y puede incluir casi cualquier código de caracteres | armazenar qualquer caracter Simples em string e pode incluir quase qualquer código de caracteres | для обозначения любого одиночного символа в строке и может включать практически любой символьный код, | match any single character in string and can include almost any character code,
including digits. | y compris des chiffres. | including digits. | incluyendo dígitos. | incluindo dígitos. | включая цифры. | including digits.
- Note: To match the special characters left bracket ([), question mark (?), number sign (#), | - note : pour utiliser les caractères spéciaux tels le crochet ouvrant ([), le point d'interrogation (?), le signe de nombre (#), | - Note: To match the special characters left bracket ([), question mark (?), number sign (#), | - Nota: Para enlazar los caracteres especiales corchete izquierdo ([), signo de interrogación (?), signo de número (#), | - Nota: Para armazenar os caracteres Especiais colchete esquerdo ([), seguido de interrogacão (?), seguido do número (#), | - Примечание: для обозначения символов левой скобки ([), вопроса (?), числа (#), звездочки (*), заключайте | - Note: To match the special characters left bracket ([), question mark (?), number sign (#),
and asterisk (*), enclose them in brackets. The right bracket (]) can't be used within a group | et l'astérisque (*), les mettre entre crochets. Le crochet droit (]) ne peut pas être utilisé dans un Groupes | and asterisk (*), enclose them in brackets. The right bracket (]) can't be used within a group | y asterisco, se deben poner entre corchetes. El corchete derecho (]) no se puede utilizar dentro de un grupo | e asterisco, se devem ser colocados entre colchetes. O colchete direito (]) não pode ser utilizado dentro de um grupo | их в квадратные скобки. Правая скобка (]), должна использоваться вместе с соответствующей группой символов, | and asterisk (*), enclose them in brackets. The right bracket (]) can't be used within a group
to match itself, but it can be used outside a group as an individual character. | de sélection, mais peut être employé en dehors | to match itself, but it can be used outside a group as an individual character. | para enlazarse a si mismo, pero se puede utilizar fuera de un grupo como un carácter individual. | para armazenar a si mesmo, mas pode-se utilizar fora de um grupo como un carácter individual. | При использовании дефиса (-) для отделения верхних и нижних границ диапазона, charlist может определять | to match itself, but it can be used outside a group as an individual character.
- By using a hyphen (-) to separate the upper and lower bounds of the range, charlist can | - en employant un trait d'union (-) pour séparer les limites supérieures et inférieures de la liste, charlist peut | - By using a hyphen (-) to separate the upper and lower bounds of the range, charlist can | - Mediante el uso de un guión (-) para separar los extremos superior e inferior del rango, la lista de caracteres puede | - Mediante eo uso de um hífem (-) para separar os extremos superior e inferior do Range, a Lista de caracteres pode | несколько символов. Например, [A-Z] пишется в случае, если в соответствующих позициях в строке | - By using a hyphen (-) to separate the upper and lower bounds of the range, charlist can
specify a range of characters. For example, [A-Z] results in a match if the corresponding | indiquer une liste des caractères. Par exemple, [ A-Z ] correspond a toutes les lettres majuscules de l'alphabet. | specify a range of characters. For example, [A-Z] results in a match if the corresponding | especificar un rango de caracteres. Por ejemplo, [A-Z] da como resultado un conjunto si la posición correspondiente | especificar um Range de caracteres. Por exemplo, [A-Z] da como resultado um conjunto se a posição correspondente | встречаются любые заглавные буквы в диапазоне A-Z. Диапазон заключается в квадратные скобки без | specify a range of characters. For example, [A-Z] results in a match if the corresponding
character position in string contains any uppercase letters in the range A-Z. Multiple ranges | Les listes multiples sont incluses dans | character position in string contains any uppercase letters in the range A-Z. Multiple ranges | al carácter en cadena contiene algunas letras en mayúsculas en el rango A-Z. Múltiples rangos | ao caracter em string Possui algumas letras em maiúsculass no Range A-Z. Multiplos Ranges estarão incluidos | использования | character position in string contains any uppercase letters in the range A-Z. Multiple ranges
are included within the brackets without delimiters. | les crochets sans délimiteurs. | are included within the brackets without delimiters. | están incluidos dentro de los corchetes sin delimitadores. | dentro dos colchetes sem domitadores. | ограничителей. | are included within the brackets without delimiters.
Example: | Exemple: | Example: | Ejemplo: | Exemplo: | Примеры: | Example:
aBBBa' is like 'a*a' | aBBBa' est reconnu par l'expression régulière 'a*a' | aBBBa' is like 'a*a' | aBBBa' es similar 'a*a' | aBBBa' é igual 'a*a' | aBBBa' аналогично 'a*a' | aBBBa' is like 'a*a'
F' is like '[A-Z]' | F' est reconnu par l'expression régulière '[A-Z]' | F' is like '[A-Z]' | F' es similar '[A-Z]' | F' é igual '[A-Z]' | F' аналогично '[A-Z]' | F' is like '[A-Z]'
F' is NOT like '[!A-Z]' | F' n'est pas reconnu par l'expression régulière '[!A-Z]' | F' is NOT like '[!A-Z]' | F' NO es similar '[!A-Z]' | F' Não é igual a '[!A-Z]' | F' НЕ аналогично '[!A-Z]' | F' is NOT like '[!A-Z]'
a2a' is like 'a#a' | a2a' est reconnu par l'expression régulière 'a#a' | a2a' is like 'a#a' | a2a' es similar 'a#a' | a2a' é igual a 'a#a' | a2a' НЕ аналогично 'a#a' | a2a' is like 'a#a'
aM5b' is like 'a[L-P]#[!c-e]' | aM5b' est reconnu par l'expression régulière 'a[L-P]#[!c-e]' | aM5b' is like 'a[L-P]#[!c-e]' | aM5b' es similar 'a[L-P]#[!c-e]' | aM5b' é igual a '[L-P]#[!c-e]' | aM5b' аналогично 'a[L-P]#[!c-e]' | aM5b' is like 'a[L-P]#[!c-e]'
BAT123khg' is like 'B?T*' | BAT123khg' est reconnu par l'expression régulière 'B?T*' | BAT123khg' is like 'B?T*' | BAT123khg' es similar 'B?T*' | BAT123khg' é igual a 'B?T*' | BAT123khg' аналогично 'B?T*' | BAT123khg' is like 'B?T*'
CAT123khg' is NOT like 'B?T*' | CAT123khg' n'est pas reconnu par l'expression régulière 'B?T*' | CAT123khg' is NOT like 'B?T*' | CAT123khg' NO es similar 'B?T*' | CAT123khg' Não é igual a 'B?T*' | CAT123khg' НЕ аналогично 'B?T*' | CAT123khg' is NOT like 'B?T*'
Old Value | Ancienne valeur | Old Value | Valor anterior | Valor anterior | Старое значение | Old Value
New Value | Nouvelle valeur | New Value | Valor nuevo | Valor novo | Новое значение | New Value
SHEET : Column Selection For Data Copy | SHEET : Sélection Colonnes pour Copie | SHEET : Column Selection For Data Copy | SHEET : Selección de columna para Copia | SHEET : Seleção de Coluna para Cópia | SHEET : Выбор колонок для копирования данных | SHEET : Column Selection For Data Copy
This sheet is to be used to indicate the cells/columns for which the contents shall be copied to a new DataList release. | Cette FEUILLE est utilisée pour indiquer les cellules pour lesquelles le contenu sera copié dans une nouvelle version de Dataliste. | This sheet is to be used to indicate the cells/columns for which the contents shall be copied to a new DataList release. | Esta hoja se utiliza para indicar las celdas/columnas para las cuales los contenidos deben ser copiados a una versión | Esta Ficha se utiliza para indicar as céluas/colunas para as quais os conteúdos devem ser copiados a uma versão | Лист используется при выделении ячеек/колонок, содержимое которых м.б. скопировано в новую версию DataList. | This sheet is to be used to indicate the cells/columns for which the contents shall be copied to a new DataList release.
The possible values are : | Les valeurs possibles sont : | The possible values are : | nueva de lista de datos. Los valores posibles son : | nova de Lista de Dados. os Valores possíveis são : | Возможные значения: | The possible values are :
- N : do not copy in any case | - N : ne pas copier | - N : do not copy in any case | - N : No copiar en cualquier caso | - N : Não copiar em qualquer caso | -N : не копировать в любом случае | - N : do not copy in any case
- C : copy in any case (when the line is significant) | - C : copier de toute façon (quand la ligne est significative) | - C : copy in any case (when the line is significant) | - C : copiar solo en cierto caso (cuando la línea es significativa) | - C : Copiar só em certo caso (quando a linha é significativa) | -С : копировать в любом случае (если линия является значимой) | - C : copy in any case (when the line is significant)
- E : copy only if the cell within new release is empty | - E : copier seulement si la cellule dans la nouvelle version est vide | - E : copy only if the cell within new release is empty | - E : copiar solamente si la celda dentro de la nueva versión está vacía | - E : Copiar somente se a célula dentro da nova versão está vazia | -Е : копировать только в те ячейки, в которых новая версия отсутствует | - E : copy only if the cell within new release is empty
SHEET : Matrix | SHEET : Matrix | SHEET : Matrix | SHEET : Matrix | SHEET : Matrix | SHEET : Matrix | SHEET : Matrix
This sheet indicates the cells/columns used for building comparison criteria. | Cette FEUILLE indique les cellules/colonnes utilisées pour définir des critères de comparaison. | This sheet indicates the cells/columns used for building comparison criteria. | Esta hoja indica las celdas/columnas utilizadas para construir criterios de comparación | Esta Ficha indica as céluas/colunas utilizadas para construir criterios de comparação | Лист используется при выделении ячеек/колонок, используемых для построения критерия сравнения | This sheet indicates the cells/columns used for building comparison criteria.
The possible values are : | Les valeurs possibles sont : | The possible values are : | nueva de lista de datos. Los valores posibles son : | nova de Lista de Dados. os Valores possíveis são : | Возможные значения: | The possible values are :
- P : present in all corresponding sheets but the contents shall not be used to build comparison criteria | - P : présent dans tout la FEUILLE correspondante mais le contenu ne sera pas employé comme Critère de comparaison | - P : present in all corresponding sheets but the contents shall not be used to build comparison criteria | - P : presente en todas las hojas correspondientes pero los contenidos no deben ser utilizados para construir criterios de comparación | - P : Presente em todas as Fichas correspondentes mas os conteúdos não devem ser utilizados para construir criterios de comparação | -P : присутствует во всех соответствующих листах, но содержание не м.б. использовано для построения критерия | - P : present in all corresponding sheets but the contents shall not be used to build comparison criteria
- U : present in all corresponding sheets and shall be used to build comparison criteria | - U : présent dans toute les FEUILLEs et sera utilisé pour établir un critère de comparaison | - U : present in all corresponding sheets and shall be used to build comparison criteria | - U : presente en todas las hojas correspondientes y deben ser utilizados para construir criterios de comparación | - U : Presente em todas as Fichas correspondentes e devem ser utilizados para construir criterios de comparação | -U : присутствует во всех соответствующих листах и м.б. использовано для построения критерия | - U : present in all corresponding sheets and shall be used to build comparison criteria
Use this Matrix Case | Utiliser ce cas de Matrix | Use this Matrix Case | Caso utilizar ésta Matriz | Caso utilizar ésta Matriz | Используйте данных матричный блок | Use this Matrix Case
SHEET : HELP_C264 | SHEET : AIDE C264 | SHEET : HELP_C264 | SHEET : AYUDA C264 | SHEET : AJUDA C264 | SHEET : Помощь по C264 | SHEET : HELP_C264
COUNTER INFORMATION FROM IED | ENTREES COMPTEUR DE l'IED | COUNTER INFORMATION FROM IED | INFORMACION CONTADOR DESDE IED | Informação CONTADOR deste IED | Информация счетчика с IED | COUNTER INFORMATION FROM IED
IED name | NOM DE l'IED | IED name | NOMBRE DE IED | Nome do IED | Имя IED | IED name
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
IED Counter Reference | Référence de la carte d'entrée Compteur de l'IED | IED Counter Reference | Referencia Contador IED | Referência Contador IED | Ссылка счетчика IED | IED Counter Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Link | Lien | Link | Vínculo | Vínculo | Связь | Link
Local Display | Affichage Local | Local Display | Despliegue Local | Display Local | Локальный дисплей | Local Display
HMI | HMI | HMI | IHM | IHM | HMI | HMI
Special | Spécial | Special | Especial | Especial | Специальный | Special
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Information Adresse T103: ASDU nb;Fonction type MODBUS: Mapping Adresse;InputFormat DNP3: Adresse IEC: LD;LN T10X MASTER: Information Adresse | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address | T101: Dirección de información T103: ASDU no;Tipo de función MODBUS: Dirección de mapeo;InputFormat DNP3: Dirección IEC: LD;LN T10X MASTER: Dirección de información | T101: Endereço de Informação T103: ASDU no;Tipo de Função MODBUS: Endereço de Mapeamento;InputFormat DNP3: Endereço IEC: LD;LN T10X MASTER: Endereço de Informação | T101: адрес информации T103: Номер ASDU ;Тип функции MODBUS: Адрес сигнала;InputFormat DNP3: Адрес IEC: LD;LN T10X MASTER: адрес информации | T101: Information Address T103: ASDU nb;Function type MODBUS: Mapping address;InputFormat DNP3: Address IEC: LD;LN T10X MASTER: Information Address
T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101:Adresse Commune ASDU T103: Information nb;Adresse CommuneASDU MODBUS: Fonction DNP3: Non utilisé IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Adresse Commune ASDU;Data type | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type | T101: Dirección común ASDU T103: No. de información;Dirección común ASDU MODBUS: Función DNP3: No utilizado IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Dirección común ASDU;Data type | T101: Endereço comum ASDU T103: No. de Informação;Endereço comum ASDU MODBUS: Função DNP3: Não Utilizado IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Endereço comum ASDU;Data type | T101: Общий адрес ASDU T103: информационный номер;Общий адрес ASDU MODBUS: Функция DNP3: Не используется IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Общий адрес ASDU;Data type | T101: Common address ASDU T103: Information nb;Common address ASDU MODBUS: Function DNP3: Not used IEC: FC;Data Object;DataAttribute;CDC T10X MASTER: Common address ASDU;Data type
Function | Fonction | Function | Función | Função | Функция | Function
Unit | Unité | Unit | Unidad | Unidade | Плата | Unit
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Counter Type | Type du Compteur | Counter Type | Tipo de Contador | Tipo de Contador | Противодействие Тип | Counter Type
Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Standard: Validation (ms);Invalidité (ms);Cumul (mn) Energy: Facteur d'echelle;Periode de transmission (mn) | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Estándar: Válidación (ms);Inválidación (ms);Cumulación (mn) Energía: Factor de posicionamiento;Periode de la transmisión (mn) | Padrão: Validação (ms);Invalidação (ms);Cumulação (mn) Energia: Fator de escala;Periode da transmissão (mn) | Стандарт: Проверка (мс);Invalidity (ms);Cumul (mn) Энергия: Scale factor;Период передачи (мс) | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn)
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
LCD Display | Affichage LCD | LCD Display | Pantalla LCD | Vista LCD | LCD Дисплей | LCD Display
HMI Display | Affichage HMI | HMI Display | Pantalla IHM | Vista IHM | HMI Дисплей | HMI Display
Integrate MV | Intègre la MV | Integrate MV | Integrate MV | Integrate MV | Integrate MV | Integrate MV
Trend Viewer | Archivé | Trend Viewer | Archivado | Arquivado | Просмотр кривых | Trend Viewer
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
SELF GENERATED COUNTER INFORMATION | ENTREES COMPTEUR AUTOMATIQUES | SELF GENERATED COUNTER INFORMATION | INFORMACION CONTADOR AUTO GENERADA | Informação CONTADOR Auto Gerada | Информация, сгенерированная счетчиком | SELBSTGENERIERTE COUNTER INFORMATION
SELF GENERATED COUNTER INFORMATION | ENTREES COMPTEUR AUTOMATIQUES | SELF GENERATED COUNTER INFORMATION | INFORMACION CONTADOR AUTO GENERADA | Informação CONTADOR Auto Gerada | Информация, сгенерированная счетчиком | SELBSTGENERIERTE COUNTER INFORMATION
SELF GENERATED COUNTER INFORMATION | ENTREES COMPTEUR AUTOMATIQUES | SELF GENERATED COUNTER INFORMATION | INFORMACION CONTADOR AUTO GENERADA | Informação CONTADOR Auto Gerada | Информация, сгенерированная счетчиком | SELBSTGENERIERTE COUNTER INFORMATION
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
Self Counter Reference | Référence interne du compteur | Self Counter Reference | Referencia Contador auto | Referência Contador Automática | Собственная ссылка Противодействие | Self Counter Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Link | Lien | Link | Vínculo | Vínculo | Связь | Link
Local Display | Affichage Local | Local Display | Despliegue Local | Display Local | Локальный дисплей | Local Display
HMI | HMI | HMI | IHM | IHM | HMI | HMI
Special | Spécial | Special | Especial | Especial | Специальный | Special
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
Number | Numéro | Number | Número | Número | Номер | Number
Function | Fonction | Function | Función | Função | Функция | Function
Unit | Unité | Unit | Unidad | Unidade | Плата | Unit
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Counter Type | Type du Compteur | Counter Type | Tipo de Contador | Tipo de Contador | Противодействие Тип | Counter Type
Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Standard: Validation (ms);Invalidité (ms);Cumul (mn) Energy: Facteur d'echelle;Periode de transmission (mn) | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn) | Estándar: Válidación (ms);Inválidación (ms);Cumulación (mn) Energía: Factor de posicionamiento;Periode de la transmisión (mn) | Padrão: Validação (ms);Invalidação (ms);Cumulação (mn) Energia: Fator de escala;Periode da transmissão (mn) | Стандарт: Проверка (мс);Invalidity (ms);Cumul (mn) Энергия: Scale factor;Период передачи (мс) | Standard: Validation (ms);Invalidity (ms);Cumul (mn) Energy: Scale factor;Transmission period (mn)
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
LCD Display | Affichage LCD | LCD Display | Pantalla LCD | Vista LCD | LCD Дисплей | LCD Display
HMI Display | Affichage HMI | HMI Display | Pantalla IHM | Vista IHM | HMI Дисплей | HMI Display
Integrate MV | Intègre la MV | Integrate MV | Integrate MV | Integrate MV | Integrate MV | Integrate MV
Trend Viewer | Archivé | Trend Viewer | Archivado | Arquivado | Просмотр кривых | Trend Viewer
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Automation Origin (if any) | Automatisme d'origine (si existant) | Automation Origin (if any) | Automation Origin (if any) | Automation Origin (if any) | Automation Origin (if any) | Automation Origin (if any)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
Counter Profiles | Profils Compteurs | Counter Profiles | Perfiles de Contador | Perfis de Contador | Профили счетчика | Counter Profiles
System Counter Profiles | Profils Compteurs systèmes | System Counter Profiles | Perfiles de systema de Contador | Perfis de Systema de Contador | Профили системного счетчика | System Counter Profiles
Function Name | Nom de la fonction | Function Name | Nombre de función | Nome da Função | Функция Name | Function Name
SCE Name (13 char) | Nom dans le SCE (13 char) | SCE Name (13 char) | Nombre SCE (13 caract) | Nome SCE (13 caract) | Имя SCE (13 символов) | SCE Name (13 char)
Counter General Parameters | Paramètres généraux du Compteur | Counter General Parameters | Parámetros generales Contador | Parâmetros Geração Contador | Основные параметры Борьба | Counter General Parameters
Energy equivalent to a pulse | Energie équivalente à un pulse | Energy equivalent to a pulse | Equivalente en energía a un pulso | Energia equivalente a um pulso | Energy equivalent to a pulse | Energy equivalent to a pulse
Computation | Calculé | Computation | Cómputación | Computação | Вычисление | Computation
SBMC dependant | Dépendance SBMC | SBMC dependant | SBMC dependiente | SBMC dependente | SBMC иждивенца | SBMC unterhaltsberechtigte
Graphical Default Format | Format graphique par défaut | Graphical Default Format | Formato gráfico del defecto | Formato gráfico do defeito | Стандартный графический формат | Graphical Default Format
Associated Alarm Parameters | Paramètres d'alarme associés à la MV | Associated Alarm Parameters | Associated Alarm Parameters | Associated aoarm Parameters | Параметры тревоги | Associated Alarm Parameters
Generation Condition | Condition de la Génération | Generation Condition | Condición de generación | Condição de Geração | Основное условие | Generation Condition
Audible Alarm | Alarme audible | Audible Alarm | Alarma audible | Alarme Auditível | Звуковая тревога | Audible Alarm
Clearing Mode | Mode d'effacement | Clearing Mode | Modo Clearing | Modo de Limpeza | Режим очистки | Clearing Mode
Alarm appearance delay (0-120 s) | Retard d'apparition de l'alarme (0-120 s) | Alarm appearance delay (0-120 s) | Retardo de aparición de Alarma (0-120 s) | Retardo de aparição de Alarme (0-120 s) | Задержка появления тревоги (0-120 с) | Alarm appearance delay (0-120 s)
Counter Processing Parameters | Paramètres de traitement du Compteur | Counter Processing Parameters | Parámetros de procesamiento Contador | Parâmetros de Processamento Contador | Парметры обработки Борьба | Counter Processing Parameters
Valid state label | Libellé de l'état valide | Valid state label | Etiqueta de estado válido | Etiqueta de estado válido | Метка статуса Valid | Valid state label
SelfCheckFault state label | Libellé de l'état d'auto vérification du défaut | SelfCheckFault state label | Etiqueta de estado FallaAutoChequeo | Etiqueta de estado FalhaAutoCheque | Метка статуса SelfCheckFault | SelfCheckFault state label
Unknown state label | Libellé de l'état inconnu | Unknown state label | Etiqueta de estado desconocido | Etiqueta de estado Desconhecido | Метка статуса Unknown | Unknown state label
Forced state label | Libellé de l'état forcé | Forced state label | Etiqueta de estado forzado | Etiqueta de estado Forçado | Метка статуса Forced | Forced state label
OverRange state label | Libellé de l'état au-dessus de l'échelle | OverRange state label | Etiqueta de estado fuera de rango | Etiqueta de estado fora de Range | Метка статуса OverRange | OverRange state label
Undefined state label | Libellé de l'état indéfini | Undefined state label | Etiqueta de estado Indefinido | Etiqueta de estado Indefinido | Метка статуса Undefined | Undefined state label
Treatment on Valid state | Traitement sur l'état valide | Treatment on Valid state | Manipulación en estado válido | Manipulação em estado válido | Обработка статуса Valid | Treatment on Valid state
Treatment on SelfCheckFault state | Traitement sur l'état d'auto vérification du défaut | Treatment on SelfCheckFault state | Manipulación en estado FallaAutoChequeo | Manipulação em estado FalhaAutoCheque | Обработка статуса SelfCheckFault | Treatment on SelfCheckFault state
Treatment on Unknown state | Traitement sur l'état inconnu | Treatment on Unknown state | Manipulación en estado Desconocido | Manipulação em estado Desconhecido | Обрабока статуса Unknown | Treatment on Unknown state
Treatment on Forced state | Traitement sur l'état forcé | Treatment on Forced state | Manipulación en estado Forzado | Manipulação em estado Forçado | Обработка статуса Forced | Treatment on Forced state
Treatment on OverRange state | Traitement sur l'état au-dessus de l'échelle | Treatment on OverRange state | Manipulación en estado fuera de rango | Manipulação em estado fora de Range | Обработка статуса OverRange | Treatment on OverRange state
Treatment on Undefined state | Traitement sur l'état indéfini | Treatment on Undefined state | Manipulación en estado Indefinido | Manipulação em estado Indefinido | Обработка статуса Undefined | Treatment on Undefined state
Treatment on Forcing state | Traitement sur l'état de forçage | Treatment on Forcing state | Manipulación en estado Forzando | Manipulação em estado Forzando | Обработка статуса Forcing | Treatment on Forcing state
Treatment on Substitution state | Traitement sur l'état de substitution | Treatment on Substitution state | Manipulación en estado por sustitución | Manipulação em estado por Substituição | Обработка статуса Substitution | Treatment on Substitution state
Treatment on Suppression state | Traitement sur l'état de suppression | Treatment on Suppression state | Manipulación en estado por supresión | Manipulação em estado por Supressão | Обработка статуса Suppression | Treatment on Suppression state
Alarm and Gravity on Valid state | Gravité d'alarme sur l'état valide | Alarm and Gravity on Valid state | Alarma y gravedad en estado valido | Alarme e gravidade em estado vaoido | Тревога и важность статуса Valid | Alarm and Gravity on Valid state
Alarm and Gravity on SelfCheckFault state | Gravité d'alarme sur l'état d'auto vérification du défaut | Alarm and Gravity on SelfCheckFault state | Alarma y gravedad en estado FallaAutoChequeo | Alarme e gravidade em estado FalhaAutoCheque | Тревога и важность статуса SelfCheckFault | Alarm and Gravity on SelfCheckFault state
Alarm and Gravity on Unknown state | Gravité d'alarme sur l'état inconnu | Alarm and Gravity on Unknown state | Alarma y gravedad en estado desconocido | Alarme e gravidade em estado Desconhecido | Тревога и важность статуса Unknown | Alarm and Gravity on Unknown state
Alarm and Gravity on Forced state | Gravité d'alarme sur l'état forcé | Alarm and Gravity on Forced state | Alarma y gravedad en estado forzado | Alarme e gravidade em estado Forçado | Тревога и важность статуса Forced | Alarm and Gravity on Forced state
Alarm and Gravity on OverRange state | Gravité d'alarme sur l'état au-dessus de l'échelle | Alarm and Gravity on OverRange state | Alarma y gravedad en estado fuera de rango | Alarme e gravidade em estado fora de Range | Тревога и важность статуса OverRange | Alarm and Gravity on OverRange state
Alarm and Gravity on Undefined state | Gravité d'alarme sur l'état indéfini | Alarm and Gravity on Undefined state | Alarma y gravedad en estado Indefinido | Alarme e gravidade em estado Indefinido | Тревога и важность статуса Undefined | Alarm and Gravity on Undefined state
Counter Printing Parameters | Paramètres d'impression du Compteur | Counter Printing Parameters | Parámetros de impresión Contador | Parâmetros de Impressão Contador | Параметры печати Борьба | Counter Printing Parameters
Printed on Sequence Of Events SOE 1 : | Imprimer sur l'imprimante Fil de l'eau 1 : | Printed on Sequence Of Events SOE 1 : | Impreso en SOE 1 : | Impresso em SOE 1 : | Вывод на SOE 1 : | Printed on Sequence Of Events SOE 1 :
Printed on Sequence Of Events SOE 2 : | Imprimer sur l'imprimante Fil de l'eau 2 : | Printed on Sequence Of Events SOE 2 : | Impreso en SOE 2 : | Impresso em SOE 1 : | Вывод на SOE 2 : | Printed on Sequence Of Events SOE 2 :
Printed on Logbook LB 1 : | Imprimer sur l'imprimante Journal de Bord 1 : | Printed on Logbook LB 1 : | Impreso en LB 1 : | Impresso em LB 1 : | Вывод на LB 1 : | Printed on Logbook LB 1 :
Printed on Logbook LB 2 : | Imprimer sur l'imprimante Journal de Bord 2 : | Printed on Logbook LB 2 : | Impreso en LB 2 : | Impresso em LB 2 : | Вывод на LB 2 : | Printed on Logbook LB 2 :
ANALOG OUTPUT BOARD AOU20x | Carte de sorties analogiques AOU20x | ANALOG OUTPUT BOARD AOU20x | TARJETAS DE SALIDAS ANALOGICAS AOU20x | Etiquetas de Saídas Analógicas AOU20x | ПЛАТЫ AOU20x | ANALOGE AUSGANGSKARTE AOU20x
Analog Output Board Number | Numéro de la carte de sorties analogiques | Analog Output Board Number | Número de tarjeta de salidas analógicas | Número de Etiqueta de Saídas Analógicas | Номер платы AO | Analogausgangskarten Nummer
Analog Output Board Slot | Position de la carte de sortie analogiques | Analog Output Board Slot | Slot de Tarjeta de salidas analógicas | Slot do Cartão de Saídas Analógicas | Слот платы AO | Analogausgangskarten Steckplatz
Analog Output Extension Rack Number | Numéro rack d'extension de la carte de sorties analogiques | Analog Output Extension Rack Number | Tarjeta de salidas analógicas Extensión Rack Número | Etiqueta de Saídas Analógicas Extensão Rack Número | продлению стойки Количество AO | Analogausgangskarten Extension Rack Nummer
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
AO Reference | Référence AO | AO Reference | Referencia AO | Referência AO | Ссылка AO | AO Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Local Display | Affichage Local | Local Display | Despliegue Local | Display Local | Локальный дисплей | Local Display
HMI | HMI | HMI | IHM | IHM | HMI | HMI
Special | Spécial | Special | Especial | Especial | Специальный | Special
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
Slot | Position | Slot | Slot | Slot | Слот | Slot
Channel | Voie | Channel | Canal | Canal | Канал | Channel
Function | Fonction | Function | Función | Função | Функция | Function
Unit | Unité | Unit | Unidad | Unidade | Плата | Unit
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Corresponding Minimal Value | Correspond à la valeur minimum | Corresponding Minimal Value | Valor correspondiente al mínimo | Valor correspondente ao Mínimo | Значение соответствующее минимуму | Corresponding Minimal Value
Corresponding Maximal Value | Correspond à la valeur maximum | Corresponding Maximal Value | Valor correspondiente al Máximo | Valor correspondente ao Máximo | Значение соответствующее максимуму | Corresponding Maximal Value
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
LCD Display | Affichage LCD | LCD Display | Pantalla LCD | Vista LCD | LCD Дисплей | LCD Display
HMI Display | Affichage HMI | HMI Display | Pantalla IHM | Vista IHM | HMI Дисплей | HMI Display
Trend Viewer | Archivé | Trend Viewer | Archivado | Arquivado | Просмотр кривых | Trend Viewer
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
SELF GENERATED SETPOINT INFORMATION | SORTIES SETPOINT AUTOMATIQUES | SELF GENERATED SETPOINT INFORMATION | INFORMACION SETPOINT AUTO GENERADA | Informação SETPOINT Auto Gerada | Информация, сгенерированная SetPoint | SELBSTGENERIERTE SETPOINT INFORMATION
SELF GENERATED SETPOINT INFORMATION | SORTIES SETPOINT AUTOMATIQUES | SELF GENERATED SETPOINT INFORMATION | INFORMACION SETPOINT AUTO GENERADA | Informação SETPOINT Auto Gerada | Информация, сгенерированная SetPoint | SELBSTGENERIERTE SETPOINT INFORMATION
SELF GENERATED SETPOINT INFORMATION | SORTIES SETPOINT AUTOMATIQUES | SELF GENERATED SETPOINT INFORMATION | INFORMACION SETPOINT AUTO GENERADA | Informação SETPOINT Auto Gerada | Информация, сгенерированная SetPoint | SELBSTGENERIERTE SETPOINT INFORMATION
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
SetPoint Reference | Référence SetPoint | SetPoint Reference | Referencia SetPoint | Referência SetPoint | Ссылка SetPoint | SetPoint Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Local Display | Affichage Local | Local Display | Despliegue Local | Display Local | Локальный дисплей | Local Display
HMI | HMI | HMI | IHM | IHM | HMI | HMI
Special | Spécial | Special | Especial | Especial | Специальный | Special
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
Number | Numéro | Number | Número | Número | Номер | Number
Function | Fonction | Function | Función | Função | Функция | Function
Unit | Unité | Unit | Unidad | Unidade | Плата | Unit
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Corresponding Minimal Value | Correspond à la valeur minimum | Corresponding Minimal Value | Valor correspondiente al mínimo | Valor correspondente ao Mínimo | Значение соответствующее минимуму | Corresponding Minimal Value
Corresponding Maximal Value | Correspond à la valeur maximum | Corresponding Maximal Value | Valor correspondiente al Máximo | Valor correspondente ao Máximo | Значение соответствующее максимуму | Corresponding Maximal Value
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
LCD Display | Affichage LCD | LCD Display | Pantalla LCD | Vista LCD | LCD Дисплей | LCD Display
HMI Display | Affichage HMI | HMI Display | Pantalla IHM | Vista IHM | HMI Дисплей | HMI Display
Trend Viewer | Archivé | Trend Viewer | Archivado | Arquivado | Просмотр кривых | Trend Viewer
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Automation Origin (if any) | Automatisme d'origine (si existant) | Automation Origin (if any) | Automation Origin (if any) | Automation Origin (if any) | Automation Origin (if any) | Automation Origin (if any)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
SHEET : IEC61850 Model | SHEET : Modèles IEC61850 | SHEET : IEC61850 Model | SHEET : Modelo IEC61850 | SHEET : Modo IEC61850 | SHEET : Модель IEC61850 | SHEET : IEC61850 Model
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
BEGIN SCADA IEC 61850 | DEBUT SCADA IEC 61850 | BEGIN SCADA IEC 61850 | COMIENZA SCADA IEC 61850 | INÍCIO SCADA IEC 61850 | НАЧАЛО ОПИСАНИЯ SCADA IEC 61850 | BEGIN SCADA IEC 61850
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
SCADA Protocol Name | Nom de protocole SCADA | SCADA Protocol Name | Nombre de Protocolo SCADA | Nome do Protocolo SCADA | SCADA ИМЯ Протокола | SCADA Protocol Name
Scada short name (16 char) | Nom court du SCADA (16 char) | Scada short name (16 char) | Nombre corto Scada (16 caract) | Nome Curto Scada (16 caract) | Сокращенное имя SCADA (16 символов) | Scada short name (16 char)
Protocol General Parameters | Paramètres généraux du Protocole | Protocol General Parameters | Parámetros generales del protocolo | Parâmetros Geração do Protocolo | Основные параметры протокола | Protocol General Parameters
TCP/IP Address | Adresse TCP/IP | TCP/IP Address | TCP/IP Dirección | TCP/IP Endereço | TCP/IP Адрес | TCP/IP Address
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
DSP210 BOARD | Carte DSP210 | DSP210 BOARD | TARJETAS DSP210 | Placas DSP210 | ПЛАТЫ DSP210 | KARTE DSP210
DSP210 Board Number | Numéro de la carte DSP210 | DSP210 Board Number | Número de tarjeta DSP210 | Número de Etiqueta de DSP210 | Номер платы DSP210 | DSP210 karte Nummer
DSP210 Board Slot | Position de la carte DSP210 | DSP210 Board Slot | Slot de trajeta DSP210 | Slot de trajeta de DSP210 | Слот платы DSP210 | DSP210 karte Steckplatz
DSP210 Extension Rack Number | Numéro rack d'extension de la carte DSP210 | DSP210 Extension Rack Number | Tarjeta DSP210 Extensión Rack Número | Etiqueta de DSP210 Extensão Rack Número | продлению стойки Количество DSP210 | DSP210 Extension Rack Nummer
Iss. | Rév. | Iss. | Rev. | Rev. | Вер. | Iss.
Customer Ref | Réf. Client | Customer Ref | Ref Cliente | Ref Cliente | Ссылка заказчика | Kundenreferenz
DO Reference | Référence DO | DO Reference | Referencia DO | Referência DO | Ссылка DO | DO Reference
Electrical Data | Données électriques | Electrical Data | Datos Eléctricos | Dados Elétricos | Данные электрической части | Elektrische Datumn
Description | Description | Description | Descripción | Descrição | Описание | Beschreibung
Labels | Libellés | Labels | Etiquetas | Etiquetas | Метки | Labels
Scada Interface | Interface Scada | Scada Interface | Interfaz Scada | Interface Scada | Scada интерфейс | FW Interface
Local Control | Contrôle Local | Local Control | Control Local | Controle Local | местного контроля | Local Control
HMI | HMI | HMI | IHM | IHM | HMI | HMI
DI/DO Link | Lien DI/DO | DI/DO Link | DI/DO Vínculo | DI/DO Vínculo | DI/DO связи | DI/DO Link
Automation | Automatisme | Automation | Automatización | Automação | Автоматика | Automation
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
Conf. Mng. | Conf. Mng. | Conf. Mng. | Admin. Config. | Admin. Config. | Управление конфигурацией | Conf. Mng.
IEC Interface | Interface IEC | IEC Interface | Interfaz IEC | Interface IEC | IEC интерфейс | IEC Interface
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Panel Number | Numéro d'armoire | Panel Number | Número de panel | Número do Painel | Номер панели | Panel Number
Tag Number | Numéro d'étiquette | Tag Number | Número de etiquetado | Número do Tag | Номер тега | Tag Number
Slot | Position | Slot | Slot | Slot | Слот | Slot
Channel | Voie | Channel | Canal | Canal | Канал | Channel
Function | Fonction | Function | Función | Função | Функция | Function
Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Type (SPC=Simple/DPC=Double/DS=Dual Switch) | Type (SPC=Single/DPC=Dual/DS=Dual Switch) | Tipo (SPC=Sencilla/DPC=Dual/DS=Dual Switch) | Tipo (SPC=Simples/DPC=Duplo/DS=Dual Switch) | Тип (SPC=Single/DPC=Dual/DS=Dual Switch) | Type (SPC=Single/DPC=Dual/DS=Dual Switch)
Voltage Level Short Name (16 char) | Niveau de tension Nom court (16 car) | Voltage Level Short Name (16 char) | Nivel de voltaje Nombre Corto (16 caract) | Nivel de Tensão Nome Curto (16 caract) | Уровень напряжения Краткое имя (16 символов) | Spannungsebene Short Name (16 char)
Bay Short Name (16 char) | Tranche Nom court (16 car) | Bay Short Name (16 char) | Bahía Nombre Corto (16 caract) | Painel Nome Curto (16 caract) | Имя ячейки Краткое имя (16 символов) | FELD Short Name (16 char)
Module Short Name (16 char) | Module Nom court (16 car) | Module Short Name (16 char) | Módulo Nombre Corto (16 caract) | Módulo Nome Curto (16 caract) | Имя Краткое имя (16 символов) | Modul Short Name (16 char)
Long name (35 char) | Nom long (35 car) | Long name (35 char) | Nombre largo (35 caract) | Nome Longo (35 caract) | Полное имя (35 символов) | Long name (35 char)
Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Simple : Texte à l'état électrique = 1 Double : Texte à l'état électrique = 10 (16 car) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char) | Sencilla : Texto en estado eléctrico = 1 Dual : Texto en estado eléctrico = 10 (16 caract) | Simples: Texto em estado Elétrico = 1 Duplo : Texto em estado Elétrico = 10 (16 caract) | Одиночный : Обозначение электрического состояния = 1 Двойной : Обозначение электрического состояния = 10 (16 символов) | Single : Text at electrical state = 1 Dual : Text at electrical state = 10 (16 char)
Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Simple : Texte à l'état électrique = 0 Double : Texte à l'état électrique =01 (16 car) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char) | Sencilla : Texto en estado eléctrico = 0 Dual : Texto en estado eléctrico = 01 (16 caract) | Simples: Texto em estado Elétrico = 0 Duplo : Texto em estado Elétrico = 01 (16 caract) | Одиночный : Обозначение электрического состояния = 0 Двойной : Обозначение электрического состояния = 01 (16 символов) | Single : Text at electrical state = 0 Dual : Text at electrical state = 01 (16 char)
Short Name (16 char) | Nom court (16 car) | Short Name (16 char) | Nombre Corto (16 caract) | Nome Curto (16 caract) | Краткое имя (16 символов) | Short Name (16 char)
SCADA 1 Address | SCADA 1 Adresse | SCADA 1 Address | SCADA 1 Dirección | SCADA 1 Endereço | SCADA 1 Адрес | SCADA 1 Address
SCADA1 Data type | SCADA 1 Type de donnée | SCADA1 Data type | SCADA1 Tipo de dato | SCADA1 Tipo de Dado | SCADA1 Тип данных | SCADA1 Data type
SCADA 2 Address | SCADA 2 Adresse | SCADA 2 Address | SCADA 2 Dirección | SCADA 2 Endereço | SCADA 2 Адрес | SCADA 2 Address
SCADA2 Data type | SCADA 2 Type de donnée | SCADA2 Data type | SCADA2 Tipo de dato | SCADA2 Tipo de Dado | SCADA2 Тип данных | SCADA2 Data type
SCADA 3 Address | SCADA 3 Adresse | SCADA 3 Address | SCADA 3 Dirección | SCADA 3 Endereço | SCADA 3 Адрес | SCADA 3 Address
SCADA3 Data type | SCADA 3 Type de donnée | SCADA3 Data type | SCADA3 Tipo de dato | SCADA3 Tipo de Dado | SCADA3 Тип данных | SCADA3 Data type
SCADA 4 Address | SCADA 4 Adresse | SCADA 4 Address | SCADA 4 Dirección | SCADA 4 Endereço | SCADA 4 Адрес | SCADA 4 Address
SCADA4 Data type | SCADA 4 Type de donnée | SCADA4 Data type | SCADA4 Tipo de dato | SCADA4 Tipo de Dado | SCADA4 Тип данных | SCADA4 Data type
LCD Control | Contrôle LCD | LCD Control | Control LCD | Ordem desde LCD | Управление LCD | LCD Control
HMI Control | Contrôle HMI | HMI Control | Control IHM | Ordem desde IHM | Управление HMI | HMI Control
Has a xPS Feedback | A un retour de position xPS | Has a xPS Feedback | Contiene retroalimentación xPS | Possui FeedBack xPS | имеет xPS отзывы | Has a xPS Feedback
Is activated by xPS | Est activé par xPS | Is activated by xPS | Es activado por xPS | É ativado por xPS | Активируется с помощью xPS | Is activated by xPS
Used by ISaGRAF | Utilisé par ISaGRAF | Used by ISaGRAF | ISaGRAF | Nome ISaGRAF (8 car) | Используется ISaGRAFом | Used by ISaGRAF
Relay | Relais | Relay | Relé | Relé | Реле | Relay
Bay Name (in SCE Template) or Bay Type | Nom de la Tranche (dans le modèle du SCE) ou Type de la Tranche | Bay Name (in SCE Template) or Bay Type | Nombre de bahía (en plantilla SCE) o tipo de bahía | Nome do Painel (em Panilha SCE) ou tipo do Painel | Имя ячейки (в SCE шаблоне) или ячейки типа | Bay Name (in SCE Template) or Bay Type
Module Name (in SCE Template) or Module Type | Nom du Module (dans le modèle du SCE) ou Type du Module | Module Name (in SCE Template) or Module Type | Nombre de módulo (en plantilla SCE) o tipo de módulo | Nome do Módulo (em Panilha SCE) ou tipo do Módulo | Имя модуля (в SCE шаблоне) или модуля типа | Module Name (in SCE Template) or Module Type
Datapoint Name (in SCE Template) or Datapoint Type | Nom du Point de Donnée (dans le modèle du SCE) ou Type du Point de Donnée | Datapoint Name (in SCE Template) or Datapoint Type | Nombre del dato (en plantilla SCE) o tipo del dato | Nome do Dado (em Panilha SCE) ou tipo do Dado | Имя точки данных (в SCE шаблоне) или точки данных типа | Datapoint Name (in SCE Template) or Datapoint Type
Process | Utiliser | Process | Proceso | Processo | Процесс | Process
IEC Address Part 1 (IEC: LD;LN) | Addresse IEC Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN) | IEC Dirección Part 1 (IEC: LD;LN) | IEC Endereço Part 1 (IEC: LD;LN) | IEC Адрес Part 1 (IEC: LD;LN) | IEC Address Part 1 (IEC: LD;LN)
IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | Addresse IEC Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Dirección Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Endereço Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Адрес Part 2 (IEC: FC;Data Object;DataAttribute;CDC) | IEC Address Part 2 (IEC: FC;Data Object;DataAttribute;CDC)
Comments | Commentaires | Comments | Comentarios | Comentários | Комментарии | Comments
Automations links (separator ";") (add "<" if output) | Liens d'Automatismes (séparateur ";") (ajouter "<" si c'est une sortie) | Automations links (separator ";") (add "<" if output) | conexión Automatión (separador ";") (añadir "<" si la producción) | Automatião conexão (separador ";") (acrescentar "<" se a produção) | связи Автоматизация (разделитель ";") (добавить "<" если выход) | Automations links (separator ";") (add "<" if output)
SHEET : List of Automations | SHEET : Liste des Automatismes | SHEET : List of Automations | SHEET : Lista de Automations | SHEET : Lista de Automations | SHEET : Список Automations | SHEET : List of Automations
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
AUTOMATIONS INFORMATION | INFORMATIONS SUR LES AUTOMATISMES | AUTOMATIONS INFORMATION | INFORMACION DE AUTOMATIONS | Informação de AUTOMATIONS | ИНФОРМАЦИЯ ПО AUTOMATIONS | AUTOMATIONS INFORMATION
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
Number | Numéro | Number | Número | Número | Номер | Number
Automation Name | Nom de l'Automatisme | Automation Name | Nombre de Automation | Nome do Automation | Имя Automation | Automation Name
Automation Type | Type d'Automatisme | Automation Type | Tipo de Automation | Tipo de Automation | Тип Automation | Automation Type
Computer | Calculateur | Computer | Computador | Computador | Компьютер | Computer
Redundant Computer | Calculateur Redondant | Redundant Computer | Computador Redundante | Computador Redundante | Резервный компьютер | Redundant Computer
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
Template | Modèle | Template | Plantilla | Panilha | Образец | Template
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : Equipments IEC Links | SHEET : Liste des Liens IEC | SHEET : Equipments IEC Links | SHEET : Enlaces Equipos IEC | SHEET : Ligações de Equipamentos IEC | SHEET : аппаратура ссылки IEC | SHEET : Equipments IEC Links
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
IEC LINKS INFORMATION | INFORMATIONS SUR LES LIENS IEC | IEC LINKS INFORMATION | IEC LINKS INFORMATION | IEC LINKS INFORMATION | ИНФОРМАЦИЯ ПО IEC LINKS | IEC LINKS INFORMATION
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
Clients \ Servers | Clients \ Servers | Clients \ Servers | Clients \ Servers | Clients \ Servers | Clients \ Servers | Clients \ Servers
Issue | Révision | Issue | Revisión | Revisão | Версия | Version
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
Substation 1 | Sous-station 1 | Substation 1 | Subestación 1 | Substação 1 | подстанции 1 | Stations 1
Substation 2 | Sous-station 2 | Substation 2 | Subestación 2 | Substação 2 | подстанции 2 | Stations 2
Substation 3 | Sous-station 3 | Substation 3 | Subestación 3 | Substação 3 | подстанции 3 | Stations 3
Substation 4 | Sous-station 4 | Substation 4 | Subestación 4 | Substação 4 | подстанции 4 | Stations 4
Substation 5 | Sous-station 5 | Substation 5 | Subestación 5 | Substação 5 | подстанции 5 | Stations 5
Substation 6 | Sous-station 6 | Substation 6 | Subestación 6 | Substação 6 | подстанции 6 | Stations 6
Substation 7 | Sous-station 7 | Substation 7 | Subestación 7 | Substação 7 | подстанции 7 | Stations 7
Substation 8 | Sous-station 8 | Substation 8 | Subestación 8 | Substação 8 | подстанции 8 | Stations 8
Substation 9 | Sous-station 9 | Substation 9 | Subestación 9 | Substação 9 | подстанции 9 | Stations 9
Substation 10 | Sous-station 10 | Substation 10 | Subestación 10 | Substação 10 | подстанции 10 | Stations 10
Substation 11 | Sous-station 11 | Substation 11 | Subestación 11 | Substação 11 | подстанции 11 | Stations 11
Substation 12 | Sous-station 12 | Substation 12 | Subestación 12 | Substação 12 | подстанции 12 | Stations 12
Substation 13 | Sous-station 13 | Substation 13 | Subestación 13 | Substação 13 | подстанции 13 | Stations 13
Substation 14 | Sous-station 14 | Substation 14 | Subestación 14 | Substação 14 | подстанции 14 | Stations 14
Substation 15 | Sous-station 15 | Substation 15 | Subestación 15 | Substação 15 | подстанции 15 | Stations 15
Substation 16 | Sous-station 16 | Substation 16 | Subestación 16 | Substação 16 | подстанции 16 | Stations 16
Substation 17 | Sous-station 17 | Substation 17 | Subestación 17 | Substação 17 | подстанции 17 | Stations 17
Substation 18 | Sous-station 18 | Substation 18 | Subestación 18 | Substação 18 | подстанции 18 | Stations 18
Substation 19 | Sous-station 19 | Substation 19 | Subestación 19 | Substação 19 | подстанции 19 | Stations 19
Substation 20 | Sous-station 20 | Substation 20 | Subestación 20 | Substação 20 | подстанции 20 | Stations 20
Substation 21 | Sous-station 21 | Substation 21 | Subestación 21 | Substação 21 | подстанции 21 | Stations 21
Substation 22 | Sous-station 22 | Substation 22 | Subestación 22 | Substação 22 | подстанции 22 | Stations 22
Substation 23 | Sous-station 23 | Substation 23 | Subestación 23 | Substação 23 | подстанции 23 | Stations 23
Substation 24 | Sous-station 24 | Substation 24 | Subestación 24 | Substação 24 | подстанции 24 | Stations 24
Substation 25 | Sous-station 25 | Substation 25 | Subestación 25 | Substação 25 | подстанции 25 | Stations 25
Substation 26 | Sous-station 26 | Substation 26 | Subestación 26 | Substação 26 | подстанции 26 | Stations 26
Substation 27 | Sous-station 27 | Substation 27 | Subestación 27 | Substação 27 | подстанции 27 | Stations 27
Substation 28 | Sous-station 28 | Substation 28 | Subestación 28 | Substação 28 | подстанции 28 | Stations 28
Substation 29 | Sous-station 29 | Substation 29 | Subestación 29 | Substação 29 | подстанции 29 | Stations 29
Substation 30 | Sous-station 30 | Substation 30 | Subestación 30 | Substação 30 | подстанции 30 | Stations 30
Substation 31 | Sous-station 31 | Substation 31 | Subestación 31 | Substação 31 | подстанции 31 | Stations 31
Substation 32 | Sous-station 32 | Substation 32 | Subestación 32 | Substação 32 | подстанции 32 | Stations 32
Substation 33 | Sous-station 33 | Substation 33 | Subestación 33 | Substação 33 | подстанции 33 | Stations 33
Substation 34 | Sous-station 34 | Substation 34 | Subestación 34 | Substação 34 | подстанции 34 | Stations 34
Substation 35 | Sous-station 35 | Substation 35 | Subestación 35 | Substação 35 | подстанции 35 | Stations 35
Substation 36 | Sous-station 36 | Substation 36 | Subestación 36 | Substação 36 | подстанции 36 | Stations 36
Substation 37 | Sous-station 37 | Substation 37 | Subestación 37 | Substação 37 | подстанции 37 | Stations 37
Substation 38 | Sous-station 38 | Substation 38 | Subestación 38 | Substação 38 | подстанции 38 | Stations 38
Substation 39 | Sous-station 39 | Substation 39 | Subestación 39 | Substação 39 | подстанции 39 | Stations 39
Substation 40 | Sous-station 40 | Substation 40 | Subestación 40 | Substação 40 | подстанции 40 | Stations 40
SHEET : SAS Model | SHEET : Modèles SAS | SHEET : SAS Model | SHEET : Modelo SAS | SHEET : Modo SAS | SHEET : Модель SAS | SHEET : SAS Model
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
BEGIN SCADA SAS | DEBUT SCADA SAS | BEGIN SCADA SAS | COMIENZA SCADA SAS | INÍCIO SCADA SAS | НАЧАЛО ОПИСАНИЯ SCADA SAS | BEGIN SCADA SAS
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
SCADA Protocol Name | Nom de protocole SCADA | SCADA Protocol Name | Nombre de Protocolo SCADA | Nome do Protocolo SCADA | SCADA ИМЯ Протокола | SCADA Protocol Name
Scada short name (16 char) | Nom court du SCADA (16 char) | Scada short name (16 char) | Nombre corto Scada (16 caract) | Nome Curto Scada (16 caract) | Сокращенное имя SCADA (16 символов) | Scada short name (16 char)
Protocol General Parameters | Paramètres généraux du Protocole | Protocol General Parameters | Parámetros generales del protocolo | Parâmetros Geração do Protocolo | Основные параметры протокола | Protocol General Parameters
Main communication channel | Voie de communication principale | Main communication channel | Canal de comunicación principal | Canal de Comunicação Principal | Основной канал связи | Main communication channel
Auxiliary Communication channel | Voie de communication auxiliaire | Auxiliary Communication channel | Canal de comunciación auxiliar | Canal de Comunicação auxiliar | Запасной канал связи | Auxiliary Communication channel
Baud rate (bit/s) | Vitesse de transmission (bit/s) | Baud rate (bit/s) | Baudios (bit/s) | Baud Rate (bit/s) | Скорость в бодах (бит/с) | Baud rate (bit/s)
Common address of ASDU | Adresse commune de l'ASDU | Common address of ASDU | Dirección común ASDU | Endereço comum ASDU | Общий адрес ASDU | Common address of ASDU
Common address of ASDU Length | Longueur de l'adresse commune de l'ASDU | Common address of ASDU Length | Longitud de la dirección común ASDU | Tamanho do Endereço comum ASDU | Длина общего адреса ASDU | Common address of ASDU Length
Object structure | Structure d'objet | Object structure | Estructura del objeto | Estrutura do objeto | Структура объекта | Object structure
Frame max length | Longueur maximale de la vue | Frame max length | Longitud máx de la trama | Tamanho máx do frame | Максимальная длина кадра | Frame max length
Measurement periodic cycle | Cycle Périodique de Mesure | Measurement periodic cycle | Ciclo de medición periódico | Ciclo periódico de Medição | Периодический цикл измерений | Measurement periodic cycle
Binary Time Size | Taille de Temps binaire | Binary Time Size | Tamaño de tiempo binario | Tamanho Binário do Tempo | Размер двоичной кодировки времени | Binary Time Size
SPS Data Type | SPS Donnée de Type | SPS Data Type | SPS Datos tipo | SPS Dados tipo | SPS Тип данных | SPS Data Type
Inverted state | Etat Inversé | Inverted state | Estado invertido | Estado invertido | Инвертированное состояние | Inverted state
Send in General Interrogation | Envoyé lors de l'Interrogation Générale | Send in General Interrogation | Enviar en general Interrogatorio | Envie em Geral Interrogation | Отправить в Генеральной Допрос | Senden in den Allgemeinen Interrogation
DPS Data Type | DPS Donnée de Type | DPS Data Type | DPS Datos tipo | DPS Dados tipo | DPS Тип данных | DPS Data Type
Inverted state | Etat Inversé | Inverted state | Estado invertido | Estado invertido | Инвертированное состояние | Inverted state
Send in General Interrogation | Envoyé lors de l'Interrogation Générale | Send in General Interrogation | Enviar en general Interrogatorio | Envie em Geral Interrogation | Отправить в Генеральной Допрос | Senden in den Allgemeinen Interrogation
MPS Data Type | MPS Donnée de Type | MPS Data Type | MPS Datos tipo | MPS Dados tipo | MPS Тип данных | MPS Data Type
Send in General Interrogation | Envoyé lors de l'Interrogation Générale | Send in General Interrogation | Enviar en general Interrogatorio | Envie em Geral Interrogation | Отправить в Генеральной Допрос | Senden in den Allgemeinen Interrogation
MV Data Type | MV Donnée de Type | MV Data Type | MV Datos tipo | MV Dados tipo | MV Тип данных | MV Data Type
Format | Format | Format | Formato | Formato | Формат | Format
Cycle Type | Type de Cycle | Cycle Type | Tipo de ciclo | Tipo de Ciclo | Тип цикла | Cycle Type
Minimum value | Valeur Min | Minimum value | Valor al mínimo | Valor ao Mínimo | Значение минимуму | Minimum value
Maximum value | Valeur Max | Maximum value | Valor al Máximo | Valor ao Máximo | Значение максимуму | Maximum value
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : CDC Type II Model | SHEET : Modèles CDC Type II | SHEET : CDC Type II Model | SHEET : Modelo CDC Type II | SHEET : Modo CDC Type II | SHEET : Модель CDC Type II | SHEET : CDC Type II Model
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
BEGIN SCADA CDC TYPE II | DEBUT SCADA CDC TYPE II | BEGIN SCADA CDC TYPE II | COMIENZA SCADA CDC TYPE II | INÍCIO SCADA CDC TYPE II | НАЧАЛО ОПИСАНИЯ SCADA CDC TYPE II | BEGIN SCADA CDC TYPE II
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
SCADA Protocol Name | Nom de protocole SCADA | SCADA Protocol Name | Nombre de Protocolo SCADA | Nome do Protocolo SCADA | SCADA ИМЯ Протокола | SCADA Protocol Name
Scada short name (16 char) | Nom court du SCADA (16 char) | Scada short name (16 char) | Nombre corto Scada (16 caract) | Nome Curto Scada (16 caract) | Сокращенное имя SCADA (16 символов) | Scada short name (16 char)
Protocol General Parameters | Paramètres généraux du Protocole | Protocol General Parameters | Parámetros generales del protocolo | Parâmetros Geração do Protocolo | Основные параметры протокола | Protocol General Parameters
Main communication channel | Voie de communication principale | Main communication channel | Canal de comunicación principal | Canal de Comunicação Principal | Основной канал связи | Main communication channel
Auxiliary Communication channel | Voie de communication auxiliaire | Auxiliary Communication channel | Canal de comunciación auxiliar | Canal de Comunicação auxiliar | Запасной канал связи | Auxiliary Communication channel
Baud rate (bit/s) | Vitesse de transmission (bit/s) | Baud rate (bit/s) | Baudios (bit/s) | Baud Rate (bit/s) | Скорость в бодах (бит/с) | Baud rate (bit/s)
Connection timeout (T0) | Expiration de la Connexion (T0) | Connection timeout (T0) | Connection tiempo fuera (T0) | Falha de Conexão (T0) | Задержка соединения (T0) | Connection timeout (T0)
Minimal int Value for Measurement | Valeur minimale de mesure | Minimal int Value for Measurement | Mínimo valor de medición | Minimal valor inteiro para Medição | Минимальное значение за целое измерение | Minimal-Integer-Wert für die Messung
Maximal int Value for Measurement | Valeur maximale de mesure | Maximal int Value for Measurement | Máximo valor de medición | Maximal valor inteiro para Medição | Максимальное целое значение для измерения | Maximale Integer-Wert für die Messung
Int Value for Invalid Measurement | Valeur de mesure invalide | Int Value for Invalid Measurement | Valor no válido para la medición | Valor inválido para a medição | Стоимость за недействительные измерения | Integer-Wert für ungültig Messung
SPS Data Type | SPS Donnée de Type | SPS Data Type | SPS Datos tipo | SPS Dados tipo | SPS Тип данных | SPS Data Type
Sending mode | Mode de transmission | Sending mode | Modo de transmisión | Modo de Envio | Коробка передач в режиме | Übertragungsmodus
Inverted state | Etat Inversé | Inverted state | Estado invertido | Estado invertido | Инвертированное состояние | Inverted state
DPS Data Type | DPS Donnée de Type | DPS Data Type | DPS Datos tipo | DPS Dados tipo | DPS Тип данных | DPS Data Type
Sending mode | Mode de transmission | Sending mode | Modo de transmisión | Modo de Envio | Коробка передач в режиме | Übertragungsmodus
Inverted state | Etat Inversé | Inverted state | Estado invertido | Estado invertido | Инвертированное состояние | Inverted state
SPC Data Type | SPC Donnée de Type | SPC Data Type | SPC Datos tipo | SPC Dados tipo | SPC Тип данных | SPC Data Type
SCADA order type | Type de commande SCADA | SCADA order type | Tipo de orden SCADA | Tipo de Ordem SCADA | Тип команды SCADA | SCADA order type
DPC Data Type | DPC Donnée de Type | DPC Data Type | DPC Datos tipo | DPC Dados tipo | DPC Тип данных | DPC Data Type
SCADA order type | Type de commande SCADA | SCADA order type | Tipo de orden SCADA | Tipo de Ordem SCADA | Тип команды SCADA | SCADA order type
MV Data Type | MV Donnée de Type | MV Data Type | MV Datos tipo | MV Dados tipo | MV Тип данных | MV Data Type
Minimum value | Valeur Min | Minimum value | Valor al mínimo | Valor ao Mínimo | Значение минимуму | Minimum value
Maximum value | Valeur Max | Maximum value | Valor al Máximo | Valor ao Máximo | Значение максимуму | Maximum value
Setpoint Data Type | SetPoint Donnée de Type | Setpoint Data Type | SetPoint Datos tipo | SetPoint Dados tipo | SetPoint Тип данных | Setpoint Data Type
Minimum value | Valeur Min | Minimum value | Valor al mínimo | Valor ao Mínimo | Значение минимуму | Minimum value
Maximum value | Valeur Max | Maximum value | Valor al Máximo | Valor ao Máximo | Значение максимуму | Maximum value
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : GI74 Model | SHEET : Modèles GI74 | SHEET : GI74 Model | SHEET : Modelo GI74 | SHEET : Modo GI74 | SHEET : Модель GI74 | SHEET : GI74 Model
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
BEGIN SCADA GI74 | DEBUT SCADA GI74 | BEGIN SCADA GI74 | COMIENZA SCADA GI74 | INÍCIO SCADA GI74 | НАЧАЛО ОПИСАНИЯ SCADA GI74 | BEGIN SCADA GI74
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
SCADA Protocol Name | Nom de protocole SCADA | SCADA Protocol Name | Nombre de Protocolo SCADA | Nome do Protocolo SCADA | SCADA ИМЯ Протокола | SCADA Protocol Name
Scada short name (16 char) | Nom court du SCADA (16 char) | Scada short name (16 char) | Nombre corto Scada (16 caract) | Nome Curto Scada (16 caract) | Сокращенное имя SCADA (16 символов) | Scada short name (16 char)
Protocol General Parameters | Paramètres généraux du Protocole | Protocol General Parameters | Parámetros generales del protocolo | Parâmetros Geração do Protocolo | Основные параметры протокола | Protocol General Parameters
TCP/IP Address | Adresse TCP/IP | TCP/IP Address | TCP/IP Dirección | TCP/IP Endereço | TCP/IP Адрес | TCP/IP Address
Network Name | NOM DU RESEAU | Network Name | Nombre de red | Nome da rede | Сетевое Имя | Netzwerk Name
Port 1 : TE address | Port 1 : Adresse TE | Port 1 : TE address | Puerto 1: TE dirección | Porto 1: TE endereço | Порт 1: TE-адрес | Port 1: TE-Adresse
Port 1 : TE block size | Port 1 : Taille de bloc TE | Port 1 : TE block size | Puerto 1: TE tamaño de bloque | Porto 1: TE bloco tamanho | Порт 1: TE размер блока | Port 1: TE Blockgröße
Port 1 : Control Timeout in ms | Port 1 : Expiration du contrôle en ms | Port 1 : Control Timeout in ms | Puerto 1: Control de Tiempo en ms | Porto 1: Controlo Timeout em ms | Порт 1: Контроль тайм-аута в мс | Port 1: Control Timeout in ms
Port 1 : HK control function | Port 1 : Fonction de contrôle HK | Port 1 : HK control function | Puerto 1: función de control de HK | Porto 1: HK função de controlo | Порт 1: HK функции контроля | Port 1 : HK control function
Port 1 : HK control block | Port 1 : Bloc de contrôle HK | Port 1 : HK control block | Puerto 1: bloque de control de HK | Porto 1: HK bloco de controlo | Порт 1: HK блок управления | Port 1 : HK control block
Port 1 : HK control word | Port 1 : Mot de contrôle HK | Port 1 : HK control word | Puerto 1: HK palabra de control | Porto 1: HK controlo palavra | Порт 1: HK управляющее слово | Port 1 : HK control word
Port 2 : TE address | Port 2 : Adresse TE | Port 2 : TE address | Puerto 2: TE dirección | Porto 2: TE endereço | Порт 2: TE-адрес | Port 2: TE-Adresse
Port 2 : TE block size | Port 2 : Taille de bloc TE | Port 2 : TE block size | Puerto 2: TE tamaño de bloque | Porto 2: TE bloco tamanho | Порт 2: TE размер блока | Port 2: TE Blockgröße
Port 2 : Control Timeout in ms | Port 2 : Expiration du contrôle en ms | Port 2 : Control Timeout in ms | Puerto 2: Control de Tiempo en ms | Porto 2: Controlo Timeout em ms | Порт 2: Контроль тайм-аута в мс | Port 2: Control Timeout in ms
Port 2 : HK control function | Port 2 : Fonction de contrôle HK | Port 2 : HK control function | Puerto 2: función de control de HK | Porto 2: HK função de controlo | Порт 2: HK функции контроля | Port 2 : HK control function
Port 2 : HK control block | Port 2 : Bloc de contrôle HK | Port 2 : HK control block | Puerto 2: bloque de control de HK | Porto 2: HK bloco de controlo | Порт 2: HK блок управления | Port 2 : HK control block
Port 2 : HK control word | Port 2 : Mot de contrôle HK | Port 2 : HK control word | Puerto 2: HK palabra de control | Porto 2: HK controlo palavra | Порт 2: HK управляющее слово | Port 2 : HK control word
SPS Data Type | SPS Donnée de Type | SPS Data Type | SPS Datos tipo | SPS Dados tipo | SPS Тип данных | SPS Data Type
Inverted state | Etat Inversé | Inverted state | Estado invertido | Estado invertido | Инвертированное состояние | Inverted state
Type propagation change | Type de changement de propagation | Type propagation change | Tipo de cambio propagación | Tipo de propagação mudança | Вид распространения изменений | Type propagation change
DPS Data Type | DPS Donnée de Type | DPS Data Type | DPS Datos tipo | DPS Dados tipo | DPS Тип данных | DPS Data Type
Inverted state | Etat Inversé | Inverted state | Estado invertido | Estado invertido | Инвертированное состояние | Inverted state
Type propagation change | Type de changement de propagation | Type propagation change | Tipo de cambio propagación | Tipo de propagação mudança | Вид распространения изменений | Type propagation change
SPC Data Type | SPC Donnée de Type | SPC Data Type | SPC Datos tipo | SPC Dados tipo | SPC Тип данных | SPC Data Type
Port for feedback | Port de retour | Port for feedback | Puerto de retroalimentación | Porto de retorno | Порт для обратной связи | Port for feedback
DPC Data Type | DPC Donnée de Type | DPC Data Type | DPC Datos tipo | DPC Dados tipo | DPC Тип данных | DPC Data Type
Port for feedback | Port de retour | Port for feedback | Puerto de retroalimentación | Porto de retorno | Порт для обратной связи | Port for feedback
MV Data Type | MV Donnée de Type | MV Data Type | MV Datos tipo | MV Dados tipo | MV Тип данных | MV Data Type
Type measurement | Type de la mesure | Type measurement | Tipo de medición | Tipo de medição | Тип измерений | Type measurement
Type propagation change | Type de changement de propagation | Type propagation change | Tipo de cambio propagación | Tipo de propagação mudança | Вид распространения изменений | Type propagation change
Unit type | Type de l'unité | Unit type | Tipo de unidad | Unidade tipo | Группы типа | Unit type
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : HNZ Model | SHEET : Modèles HNZ | SHEET : HNZ Model | SHEET : Modelo HNZ | SHEET : Modo HNZ | SHEET : Модель HNZ | SHEET : HNZ Model
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
BEGIN SCADA HNZ | DEBUT SCADA HNZ | BEGIN SCADA HNZ | COMIENZA SCADA HNZ | INÍCIO SCADA HNZ | НАЧАЛО ОПИСАНИЯ SCADA HNZ | BEGIN SCADA HNZ
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
SCADA Protocol Name | Nom de protocole SCADA | SCADA Protocol Name | Nombre de Protocolo SCADA | Nome do Protocolo SCADA | SCADA ИМЯ Протокола | SCADA Protocol Name
Scada short name (16 char) | Nom court du SCADA (16 char) | Scada short name (16 char) | Nombre corto Scada (16 caract) | Nome Curto Scada (16 caract) | Сокращенное имя SCADA (16 символов) | Scada short name (16 char)
Protocol General Parameters | Paramètres généraux du Protocole | Protocol General Parameters | Parámetros generales del protocolo | Parâmetros Geração do Protocolo | Основные параметры протокола | Protocol General Parameters
Main communication channel | Voie de communication principale | Main communication channel | Canal de comunicación principal | Canal de Comunicação Principal | Основной канал связи | Main communication channel
Auxiliary Communication channel | Voie de communication auxiliaire | Auxiliary Communication channel | Canal de comunciación auxiliar | Canal de Comunicação auxiliar | Запасной канал связи | Auxiliary Communication channel
Baud rate (bit/s) | Vitesse de transmission (bit/s) | Baud rate (bit/s) | Baudios (bit/s) | Baud Rate (bit/s) | Скорость в бодах (бит/с) | Baud rate (bit/s)
Protocol | Protocole | Protocol | Protocolo | Protocolo | Протокола | Protocol
Time Reference | Temps de référence | Time Reference | Tiempo de referencia | Tempo de referência | Время ссылку | Zeitplan
Station address | Adresse de la Station | Station address | Estación de dirección | Estação endereço | Станция адрес | Station address
Network station number | Numéro de Station réseau | Network station number | Número de la estación de red | Rede estação número | Сетевой номер станции | Network station number
RTU Db version | RTU version base de donnée | RTU Db version | Base de datos versión RTU | RTU versão base | РТУ версию базы данных | RTU Db version
Enable concatenation | Concatenation possible | Enable concatenation | Permitir la concatenación | Ativar concatenation | Включить конкатенация | Enable concatenation
Checksum size (fcs) | Taille du Checksum (fcs) | Checksum size (fcs) | Checksum tamaño (fcs) | Checksum tamanho (fcs) | Checksum размера (fcs) | Checksum size (fcs)
Max number of retries | Nombre max de tentatives | Max number of retries | Max number of retries | Max number of retries | Max number of retries | Max number of retries
Inter frame duration | Durée inter trame | Inter frame duration | Duración entre 2 fotogramas | Duração entre 2 frames | Продолжительность от 2 кадров | Inter frame duration
Anticipate rate | Taux d'Anticipation | Anticipate rate | Anticipar tasa | Antecipe taxa | Предвидеть курс | Anticipate rate
Frame max length | Longueur maximale de la vue | Frame max length | Longitud máx de la trama | Tamanho máx do frame | Максимальная длина кадра | Frame max length
Measurement Cycle 1 (s) | Cycle de Mesure 1 (s) | Measurement Cycle 1 (s) | Ciclo de medición 1 (s) | Medição ciclo 1 (s) | Измерение цикла 1 (s) | Measurement Cycle 1 (s)
Measurement Cycle 2 (s) | Cycle de Mesure 2 (s) | Measurement Cycle 2 (s) | Ciclo de medición 2 (s) | Medição ciclo 2 (s) | Измерение цикла 2 (s) | Measurement Cycle 2 (s)
Measurement Cycle 3 (s) | Cycle de Mesure 3 (s) | Measurement Cycle 3 (s) | Ciclo de medición 3 (s) | Medição ciclo 3 (s) | Измерение цикла 3 (s) | Measurement Cycle 3 (s)
Measurement Cycle 4 (s) | Cycle de Mesure 4 (s) | Measurement Cycle 4 (s) | Ciclo de medición 4 (s) | Medição ciclo 4 (s) | Измерение цикла 4 (s) | Measurement Cycle 4 (s)
Fifo : loss information or RTU init address (byte.bit) | Fifo : adresse de perte de donnée ou RTU Init (octet.bit) | Fifo : loss information or RTU init address (byte.bit) | Fifo : pérdida de información de dirección o RTU Init (byte.bit) | Fifo : perda informações endereço o RTU Init (byte.bit) | Fifo : утрата информации - РТУ иниц адрес (byte.bit) | Fifo : loss information or RTU init address (byte.bit)
Fifo : depth of chronologic sorting (ms) | Fifo : profondeur de tri chronologique (ms) | Fifo : depth of chronologic sorting (ms) | Fifo : profundidad de la clasificación cronológica (ms) | Fifo : profundidade de triagem cronológico (ms) | Fifo : Глубина chronologic сортировка (ms) | Fifo : depth of chronologic sorting (ms)
Fifo : empty condition | Fifo : condition vide | Fifo : empty condition | Fifo : condición de vacío | Fifo : vazias condição | Fifo : пусто условие | Fifo : empty condition
Fifo : No activity, retry or supervision delay (ms) | Fifo : délai de non activité, nouvelle tentative ou supervision (ms) | Fifo : No activity, retry or supervision delay (ms) | Fifo : Ninguna actividad, o la supervisión de reintento de retraso (ms) | Fifo : Sem atividade, tentar novamente ou supervisão atraso (ms) | Fifo : Нет деятельности, повторить или надзор задержка (мс) | Fifo : No activity, retry or supervision delay (ms)
RTE : Period to analyze quality of line (s) | RTE : Periode d'analyse de qualité de ligne (s) | RTE : Period to analyze quality of line (s) | RTE : Período para analizar la calidad de la línea (s) | RTE : Período para análise da qualidade de linha (s) | РTE : Период для анализа качества линии (s) | RTE : Period to analyze quality of line (s)
RTE : Bulle message allowed | RTE : Message Bulle autorisé | RTE : Bulle message allowed | RTE : Bulle permitido mensaje | RTE : Bulle mensagem permitido | РTE : Бюль сообщений разрешен | RTE : Bulle message allowed
RTE : Period for sending Bulle message (s) | RTE : Periode d'envoi d'un message Bulle (s) | RTE : Period for sending Bulle message (s) | RTE : Período para el envío de Bulle mensaje (s) | RTE : Prazo para envio Bulle mensagem (s) | РTE : Срок отправки сообщения Бюль (s) | RTE : Period for sending Bulle message (s)
RTE : TOR Battante address (byte.bit) | RTE : Adresse de TOR Battante (octet.bit) | RTE : TOR Battante address (byte.bit) | RTE : TOR Battante dirección (byte.bit) | RTE : TOR Battante endereço (byte.bit) | РTE : TOР Battante адрес (byte.bit) | RTE : TOR Battante address (byte.bit)
MV Data Type | MV Donnée de Type | MV Data Type | MV Datos tipo | MV Dados tipo | MV Тип данных | MV Data Type
Used cycle | Cycle utilisé | Used cycle | Usado ciclo | Usado ciclo | Используется цикла | Used cycle
Format | Format | Format | Formato | Formato | Формат | Format
Message Structure | Structure de message | Message Structure | Estructura del mensaje | Estrutura das mensagens | Сообщение Структура | Message Structure
Original Value converted | Conversion de la valeur originale | Original Value converted | Valor original convertido | Valor original convertido | Первоначальная стоимость преобразованы | Original Value converted
Sent on variation | Envoyé sur variation | Sent on variation | Enviado en la variación | Enviada em variação | Переданные по вариации | Sent on variation
Variation Mode | Mode de variation | Variation Mode | Modo de variación | Modo de variação | вариации режиме | Variation Mode
Deadband | Bande morte | Deadband | Venda muerta | Faixa muerta | Порог чувствительности | Deadband
Setpoint Data Type | SetPoint Donnée de Type | Setpoint Data Type | SetPoint Datos tipo | SetPoint Dados tipo | SetPoint Тип данных | Setpoint Data Type
SCADA order type | Type de commande SCADA | SCADA order type | Tipo de orden SCADA | Tipo de Ordem SCADA | Тип команды SCADA | SCADA order type
Format | Format | Format | Formato | Formato | Формат | Format
Minimum value | Valeur Min | Minimum value | Valor al mínimo | Valor ao Mínimo | Значение минимуму | Minimum value
Maximum value | Valeur Max | Maximum value | Valor al Máximo | Valor ao Máximo | Значение максимуму | Maximum value
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
Default Unit | Unité par défaut | Default Unit | Unidad por defecto | Unidade padrão | Группа по умолчанию | Default Unit
Default Unit for datapoint | Unité par défaut pour le point de donnée | Default Unit for datapoint | Unidad por defecto de Datapoint | Unidade padrão para Datapoint | Группа по умолчанию Datapoint | Default Unit for datapoint
Default Unit | Unité par défaut | Default Unit | Unidad por defecto | Unidade padrão | Группа по умолчанию | Default Unit
Default Unit for datapoint | Unité par défaut pour le point de donnée | Default Unit for datapoint | Unidad por defecto de Datapoint | Unidade padrão para Datapoint | Группа по умолчанию Datapoint | Default Unit for datapoint
Default Unit | Unité par défaut | Default Unit | Unidad por defecto | Unidade padrão | Группа по умолчанию | Default Unit
Default Unit for datapoint | Unité par défaut pour le point de donnée | Default Unit for datapoint | Unidad por defecto de Datapoint | Unidade padrão para Datapoint | Группа по умолчанию Datapoint | Default Unit for datapoint
SHEET : T101 MASTER Model | SHEET : Modèles T101 MAITRE | SHEET : T101 Model MASTER | SHEET : Modelo T101 MASTER | SHEET : Modo T101 MASTER | SHEET : Модель T101 MASTER | SHEET : T101 MASTER Model
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
BEGIN T101 MASTER | DEBUT T101 MAITRE | BEGIN T101 MASTER | COMIENZA T101 MASTER | INÍCIO T101 MASTER | НАЧАЛО ОПИСАНИЯ T101 MASTER | BEGIN T101 MASTER
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
Protocol Name | Nom du protocole | Protocol Name | Nombre de Protocolo SCADA | Nome do Protocolo SCADA | SCADA ИМЯ Протокола | SCADA Protocol Name
Short name (16 char) | Nom court(16 char) | Short name (16 char) | Nombre corto(16 caract) | Nome Curto(16 caract) | Сокращенное имя(16 символов) | short name (16 char)
Protocol General Parameters | Paramètres généraux du Protocole | Protocol General Parameters | Parámetros generales del protocolo | Parâmetros Geração do Protocolo | Основные параметры протокола | Protocol General Parameters
Time Reference | Temps de référence | Time Reference | Tiempo de referencia | Tempo de referência | Время ссылку | Zeitplan
number of retries | number of retries | number of retries | number of retries | number of retries | number of retries | number of retries
station address size (bytes) | station address size (bytes) | station address size (bytes) | station address size (bytes) | station address size (bytes) | station address size (bytes) | station address size (bytes)
ASDU address size (bytes) | ASDU address size (bytes) | ASDU address size (bytes) | ASDU address size (bytes) | ASDU address size (bytes) | ASDU address size (bytes) | ASDU address size (bytes)
info address size (bytes) | info address size (bytes) | info address size (bytes) | info address size (bytes) | info address size (bytes) | info address size (bytes) | info address size (bytes)
transmission cause size (bytes) | taill cause de transmission (bytes) | transmission cause size (bytes) | transmission cause size (bytes) | transmission cause size (bytes) | transmission cause size (bytes) | transmission cause size (bytes)
acknowledgement time-out (x 100 ms) | acknowledgement time-out (x 100 ms) | acknowledgement time-out (x 100 ms) | acknowledgement time-out (x 100 ms) | acknowledgement time-out (x 100 ms) | acknowledgement time-out (x 100 ms) | acknowledgement time-out (x 100 ms)
synchronization cycle (x 10 s) | synchronization cycle (x 10 s) | synchronization cycle (x 10 s) | synchronization cycle (x 10 s) | synchronization cycle (x 10 s) | synchronization cycle (x 10 s) | synchronization cycle (x 10 s)
downgraded cycle (x 100 ms) | downgraded cycle (x 100 ms) | downgraded cycle (x 100 ms) | downgraded cycle (x 100 ms) | downgraded cycle (x 100 ms) | downgraded cycle (x 100 ms) | downgraded cycle (x 100 ms)
Type of link | Type de lien | Type of link | Tipo de enlace | Tipo de ligação | Вид ссылки | Art der Verknüpfung
test frame time-out (s) | test frame time-out (s) | test frame time-out (s) | test frame time-out (s) | test frame time-out (s) | test frame time-out (s) | test frame time-out (s)
Inter frame duration | Durée inter trame | Inter frame duration | Duración entre 2 fotogramas | Duração entre 2 frames | Продолжительность от 2 кадров | Inter frame duration
Baud rate (bit/s) | Vitesse de transmission (bit/s) | Baud rate (bit/s) | Baudios (bit/s) | Baud Rate (bit/s) | Скорость в бодах (бит/с) | Baud rate (bit/s)
Legacy IED parameters | Legacy IED parameters | Legacy IED parameters | Legacy IED parameters | Legacy IED parameters | Legacy IED parameters | Legacy IED parameters
automatic disturbance | automatic disturbance | automatic disturbance | automatic disturbance | automatic disturbance | automatic disturbance | automatic disturbance
localisation for disturbance file | localisation for disturbance file | localisation for disturbance file | localisation for disturbance file | localisation for disturbance file | localisation for disturbance file | localisation for disturbance file
SPS Data Type | SPS Donnée de Type | SPS Data Type | SPS Datos tipo | SPS Dados tipo | SPS Тип данных | SPS Data Type
DPS Data Type | DPS Donnée de Type | DPS Data Type | DPS Datos tipo | DPS Dados tipo | DPS Тип данных | DPS Data Type
contact identifier | contact identifier | contact identifier | contact identifier | contact identifier | contact identifier | contact identifier
MPS Data Type | MPS Donnée de Type | MPS Data Type | MPS Datos tipo | MPS Dados tipo | MPS Тип данных | MPS Data Type
SPC Data Type | SPC Donnée de Type | SPC Data Type | SPC Datos tipo | SPC Dados tipo | SPC Тип данных | SPC Data Type
order type | Type de commande | order type | Tipo de orden | Tipo de Ordem | Тип команды | order type
acknowledgement delay | délai d'acquittement | acknowledgement delay | acknowledgement delay | acknowledgement delay | acknowledgement delay | acknowledgement delay
DPC Data Type | DPC Donnée de Type | DPC Data Type | DPC Datos tipo | DPC Dados tipo | DPC Тип данных | DPC Data Type
order type | Type de commande | order type | Tipo de orden | Tipo de Ordem | Тип команды | order type
contact type | Type de contact | contact type | contact tipo | contact tipo | Τύπος επαφής | contact type
acknowledgement delay | délai d'acquittement | acknowledgement delay | acknowledgement delay | acknowledgement delay | acknowledgement delay | acknowledgement delay
MV Data Type | MV Donnée de Type | MV Data Type | MV Datos tipo | MV Dados tipo | MV Тип данных | MV Data Type
output format | output format | output format | output format | output format | output format | output format
Setpoint Data Type | SetPoint Donnée de Type | Setpoint Data Type | SetPoint Datos tipo | SetPoint Dados tipo | SetPoint Тип данных | Setpoint Data Type
order type | Type de commande | order type | Tipo de orden | Tipo de Ordem | Тип команды | order type
output format | output format | output format | output format | output format | output format | output format
minimal value | minimal value | minimal value | minimal value | minimal value | minimal value | minimal value
maximal value | maximal value | maximal value | maximal value | maximal value | maximal value | maximal value
acknowledgement delay | délai d'acquittement | acknowledgement delay | acknowledgement delay | acknowledgement delay | acknowledgement delay | acknowledgement delay
Counter Data Type | Compteur de Donnée de Type | Counter Data Type | Counter Datos tipo | Contador de Dados tipo | Counter Тип данных | Counter Data Type
output format | output format | output format | output format | output format | output format | output format
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
SHEET : T104 MASTER Model | SHEET : Modèles T104 MAITRE | SHEET : T104 MASTER Model | SHEET : Modelo T101 MASTER | SHEET : Modo T101 MASTER | SHEET : Модель T101 MASTER | SHEET : T101 MASTER Model
Designation : | Désignation : | Designation : | Denominación : | Denominação : | Назначение : | Bezeichnung:
Symbol : | Réf. GE : | Symbol : | Símbolo : | Símbolo : | Обозначение : | Symbol :
Issue : | Révision : | Issue : | Revisión : | Revisão : | Версия : | Version:
Ref : | N° Document : | Ref : | Ref : | Ref : | Ссылка : | Ref :
Date : | Date : | Date : | Fecha : | Data : | Дата : | Datum:
Substation Automation | Sous-Station Automation | Substation Automation | Automatización de Subestaciones | Automação de Subestações | Автоматизация Подстанций | Substation Automation
Data Of : | Données de : | Data Of : | Datos de : | Dados de : | Пpoekt : | Data Of :
BEGIN T104 MASTER | DEBUT T104 MAITRE | BEGIN T104 MASTER | COMIENZA T104 MASTER | INÍCIO T104 MASTER | НАЧАЛО ОПИСАНИЯ T104 MASTER | BEGIN T104 MASTER
Keys : | Légende : | Keys : | Claves : | CHAVES : | Ключи : | Keys :
GE Reserved | Réservé à GE | GE Reserved | Reservado GE | Reservado GE | Зарезервировано GE | GE Reserved
Read Only | Lecture seule | Read Only | Solo lectura | Somemte Leitura | Только Чтение | Read Only
Protocol Name | Nom du protocole | Protocol Name | Nombre de Protocolo SCADA | Nome do Protocolo SCADA | SCADA ИМЯ Протокола | SCADA Protocol Name
Short name (16 char) | Nom court(16 char) | Short name (16 char) | Nombre corto(16 caract) | Nome Curto(16 caract) | Сокращенное имя(16 символов) | short name (16 char)
Protocol General Parameters | Paramètres généraux du Protocole | Protocol General Parameters | Parámetros generales del protocolo | Parâmetros Geração do Protocolo | Основные параметры протокола | Protocol General Parameters
Time Reference | Référence horaire | Time Reference | Tiempo de referencia | Tempo de referência | Время ссылку | Zeitplan
TCP/IP Address | Adresse TCP/IP | TCP/IP Address | TCP/IP Address | TCP/IP Address | TCP/IP Address | TCP/IP Address
Redundant TCP/IP Address | Adresse TCP/IP redondée | Redundant TCP/IP Address | TCT/IP Address redundante | TCP/IP Address redundante | Redundant TCP/IP Address | Redundant TCP/IP Address
t0: connection established timeout (s) | t0: délai d'établissement de connexion (s) | t0: connection established timeout (s) | t0: connection established timeout (s) | t0: connection established timeout (s) | t0: connection established timeout (s) | t0: connection established timeout (s)
t1: APDUs send or test time out (s) | t1: délai d'envoi ou test d'APDU (s) | t1: APDUs send or test time out (s) | t1: APDUs send or test time out (s) | t1: APDUs send or test time out (s) | t1: APDUs send or test time out (s) | t1: APDUs send or test time out (s)
t2: acknowledges in case of no data time out (s) | t2: délai d'acquittement si pas de données (s) | t2: acknowledges in case of no data time out (s) | t2: acknowledges in case of no data time out (s) | t2: acknowledges in case of no data time out (s) | t2: acknowledges in case of no data time out (s) | t2: acknowledges in case of no data time out (s)
t3: test frame sending in case of no data timeout (s) | t3: délai d'envoi de trame de test en cas d'état en veille (s) | t3: test frame sending in case of no data timeout (s) | t3: test frame sending in case of no data timeout (s) | t3: test frame sending in case of no data timeout (s) | t3: test frame sending in case of no data timeout (s) | t3: test frame sending in case of no data timeout (s)
k: window size of transmitted unacknowledged frames | k: taille de la fenêtre des trames non transmises | k: window size of transmitted unacknowledged frames | k: window size of transmitted unacknowledged frames | k: window size of transmitted unacknowledged frames | k: window size of transmitted unacknowledged frames | k: window size of transmitted unacknowledged frames
w: window size of acknowledged received frames | w: taille de la fenêtre des trames reçues | w: window size of acknowledged received frames | w: window size of acknowledged received frames | w: window size of acknowledged received frames | w: window size of acknowledged received frames | w: window size of acknowledged received frames
synchronization cycle (x 10s) | Cycle de synchronisation (x 10s) | synchronization cycle (x 10s) | synchronization cycle (x 10s) | synchronization cycle (x 10s) | synchronization cycle (x 10s) | synchronization cycle (x 10s)
Inter frame duration | Durée inter trame | Inter frame duration | Duración entre 2 fotogramas | Duração entre 2 frames | Продолжительность от 2 кадров | Inter frame duration
SPS Data Type | SPS Donnée de Type | SPS Data Type | SPS Datos tipo | SPS Dados tipo | SPS Тип данных | SPS Data Type
DPS Data Type | DPS Donnée de Type | DPS Data Type | DPS Datos tipo | DPS Dados tipo | DPS Тип данных | DPS Data Type
contact identifier | Identifiant contact | contact identifier | contact identifier | contact identifier | contact identifier | contact identifier
MPS Data Type | MPS Donnée de Type | MPS Data Type | MPS Datos tipo | MPS Dados tipo | MPS Тип данных | MPS Data Type
SPC Data Type | SPC Donnée de Type | SPC Data Type | SPC Datos tipo | SPC Dados tipo | SPC Тип данных | SPC Data Type
order type | Type de commande | order type | Tipo de orden | Tipo de Ordem | Тип команды | order type
acknowledgement delay | Délai acquittement | acknowledgement delay | acknowledgement delay | acknowledgement delay | acknowledgement delay | acknowledgement delay
DPC Data Type | DPC Donnée de Type | DPC Data Type | DPC Datos tipo | DPC Dados tipo | DPC Тип данных | DPC Data Type
order type | Type de commande | order type | Tipo de orden | Tipo de Ordem | Тип команды | order type
contact type | Type de contact | contact type | contact tipo | contact tipo | Τύπος επαφής | contact type
acknowledgement delay | Délai acquittement | acknowledgement delay | acknowledgement delay | acknowledgement delay | acknowledgement delay | acknowledgement delay
MV Data Type | MV Donnée de Type | MV Data Type | MV Datos tipo | MV Dados tipo | MV Тип данных | MV Data Type
output format | Format de sortie | output format | output format | output format | output format | output format
Setpoint Data Type | SetPoint Donnée de Type | Setpoint Data Type | SetPoint Datos tipo | SetPoint Dados tipo | SetPoint Тип данных | Setpoint Data Type
order type | Type de commande | order type | Tipo de orden | Tipo de Ordem | Тип команды | order type
output format | Format de sortie | output format | output format | output format | output format | output format
minimal value | Valeur minimale | minimal value | minimal value | minimal value | minimal value | minimal value
maximal value | Valeur maximale | maximal value | maximal value | maximal value | maximal value | maximal value
acknowledgement delay | Délai acquittement | acknowledgement delay | acknowledgement delay | acknowledgement delay | acknowledgement delay | acknowledgement delay
Counter Data Type | Compteur de Donnée de Type | Counter Data Type | Counter Datos tipo | Contador de Dados tipo | Counter Тип данных | Counter Data Type
output format | Format de sortie | output format | output format | output format | output format | output format
END OF DATA | FIN DES DONNEES | END OF DATA | FIN DE DATOS | FIM DOS DADOS | КОНЕЦ ДАННЫХ | END OF DATA
Note on A150: Extension Racks : Number of Extension Racks attatched to current equipment.
Note on C150: Extension Racks : Number of Extension Racks attatched to current equipment.
Note on E150: Extension Racks : Number of Extension Racks attatched to current equipment.
Note on G150: Extension Racks : Number of Extension Racks attatched to current equipment.
Note on I150: Extension Racks : Number of Extension Racks attatched to current equipment.
Note on K150: Extension Racks : Number of Extension Racks attatched to current equipment.
Note on M150: Extension Racks : Number of Extension Racks attatched to current equipment.
Note on A991: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode Values for DetectMode: 0 : Permanent 1 : Transient 2 : Permanent with computer auto-reset
Note on E991: T101: Common address of ASDU;;DetectMode T103: Information number;Common address of ASDU;DetectMode (separator : ';') MODBUS: Function;;DetectMode DNP3: ;;DetectMode
Note on A1076: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator : ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute
Note on E1076: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator : ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute
Note on K1076: T101: Common address of ASDU T103: Information number;Common address of ASDU (separator : ';') MODBUS: Function DNP3: Not used
Note on M1076: T101: Common address of ASDU T103: Information number;Common address of ASDU (separator : ';') MODBUS: Function DNP3: Not used
Note on A1156: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on E1156: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on K1156: T101: Information Address T103: ASDU numberb;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address
Note on M1156: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address T103: ASDU number;Function type;Unit of the MEAS (separator : ';') MODBUS: Mapping address;Data Format (separator : ';') DNP3: Address Unit of the MEAS values: 0 : Voltage (default value if not set) 1 : Current 2 : Power 3 : Frequency 4 : No unit Data Format values: 0 : INT8_LB (default value if not set) 1 : INT8_HB 2 : UINT8_LB (default value if not set) 3 : UINT8_HB 4 : INT16 5 : UINT16 6 : INT32_LW_LB 7 : INT32_LW_HB 8 : INT32_HW_LB 9 : INT32_HW_HB 10 : UINT32_LW_LB 11 : UINT32_LW_HB 12 : UINT32_HW_LB 13 : UINT32_HW_HB 14 : REAL32_LW_LB 15 : REAL32_LW_HB 16 : REAL32_HW_LB 17 : REAL32_HW_HB 18 : M230_T5_TYPE (32 bits – unsigned MV) 19 : M230_T6_TYPE (32 bits – signed MV) 20 : M230_T7_TYPE (32 bits – power factor) 21 : unsigned ION_Modulus_10000 22 : signed ION_Modulus_10000 23 : KITZ202_K8 (48 bits values xx yy . zz)
Note on A1157: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used
Note on E1157: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used
Note on K1157: T101: Common address of ASDU T103: Information number;Common address of ASDU (separator : ';') MODBUS: Function DNP3: Not used
Note on M1157: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU T103 : Information number;Common address of ASDU;Index in ASDU (separator : ';') MODBUS : Function DNP3 : Not used
Note on A1236: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address DNP3: Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on E1236: IED Address (column 1) : The configuration of the address of the Data depend on the protocol used. How to fill : T101: Information Address;Output Format T103: ASDU number;Function type;Output Format (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address Ouput Format for Setpoint values: 6 : REAL32 (IEE754) (Default value if not set) 7 : Normalized 8 : Scaled
Note on K1236: T101: Information Address T103: ASDU numberb;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address
Note on M1236: T101: Information Address T103: ASDU numberb;Function type (separator : ';') MODBUS: Mapping address;Bit number (separator : ';') DNP3: Address
Note on A1237: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator : ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute
Note on E1237: IED Address (column 2) : The configuration of the address of the Data depend on the protocol used. How to fill : T101 : Common address of ASDU;;OrderType T103 : Information number;Common address of ASDU;OrderType (separator : ';') MODBUS : Function;;OrderType DNP3 : ;;OrderType OrderType values: 0 : SBO (Default value if not set) 1 : Direct execute
Note on K1237: T101: Common address of ASDU T103: Information number;Common address of ASDU (separator : ';') MODBUS: Function DNP3: Not used
Note on M1237: T101: Common address of ASDU T103: Information number;Common address of ASDU (separator : ';') MODBUS: Function DNP3: Not used
Note on A1922: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on C1922: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on E1922: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on G1922: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on I1922: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on K1922: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on M1922: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on A2019: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on C2019: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on E2019: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on G2019: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on I2019: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on K2019: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on M2019: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on A2162: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on C2162: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on E2162: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on G2162: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on I2162: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on K2162: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on M2162: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on A2390: Computation :
Note on C2390: Computation :
Note on E2390: Computation :
Note on G2390: Computation :
Note on I2390: Computation :
Note on K2390: Computation :
Note on M2390: Computation :
Note on A2391: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on C2391: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on E2391: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on G2391: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on I2391: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on K2391: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on M2391: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on A2392: Graphical Default Format: default format is a string like ##0,0# --> 2 digits before comma, 1 after, 0 displayed as 0,0
Note on C2392: Graphical Default Format: default format is a string like ##0,0# --> 2 digits before comma, 1 after, 0 displayed as 0,0
Note on E2392: Graphical Default Format: default format is a string like ##0,0# --> 2 digits before comma, 1 after, 0 displayed as 0,0
Note on G2392: Graphical Default Format: default format is a string like ##0,0# --> 2 digits before comma, 1 after, 0 displayed as 0,0
Note on I2392: Graphical Default Format: default format is a string like ##0,0# --> 2 digits before comma, 1 after, 0 displayed as 0,0
Note on K2392: Graphical Default Format: default format is a string like ##0,0# --> 2 digits before comma, 1 after, 0 displayed as 0,0
Note on M2392: Graphical Default Format: default format is a string like ##0,0# --> 2 digits before comma, 1 after, 0 displayed as 0,0
Note on A2393: Transmission on Event :
Note on C2393: Computation :
Note on E2393: Transmission on Event :
Note on G2393: Computation :
Note on I2393: Computation :
Note on K2393: Transmission on Event :
Note on M2393: Transmission on Event :
Note on A2394: Deadband :
Note on C2394: Computation :
Note on E2394: Deadband :
Note on G2394: Computation :
Note on I2394: Computation :
Note on K2394: Deadband :
Note on M2394: Deadband :
Note on A4285: Function Name : Name of this function. All links to this function in others sheets (Computer sheet, Substation data sheet) will use the Function Name. Limitation : A function Name must be unique in Electric function and System functions sheet.
Note on A4286: SCE Name : In the SCE, name of the Datapoint profile associated to this function. Limitation : - A SCE Name must be unique in Electric function and System functions sheet. - SCE Name should not exceed 13 chars.
Note on A4288: Energy equivalent to a pulse:
Note on C4288: Energy equivalent to a pulse:
Note on E4288: Energy equivalent to a pulse:
Note on G4288: Energy equivalent to a pulse:
Note on I4288: Energy equivalent to a pulse:
Note on K4288: Energy equivalent to a pulse:
Note on M4288: Energy equivalent to a pulse:
Note on A4289: Computation :
Note on C4289: Computation :
Note on E4289: Computation :
Note on G4289: Computation :
Note on I4289: Computation :
Note on K4289: Computation :
Note on M4289: Computation :
Note on A4290: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on C4290: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on E4290: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on G4290: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on I4290: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on K4290: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on M4290: SBMC dependant: Flag indicating that SBMC mode is inherited from Bay SBMC dependant.
Note on A4291: Graphical Default Format: default format is a string like ##0,0# --> 2 digits before comma, 1 after, 0 displayed as 0,0
Note on C4291: Graphical Default Format: default format is a string like ##0,0# --> 2 digits before comma, 1 after, 0 displayed as 0,0
Note on E4291: Graphical Default Format: default format is a string like ##0,0# --> 2 digits before comma, 1 after, 0 displayed as 0,0
Note on G4291: Graphical Default Format: default format is a string like ##0,0# --> 2 digits before comma, 1 after, 0 displayed as 0,0
Note on I4291: Graphical Default Format: default format is a string like ##0,0# --> 2 digits before comma, 1 after, 0 displayed as 0,0
Note on K4291: Graphical Default Format: default format is a string like ##0,0# --> 2 digits before comma, 1 after, 0 displayed as 0,0
Note on M4291: Graphical Default Format: default format is a string like ##0,0# --> 2 digits before comma, 1 after, 0 displayed as 0,0
Note on A4293: Generation condition :
Note on E4293: Generation condition :
Note on M4293: Generation condition :
Note on A4294: Audible alarm :
Note on E4294: Audible alarm :
Note on M4294: Audible alarm :
Note on A4295: Clearing mode :
Note on E4295: Clearing mode :
Note on M4295: Clearing mode :
Note on A4296: Alarm appearance delay :
Note on E4296: Alarm appearance delay :
Note on M4296: Alarm appearance delay :
Note on A4298: State label : label associated to this specific state. Limitation : Labed should not exceed 16 chars.
Note on A4299: State label : label associated to this specific state. Limitation : Labed should not exceed 16 chars.
Note on A4300: State label : label associated to this specific state. Limitation : Labed should not exceed 16 chars.
Note on A4301: State label : label associated to this specific state. Limitation : Labed should not exceed 16 chars.
Note on A4302: State label : label associated to this specific state. Limitation : Labed should not exceed 16 chars.
Note on A4303: State label : label associated to this specific state. Limitation : Labed should not exceed 16 chars.
Note on A4304: State treatment : Treatment associated to this specific state. Information : Possible values are : Archive only : this state is only archive Archive and logging : this state is archive and logged No archive, No logging : this state isn't archive and logged
Note on A4305: State treatment : Treatment associated to this specific state. Information : Possible values are : Archive only : this state is only archive Archive and logging : this state is archive and logged No archive, No logging : this state isn't archive and logged
Note on A4306: State treatment : Treatment associated to this specific state. Information : Possible values are : Archive only : this state is only archive Archive and logging : this state is archive and logged No archive, No logging : this state isn't archive and logged
Note on A4307: State treatment : Treatment associated to this specific state. Information : Possible values are : Archive only : this state is only archive Archive and logging : this state is archive and logged No archive, No logging : this state isn't archive and logged
Note on A4308: State treatment : Treatment associated to this specific state. Information : Possible values are : Archive only : this state is only archive Archive and logging : this state is archive and logged No archive, No logging : this state isn't archive and logged
Note on A4309: State treatment : Treatment associated to this specific state. Information : Possible values are : Archive only : this state is only archive Archive and logging : this state is archive and logged No archive, No logging : this state isn't archive and logged
Note on A4313: Alarm : Specify alarm management on this specific state. Information : This state can be : No : not alarmed. Yes, Gravity X : alarmed and has gravity X associated.
Note on A4314: Alarm : Specify alarm management on this specific state. Information : This state can be : No : not alarmed. Yes, Gravity X : alarmed and has gravity X associated.
Note on A4315: Alarm : Specify alarm management on this specific state. Information : This state can be : No : not alarmed. Yes, Gravity X : alarmed and has gravity X associated.
Note on A4316: Alarm : Specify alarm management on this specific state. Information : This state can be : No : not alarmed. Yes, Gravity X : alarmed and has gravity X associated.
Note on A4317: Alarm : Specify alarm management on this specific state. Information : This state can be : No : not alarmed. Yes, Gravity X : alarmed and has gravity X associated.
Note on A4318: Alarm : Specify alarm management on this specific state. Information : This state can be : No : not alarmed. Yes, Gravity X : alarmed and has gravity X associated.
Note on A5382: Deadband :
Note on C5382: Computation :
Note on E5382: Deadband :
Note on G5382: Computation :
Note on I5382: Computation :
Note on K5382: Deadband :
Note on M5382: Deadband :