## 213 BCU
220kV BC
Sr. No. | Voltage Level | Feeder Name | NAME ( BAY-213 BC )
|  |  | SIGNAL DESCRIPTION | Information type | Telegram address | Position | EVENT | ALARM
BINARY INPUT (Double Point)
1 | 200KV | 200KV BC | 89A POSITION | DP | B213_BCU89A$CSWI1$ST$Pos:2 | stVal | √
2 |  |  | 89AE1 POSITION | DP | B213_BCU89AE1$CSWI1$ST$Pos:2 | stVal | √
3 |  |  | 89AE2 POSITION | DP | B213_BCU89AE2$CSWI1$ST$Pos:2 | stVal | √
4 |  |  | 89B POSITION | DP | B213_BCU89B$CSWI1$ST$Pos:2 | stVal | √
5 |  |  | 89BE1 POSITION | DP | B213_BCU89BE1$CSWI1$ST$Pos:2 | stVal | √
6 |  |  | 89BE2 POSITION | DP | B213_BCU89BE2$CSWI1$ST$Pos:2 | stVal | √
7 |  |  | CB B-PH POSITION | DP | B213_BCUCB_1P_POSITION$RSLEDGAPC1$ST$DPS2 | stVal | √
8 |  |  | CB R-PH POSITION | DP | B213_BCUCB_1P_POSITION$RSLEDGAPC1$ST$DPS | stVal | √
9 |  |  | CB Y-PH POSITION | DP | B213_BCUCB_1P_POSITION$RSLEDGAPC1$ST$DPS1 | stVal | √
10 |  |  | CB POSITION | DP | B213_BCUCB$CSWI1$ST$Pos:2 | stVal | √
11
12 |  |  | COMMANDS
13
14 |  |  | 89A CONTROL | DC | B213_BCU89A$CSWI1$CO$Pos:8 | Oper$ctlVal | √
15 |  |  | 89AE1 CONTROL | DC | B213_BCU89AE1$CSWI1$CO$Pos:8 | Oper$ctlVal | √
16 |  |  | 89AE2 CONTROL | DC | B213_BCU89AE2$CSWI1$CO$Pos:8 | Oper$ctlVal | √
17 |  |  | 89B CONTROL | DC | B213_BCU89B$CSWI1$CO$Pos:8 | Oper$ctlVal | √
18 |  |  | 89BE1 CONTROL | DC | B213_BCU89BE1$CSWI1$CO$Pos:8 | Oper$ctlVal | √
19 |  |  | 89BE2 CONTROL | DC | B213_BCU89BE2$CSWI1$CO$Pos:8 | Oper$ctlVal | √
20 |  |  | CB CONTROL | DC | B213_BCUCB$CSWI1$CO$Pos:8 | Oper$ctlVal | √
21 |  |  | 86A TRIP RELAY RESET | SC | B213_BCUUD1$RSLEDGAPC1$CO$SPC:8 | Oper$ctlVal | √
22 |  |  | 86B TRIP RELAY RESET | SC
23
24 |  |  | MEASUREMENT
25
26 |  |  | POWER FACTOR | ME_FL | B213_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotPF:1 | mag$f
27 |  |  | FREQUENCY | ME_FL | B213_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$Hz:1 | mag$f
28 |  |  | ACTIVE POWER | ME_FL | B213_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotW:1 | mag$f
29 |  |  | REACTIVE POWER | ME_FL | B213_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVAr:1 | mag$f
30 |  |  | APPARENT POWER | ME_FL | B213_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVA:1 | mag$f
31 |  |  | I-R -PH CURRENT | ME_FL | B213_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsA$cVal$mag$f
32 |  |  | I-Y -PH CURRENT | ME_FL | B213_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsB$cVal$mag$f
33 |  |  | I-B -PH CURRENT | ME_FL | B213_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsC$cVal$mag$f
34 |  |  | R-Y VOLTAGE | ME_FL | B213_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsAB$cVal$mag$f
35 |  |  | Y-B VOLTAGE | ME_FL | B213_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsBC$cVal$mag$f
36 |  |  | B-R VOLYAGE | ME_FL | B213_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsCA$cVal$mag$f
37
38 |  |  | CB-B PH COUNTER | ME_I | B213_BCUUD3$RSLEDGAPC1$ST$INS2 | stVal |  | √
39 |  |  | CB-R PH COUNTER | ME_I | B213_BCUUD3$RSLEDGAPC1$ST$INS | stVal |  | √
40 |  |  | CB-Y PH COUNTER | ME_I | B213_BCUUD3$RSLEDGAPC1$ST$INS1 | stVal |  | √
41
42 |  |  | BINARY INPUT (Single Point)
43
44 |  |  | LED RESET | SP | B213_BCUApplication$LLN0$ST$LEDRs:2 | stVal | √
45 |  |  | BCU MODE | SP | B213_BCUApplication$LLN0$ST$LocKey | stVal | √
46 |  |  | 87B RELAY SUPERVISION | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS14 | stVal | √ | √
47 |  |  | 86A TRIP RELAY RESET
48 |  |  | 86A TRIP RELAY SUPERVISION
49 |  |  | 86A TRIP RELAY OPERATED
50 |  |  | 86B TRIP RELAY RESET | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPC:2 | stVal | √ | √
51 |  |  | 86B TRIP RELAY SUPERVISION | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS12 | stVal | √ | √
52 |  |  | 86B TRIP RELAY OPERATED | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS11 | stVal | √ | √
53 |  |  | AC KIOSK SMOKE DETECTED | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS19 | stVal | √ | √
54 |  |  | AC KIOSK HEAT FIRE DETECTED | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS18 | stVal | √
55 |  |  | CB AC SUPPLY FAIL | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS9 | stVal | √ | √
56 |  |  | AC SUPPLY-1 ON | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS20 | stVal | √ | √
57 |  |  | AC SUPPLY-1/2 FAIL | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS22 | stVal | √ | √
58 |  |  | AC SUPPLY-2 ON | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS21 | stVal | √ | √
59 |  |  | CB DC SUPPLY-1 FAIL | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS5 | stVal | √ | √
60 |  |  | CB DC SUPPLY-2 FAIL | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS6 | stVal | √ | √
61 |  |  | CB LOCAL | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS7 | stVal | √ | √
62 |  |  | EMERGENCY/MANUAL CLOSE | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS16 | stVal | √ | √
63 |  |  | EMERGENCY/MANUAL TRIP | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS15 | stVal | √ | √
64 |  |  | CB POLE DISCREPANCY OPERATED | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS1 | stVal | √ | √
65 |  |  | CB REMOTE POSITION SELECTED | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS8 | stVal | √ | √
66 |  |  | CB SF6 LOCKOUT | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS3 | stVal | √
67 |  |  | CB SF6 LOW ALARM | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS2 | stVal | √
68 |  |  | CB SPRING CHARGE STATUS | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS | stVal | √
69 |  |  | DC SUPPLY-1 FAIL | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS13 | stVal | √
70 |  |  | CB TC-1 R-PHASE FAULTY |  |  |  | √ | √
71 |  |  | CB TC-1 Y-PHASE FAULTY |  |  |  | √ | √
72 |  |  | CB TC-1 B-PHASE FAULTY |  |  |  | √ | √
73 |  |  | CB TC-2 R-PHASE FAULTY |  |  |  | √ | √
74 |  |  | CB TC-2 Y-PHASE FAULTY |  |  |  | √ | √
75 |  |  | CB TC-2 B-PHASE FAULTY |  |  |  | √ | √
76 |  |  | TIME SYNCHRONISATION ERROR | SP | B706_BCUApplication$LMTS0$ST$TmSynErr | stVal | √ | √
77 |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B213_BCUUD1$RSLEDGAPC1$ST$SPS35 | stVal | √
78 |  |  | CB MANUAL TRIP
79 |  |  | CB MANUAL CLOSE
80 |  |  | BUSBAR OPERATED
81 |  |  | BCU IN LOCAL/REMOTE
82 |  |  | SETTINGS CHANGED |  |  |  |  | √
83 |  |  | RELAY IN TEST MODE |  |  |  |  | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 50-51N
220KV BC
Sr. No. | Voltage Level | Feeder Name | NAME ( 213 BC )
|  |  | SIGNAL DESCRIPTION | Information type | Telegram address | Position | EVENT | ALARM
BINARY INPUT (Single Point)
1
2 |  |  | TIME SYNCHRONISATION ERROR | SP | B213_5051NEXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
3 |  |  | VT FUSE FAILURE | SP | B213_5051NEXT$pdGGIO3$ST$SPCSO41:0 | stVal | √ | √
4 |  |  | DIRECTIONAL DMT TRIP | SP | B213_5051NPROT$PTRC3$ST$Op | stVal | √ | √
5 |  |  | DIRECTIONAL DMT PICKUP | SP | B213_5051NPROT$PTRC3$ST$Str | stVal | √
6 |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-1 TRIP | SP | B213_5051NPROT$PTOC10$ST$Op | stVal | √ | √
7 |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-1 PICKUP | SP | B213_5051NPROT$PTOC10$ST$Str | stVal | √
8 |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-2 TRIP | SP | B213_5051NPROT$PTOC11$ST$Op | stVal | √ | √
9 |  |  | DIRECTIONAL DMT OVERCURRENT STAGE-2 PICKUP | SP | B213_5051NPROT$PTOC11$ST$Str | stVal | √
10 |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-1 TRIP | SP | B213_5051NPROT$PTOC12$ST$Op | stVal | √ | √
11 |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-1 PICKUP | SP | B213_5051NPROT$PTOC12$ST$Str | stVal | √
12 |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-2 TRIP | SP | B213_5051NPROT$PTOC13$ST$Op | stVal | √ | √
13 |  |  | DIRECTIONAL DMT EARTHFAULT STAGE-2 PICKUP | SP | B213_5051NPROT$PTOC13$ST$Str | stVal | √
14 |  |  | DIRECTIONAL IDMT EARTHFAULT TRIP | SP | B213_5051NPROT$PTOC4$ST$Op | stVal | √ | √
15 |  |  | DIRECTIONAL IDMT EARTHFAULT PICKUP | SP | B213_5051NPROT$PTOC4$ST$Str | stVal | √
16 |  |  | DIRECTIONAL IDMT OVERCURRENT TRIP | SP | B213_5051NPROT$PTOC3$ST$Op | stVal | √ | √
17 |  |  | DIRECTIONAL IDMT OVERCURRENT PICKUP | SP | B213_5051NPROT$PTOC3$ST$Str | stVal | √
18 |  |  | DMT TRIP | SP | B213_5051NPROT$PTRC2$ST$Op | stVal | √ | √
19 |  |  | DMT PICKUP | SP | B213_5051NPROT$PTRC2$ST$Str | stVal | √
20 |  |  | DMT OVERCURRENT STAGE-1 TRIP | SP | B213_5051NPROT$PTOC6$ST$Op | stVal | √ | √
21 |  |  | DMT OVERCURRENT STAGE-1 PICKUP | SP | B213_5051NPROT$PTOC6$ST$Str | stVal | √
22 |  |  | DMT OVERCURRENT STAGE-2 TRIP | SP | B213_5051NPROT$PTOC7$ST$Op | stVal | √ | √
23 |  |  | DMT OVERCURRENT STAGE-2 PICKUP | SP | B213_5051NPROT$PTOC7$ST$Str | stVal | √
24 |  |  | DMT OVERCURRENT STAGE-3 TRIP | SP | B213_5051NPROT$PTOC18$ST$Op | stVal | √ | √
25 |  |  | DMT OVERCURRENT STAGE-3 PICKUP | SP | B213_5051NPROT$PTOC18$ST$Str | stVal | √
26 |  |  | DMT EARTHFAULT STAGE-1 TRIP | SP | B213_5051NPROT$PTOC8$ST$Op | stVal | √ | √
27 |  |  | DMT EARTHFAULT STAGE-1 PICKUP | SP | B213_5051NPROT$PTOC8$ST$Str | stVal | √
28 |  |  | DMT EARTHFAULT STAGE-2 TRIP | SP | B213_5051NPROT$PTOC9$ST$Op | stVal | √ | √
29 |  |  | DMT EARTHFAULT STAGE-2 PICKUP | SP | B213_5051NPROT$PTOC9$ST$Str | stVal | √
30 |  |  | THERMAL OVERLOAD TRIP | SP | B213_5051NPROT$PTTR1$ST$Op | stVal | √ | √
31 |  |  | THERMAL OVERLOAD PICKUP | SP | B213_5051NPROT$PTTR1$ST$Str | stVal | √
32 |  |  | GENERAL TRIP | SP | B213_5051NPROT$PTRC1$ST$Tr | stVal | √ | √
33 |  |  | GENERAL PICKUP | SP | B213_5051NPROT$PTRC1$ST$Str | stVal | √
34 |  |  | SETTINGS CHANGED |  |  |  |  | √
35 |  |  | RELAY IN TEST MODE |  |  |  |  | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.