## B200_MCU
400kV LINE
Sr. No. | Voltage Level | Feeder Name | NAME ( 200 MCU )
|  |  | SIGNAL DESCRIPTION | Information type | Telegram address | Position | EVENT | ALARM
BINARY INPUT (Single Point)
1 | 200KV | 200KV MCU | GENERAL TRIP R-PH | SP | BBP_220KV_MCUPROT$PTRC1$ST$Tr | phsA | √ | √
2 |  |  | GENERAL TRIP Y-PH | SP | BBP_220KV_MCUPROT$PTRC1$ST$Tr | phsB | √ | √
3 |  |  | GENERAL TRIP B-PH | SP | BBP_220KV_MCUPROT$PTRC1$ST$Tr | phsC | √ | √
4 |  |  | TRIP COMMAND BUS-BUS-3 B-PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO23:0 | stVal | √ | √
5 |  |  | TRIP COMMAND BUS-BUS-3 Y-PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO22:0 | stVal | √ | √
6 |  |  | TRIP COMMAND BUS-BUS-3 R-PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO21:0 | stVal | √ | √
7 |  |  | TRIP COMMAND BUS-2 B- PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO13:0 | stVal | √ | √
8 |  |  | TRIP COMMAND BUS-2 Y- PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO12:0 | stVal | √ | √
9 |  |  | TRIP COMMAND BUS-2 R- PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO11:0 | stVal | √ | √
10 |  |  | TRIP COMMAND BUS-1 B- PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO3:0 | stVal | √ | √
11 |  |  | TRIP COMMAND BUS-1 Y- PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO2:0 | stVal | √ | √
12 |  |  | TRIP COMMAND BUS-1 R- PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO1:0 | stVal | √ | √
13 |  |  | BREAKER FAILURE OPERATED BUS-3 B-PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO26:0 | stVal | √ | √
14 |  |  | BREAKER FAILURE OPERATED BUS-3 Y-PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO25:0 | stVal | √ | √
15 |  |  | BREAKER FAILURE OPERATED BUS-3 R-PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO24:0 | stVal | √ | √
16 |  |  | BREAKER FAILURE OPERATED BUS-2 B-PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO16:0 | stVal | √ | √
17 |  |  | BREAKER FAILURE OPERATED BUS-2 Y-PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO15:0 | stVal | √ | √
18 |  |  | BREAKER FAILURE OPERATED BUS-2 R-PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO14:0 | stVal | √ | √
19 |  |  | BREAKER FAILURE OPERATED BUS-1 B-PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO6:0 | stVal | √ | √
20 |  |  | BREAKER FAILURE OPERATED BUS-1 Y-PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO5:0 | stVal | √ | √
21 |  |  | BREAKER FAILURE OPERATED BUS-1 R-PH | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO4:0 | stVal | √ | √
22 |  |  | BUS-3 BUS CT SUPERVISION ALARM | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO30:0 | stVal | √ | √
23 |  |  | BUS-2 CT SUPERVISION ALARM | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO20:0 | stVal | √ | √
24 |  |  | BUS-1 CT SUPERVISION ALARM | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO10:0 | stVal | √ | √
25 |  |  | BLOCKED TRIP COMMAND BUS-3 (BUS-3) | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO28:0 | stVal | √ | √
26 |  |  | BLOCKED TRIP COMMAND BUS-2 | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO18:0 | stVal | √ | √
27 |  |  | BLOCKED TRIP COMMAND BUS-1 | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO8:0 | stVal | √ | √
28 |  |  | BLOCKED BY BUS-3 | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO27:0 | stVal | √ | √
29 |  |  | BLOCKED BY BUS-2 | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO17:0 | stVal | √ | √
30 |  |  | BLOCKED BY BUS-1 | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO7:0 | stVal | √ | √
31 |  |  | BUS-3 PROTECTION BLOCKED BY HANDLE | SP | BBP_220KV_MCUPROT$GGIO1$ST$SPCSO33:0 | stVal | √ | √
32 |  |  | BUS-1 PROTECTION BLOCKED BY HANDLE | SP | BBP_220KV_MCUPROT$GGIO1$ST$SPCSO32:0 | stVal | √ | √
33 |  |  | BUS-2 PROTECTION BLOCKED BY HANDLE | SP | BBP_220KV_MCUPROT$GGIO1$ST$SPCSO31:0 | stVal | √ | √
34 |  |  | BLOCKED BREAKER FAILURE PROTECTION BUS-3 | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO29:0 | stVal | √ | √
35 |  |  | BLOCKED BREAKER FAILURE PROTECTION BUS-2 | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO19:0 | stVal | √ | √
36 |  |  | BLOCKED BREAKER FAILURE PROTECTION BUS-1 | SP | BBP_220KV_MCUPROT$GGIO4$ST$SPCSO9:0 | stVal | √ | √
37 |  |  | BUS-3 BUS TRIP | SP | BBP_220KV_MCUPROT$GGIO3$ST$SPCSO14:0 | stVal | √ | √
38 |  |  | BUSBAR TRIP | SP | BBP_220KV_MCUPROT$PDIF1$ST$Op | stVal | √ | √
39 |  |  | BUS ZONE 1 TRIP | SP | BBP_220KV_MCUPROT$GGIO3$ST$SPCSO13:0 | stVal | √ | √
40 |  |  | BUS ZONE 2 TRIP | SP | BBP_220KV_MCUPROT$GGIO3$ST$SPCSO12:0 | stVal | √ | √
41 |  |  | BLOCKED BREAKER FAILURE PROTECTION BUS-3 | SP | BBP_220KV_MCUPROT$GGIO3$ST$SPCSO17:0 | stVal | √ | √
42 |  |  | BLOCKED BREAKER FAILURE PROTECTION BUS-2 | SP | BBP_220KV_MCUPROT$GGIO3$ST$SPCSO16:0 | stVal | √ | √
43 |  |  | BLOCKED BREAKER FAILURE PROTECTION BUS-1 | SP | BBP_220KV_MCUPROT$GGIO3$ST$SPCSO15:0 | stVal | √ | √
44 |  |  | B213- BAY UNIT OUT OF SERVICE | SP | BBP_220KV_MCUPROT$GGIO3$ST$SPCSO7:0 | stVal | √ | √
45 |  |  | B213- BAY UNIT FAILURE | SP | BBP_220KV_MCUPROT$GGIO3$ST$SPCSO1:0 | stVal | √ | √
46 |  |  | B212- BAY UNIT OUT OF SERVICE | SP | BBP_220KV_MCUPROT$GGIO2$ST$SPCSO57:0 | stVal | √ | √
47 |  |  | B212- BAY UNIT FAILURE | SP | BBP_220KV_MCUPROT$GGIO2$ST$SPCSO51:0 | stVal | √ | √
48 |  |  | B211- BAY UNIT OUT OF SERVICE | SP | BBP_220KV_MCUPROT$GGIO2$ST$SPCSO47:0 | stVal | √ | √
49 |  |  | B211- BAY UNIT FAILURE | SP | BBP_220KV_MCUPROT$GGIO2$ST$SPCSO41:0 | stVal | √ | √
50 |  |  | B210- BAY UNIT OUT OF SERVICE | SP | BBP_220KV_MCUPROT$GGIO2$ST$SPCSO37:0 | stVal | √ | √
51 |  |  | B210- BAY UNIT FAILURE | SP | BBP_220KV_MCUPROT$GGIO2$ST$SPCSO31:0 | stVal | √ | √
52 |  |  | B209- BAY UNIT OUT OF SERVICE | SP | BBP_220KV_MCUPROT$GGIO2$ST$SPCSO27:0 | stVal | √ | √
53 |  |  | B209- BAY UNIT FAILURE | SP | BBP_220KV_MCUPROT$GGIO2$ST$SPCSO21:0 | stVal | √ | √
54 |  |  | B208- BAY UNIT OUT OF SERVICE | SP | BBP_220KV_MCUPROT$GGIO2$ST$SPCSO17:0 | stVal | √ | √
55 |  |  | B208- BAY UNIT FAILURE | SP | BBP_220KV_MCUPROT$GGIO2$ST$SPCSO11:0 | stVal | √ | √
56 |  |  | B207- BAY UNIT OUT OF SERVICE | SP | BBP_220KV_MCUPROT$GGIO2$ST$SPCSO7:0 | stVal | √ | √
57 |  |  | B207- BAY UNIT FAILURE | SP | BBP_220KV_MCUPROT$GGIO2$ST$SPCSO1:0 | stVal | √ | √
58 |  |  | B206- BAY UNIT OUT OF SERVICE | SP | BBP_220KV_MCUPROT$GGIO1$ST$SPCSO57:0 | stVal | √ | √
59 |  |  | B206- BAY UNIT FAILURE | SP | BBP_220KV_MCUPROT$GGIO1$ST$SPCSO51:0 | stVal | √ | √
60 |  |  | B205- BAY UNIT OUT OF SERVICE | SP | BBP_220KV_MCUPROT$GGIO1$ST$SPCSO47:0 | stVal | √ | √
61 |  |  | B205- BAY UNIT FAILURE | SP | BBP_220KV_MCUPROT$GGIO1$ST$SPCSO41:0 | stVal | √ | √
62 |  |  | B204- BAY UNIT OUT OF SERVICE | SP | BBP_220KV_MCUPROT$GGIO1$ST$SPCSO37:0 | stVal | √ | √
63 |  |  | B204- BAY UNIT FAILURE | SP | BBP_220KV_MCUPROT$GGIO1$ST$SPCSO31:0 | stVal | √ | √
64 |  |  | B203- BAY UNIT OUT OF SERVICE | SP | BBP_220KV_MCUPROT$GGIO1$ST$SPCSO27:0 | stVal | √ | √
65 |  |  | B203- BAY UNIT FAILURE | SP | BBP_220KV_MCUPROT$GGIO1$ST$SPCSO21:0 | stVal | √ | √
66 |  |  | B202- BAY UNIT OUT OF SERVICE | SP | BBP_220KV_MCUPROT$GGIO1$ST$SPCSO17:0 | stVal | √ | √
67 |  |  | B202- BAY UNIT FAILURE | SP | BBP_220KV_MCUPROT$GGIO1$ST$SPCSO11:0 | stVal | √ | √
68 |  |  | B201- BAY UNIT OUT OF SERVICE | SP | BBP_220KV_MCUPROT$GGIO1$ST$SPCSO7:0 | stVal | √ | √
69 |  |  | B201- BAY UNIT FAILURE | SP | BBP_220KV_MCUPROT$GGIO1$ST$SPCSO1:0 | stVal | √ | √
70 |  |  | TIME SYNCHRONISATION ERROR | SP | BBP_220KV_MCUEXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
71 |  |  | BAY UNIT FAILURE GROUP ALARM | SP | BBP_220KV_MCUEXT$pdGGIO164$ST$SPCSO23:0 | stVal | √ | √
72 |  |  | BAY OUT OF SERVICE GROUP ALARM | SP | BBP_220KV_MCUEXT$pdGGIO164$ST$SPCSO21:0 | stVal | √ | √
73 |  |  | BUS-3 BUS SWITCH OUT | SP | BBP_220KV_MCUCTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
74 |  |  | DC SOURCE-2 FAIL | SP | BBP_220KV_MCUCTRL$GGIO1$ST$SPCSO5:0 | stVal | √ | √
75 |  |  | DC SOURCE-1 FAIL | SP | BBP_220KV_MCUCTRL$GGIO1$ST$SPCSO4:0 | stVal | √ | √
76 |  |  | BUS-2 SWITCH OUT | SP | BBP_220KV_MCUCTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
77 |  |  | BUS-1 SWITCH OUT | SP | BBP_220KV_MCUCTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
78 |  |  | LED RESET | SP | BBP_220KV_MCUCTRL$LLN0$ST$LEDRs:2 | stVal | √
79 |  |  | Busbar-1 Zone OPERATED | SP | BBP_220KV_MCUPROT$GGIO3$SPCSO12 | stVal | √ | √
80 |  |  | Busbar-2 Zone OPERATED | SP | BBP_220KV_MCUPROT$GGIO3$SPCSO13 | stVal | √ | √
81 |  |  | BUS-3 BUSBAR ZONE OPERATED | SP | BBP_220KV_MCUPROT$GGIO3$SPCSO14 | stVal | √ | √
82 |  |  | BUS-1 BLOCK DUE TO INDERM STATE | SP | BBP_220KV_MCUCTRL$GGIO1$SPCSO9 | stVal | √ | √
83 |  |  | BUS-1 BLOCK DUE TO COMMUNICATION FAIL | SP | BBP_220KV_MCUCTRL$GGIO1$SPCSO10 | stVal | √ | √
84 |  |  | BUS-2 BLOCK DUE TO INDERM STATE | SP | BBP_220KV_MCUCTRL$GGIO1$SPCSO11 | stVal | √ | √
85 |  |  | BUS-2 BLOCK DUE TO COMMUNICATION FAIL | SP | BBP_220KV_MCUCTRL$GGIO1$SPCSO12 | stVal | √ | √
86 |  |  | BUS-3 BLOCK DUE TO INDERM STATE | SP | BBP_220KV_MCUCTRL$GGIO1$SPCSO13 | stVal | √ | √
87 |  |  | BUS-3 BLOCK DUE TO COMMUNICATION FAIL | SP | BBP_220KV_MCUCTRL$GGIO1$SPCSO14 | stVal | √ | √
88 |  |  | LBB TRIP | SP | BBP_220KV_MCUPROT$RBRF1$OpEx | stVal | √ | √
89 |  |  | LBB RETRIP | SP | BBP_220KV_MCUPROT$RBRF1$OpIn | stVal | √ | √
90 |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | BBP_220KV_MCUCTRL$GGIO1$SPCSO15 | stVal | √ | √
71 |  |  | BUSBAR CHECKZONE ALARM
72 |  |  | BUSBAR CHECKZONE TRIP
73 |  |  | BREAKER FAILURE - BUSBAR 1 BLOCKED
74 |  |  | BREAKER FAILURE - BUSBAR 2 BLOCKED
75 |  |  | ISOLATOR IN INTERMEDIATE STATUS
76 |  |  | BAY N TRIP
77 |  |  | BUSBAR BLOCKED DUE TO COMMUNICATION ERROR_Bay_n
78 |  |  | BAY_N_BREAKER FAILURE R-PH INITIATION
79 |  |  | BAY_N_BREAKER FAILURE Y-PH INITIATION
80 |  |  | BAY_N_BREAKER FAILURE B-PH INITIATION
81 |  |  | BAY_N_BREAKER FAILURE 3PH INITIATION
82 |  |  | BAY_N_EXTERNAL BUSBAR ZONE n
83 |  |  | BAY_N_BREAKER FAILURE RETRIP
84 |  |  | BAY_N_BREAKER FAILURE BACKTRIP
85 |  |  | BAY_N_BREAKER FAILURE RPH- RETRIP
86 |  |  | BAY_N_BREAKER FAILURE YPH- RETRIP
87 |  |  | BAY_N_BREAKER FAILURE BPH- RETRIP
88 |  |  | BBP CENTRAL UNIT IED UNHEALTHY
89 |  |  | SETTING CHANGE
90 |  |  | BUS ZONE MERGE/BUS INTERCONNECT ALARM
91 |  |  | RELAY IN TEST MODE
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.