## 209 TBC
220KV TBC
Sr. No. | Voltage Level | Feeder Name | NAME ( BAY-207 TBC )
|  |  | SIGNAL DESCRIPTION | Information type | Telegram address | Position | EVENT | ALARM
BINARY INPUT (Double Point)
1 | 200KV | 200KV TBC | 89A POSITION | DP | B209_BCU89A$CSWI1$ST$Pos:2 | stVal | √
2 |  |  | 89AE POSITION | DP | B209_BCU89AE$CSWI1$ST$Pos:2 | stVal | √
3 |  |  | 89B POSITION | DP | B209_BCU89B$CSWI1$ST$Pos:2 | stVal | √
4 |  |  | 89C POSITION | DP | B209_BCU89C$CSWI1$ST$Pos:2 | stVal | √
5 |  |  | 89C POSITION | DP | B209_BCU89C$CSWI1$ST$Pos:2 | stVal | √
6 |  |  | 89CE1 POSITION | DP | B209_BCU89CE1$CSWI1$ST$Pos:2 | stVal | √
7 |  |  | 89CE2 POSITION | DP | B209_BCU89CE2$CSWI1$ST$Pos:2 | stVal | √
8 |  |  | CB B-PH POSITION | DP | B209_BCUCB_1P_POSITION$RSLEDGAPC1$ST$DPS2 | stVal | √
9 |  |  | CB R-PH POSITION | DP | B209_BCUCB_1P_POSITION$RSLEDGAPC1$ST$DPS | stVal | √
10 |  |  | CB Y-PH POSITION | DP | B209_BCUCB_1P_POSITION$RSLEDGAPC1$ST$DPS1 | stVal | √
11 |  |  | CB POSITION | DP | B209_BCUCB$CSWI1$ST$Pos:2 | stVal | √
12
13 |  |  | BINARY INPUT (Single Point)
14
15 |  |  | LED RESET | SP | B209_BCUApplication$LLN0$ST$LEDRs:2 | stVal | √
16 |  |  | BCU MODE | SP | B209_BCUApplication$LLN0$ST$LocKey | stVal | √
17 |  |  | 86A TRIP RELAY RESET | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPC:2 | stVal | √ | √
18 |  |  | 86A TRIP RELAY SUPERVISION | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS12 | stVal | √ | √
19 |  |  | 86A TRIP RELAY OPERATED | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS11 | stVal | √ | √
20 |  |  | 86B TRIP RELAY RESET | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPC1:2 | stVal | √ | √
21 |  |  | 86B TRIP RELAY SUPERVISION | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS24 | stVal | √ | √
22 |  |  | 86B TRIP RELAY OPERATED | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS23 | stVal | √ | √
23 |  |  | 87B TRIP RELAY SUPERVISION | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS14 | stVal | √ | √
24 |  |  | AC KIOSK HEAT FIRE DETECTED | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS19 | stVal | √ | √
25 |  |  | AC KIOSK SMOKE DETECTED | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS18 | stVal | √ | √
26 |  |  | CB AC SUPPLY FAIL | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS9 | stVal | √ | √
27 |  |  | AC SUPPLY-1 ON | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS20 | stVal | √ | √
28 |  |  | AC SUPPLY-1/2 FAIL | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS22 | stVal | √ | √
29 |  |  | AC SUPPLY-2 ON | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS21 | stVal | √ | √
30 |  |  | NORMAL MODE | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS26 | stVal | √ | √
31 |  |  | TRANSFER MODE | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS25 | stVal | √
32 |  |  | BUS-1 VT RESET | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS35 | stVal | √ | √
33 |  |  | BUS-1 VT SELECTED | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS34 | stVal | √ | √
34 |  |  | BUS-2 VT RESET | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS28 | stVal | √ | √
35 |  |  | BUS-2 VT SELECTED | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS27 | stVal | √ | √
36 |  |  | CB DC SUPPLY-1 FAIL | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS5 | stVal | √ | √
37 |  |  | CB DC SUPPLY-2 FAIL | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS6 | stVal | √ | √
38 |  |  | CB LOCAL | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS7 | stVal | √ | √
39 |  |  | EMERGENCY/MANUAL CLOSE | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS16 | stVal | √ | √
40 |  |  | EMERGENCY/MANUAL TRIP | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS15 | stVal | √ | √
41 |  |  | CB POLE DISCREPANCY OPERATED | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS1 | stVal | √ | √
42 |  |  | CB REMOTE POSITION SELECTED | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS8 | stVal | √ | √
43 |  |  | CB SF6 LOCKOUT | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS3 | stVal | √ | √
44 |  |  | CB SF6 LOW ALARM | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS2 | stVal | √
45 |  |  | CB SPRING CHARGE STATUS | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS | stVal | √
46 |  |  | DC SUPPLY-1 FAIL | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS13 | stVal | √
47 |  |  | CB TC-1 R-PHASE FAULTY |  |  |  | √ | √
48 |  |  | CB TC-1 Y-PHASE FAULTY |  |  |  | √ | √
49 |  |  | CB TC-1 B-PHASE FAULTY |  |  |  | √ | √
50 |  |  | CB TC-2 R-PHASE FAULTY |  |  |  | √ | √
51 |  |  | CB TC-2 Y-PHASE FAULTY |  |  |  | √ | √
52 |  |  | CB TC-2 B-PHASE FAULTY |  |  |  | √ | √
53 |  |  | TRANSFER RESET | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS33 | stVal | √
54 |  |  | TRANSFER SELECTED | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS32 | stVal | √
55 |  |  | TIME SYNCHRONISATION ERROR | SP | B706_BCUApplication$LMTS0$ST$TmSynErr | stVal | √ | √
56 |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B209_BCUUD1$RSLEDGAPC1$ST$SPS35 | stVal | √
57
58 |  |  | MEASUREMENT
59
60 |  |  | POWER FACTOR | ME_FL | B209_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotPF:1 | mag$f
61 |  |  | FREQUENCY | ME_FL | B209_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$Hz:1 | mag$f
62 |  |  | ACTIVE POWER | ME_FL | B209_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotW:1 | mag$f
63 |  |  | REACTIVE POWER | ME_FL | B209_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVAr:1 | mag$f
64 |  |  | APPARENT POWER | ME_FL | B209_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVA:1 | mag$f
65 |  |  | I-R -PH CURRENT | ME_FL | B209_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsA$cVal$mag$f
66 |  |  | I-Y -PH CURRENT | ME_FL | B209_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsB$cVal$mag$f
67 |  |  | I-B -PH CURRENT | ME_FL | B209_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsC$cVal$mag$f
68 |  |  | R-Y VOLTAGE | ME_FL | B209_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsAB$cVal$mag$f
69 |  |  | Y-B VOLTAGE | ME_FL | B209_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsBC$cVal$mag$f
70 |  |  | B-R VOLYAGE | ME_FL | B209_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsCA$cVal$mag$f
71
72 |  |  | CB-B PH COUNTER | ME_I | B209_BCUUD3$RSLEDGAPC1$ST$INS2 | stVal |  | √
73 |  |  | CB-R PH COUNTER | ME_I | B209_BCUUD3$RSLEDGAPC1$ST$INS | stVal |  | √
74 |  |  | CB-Y PH COUNTER | ME_I | B209_BCUUD3$RSLEDGAPC1$ST$INS1 | stVal |  | √
75
76 |  |  | COMMANDS
77
78 |  |  | 89A CONTROL | DC | B209_BCU89A$CSWI1$CO$Pos:8 | Oper$ctlVal | √
79 |  |  | 89AE CONTROL | DC | B209_BCU89AE$CSWI1$CO$Pos:8 | Oper$ctlVal | √ | √
80 |  |  | 89B CONTROL | DC | B209_BCU89B$CSWI1$CO$Pos:8 | Oper$ctlVal | √
81 |  |  | 89C CONTROL | DC | B209_BCU89C$CSWI1$CO$Pos:8 | Oper$ctlVal | √
82 |  |  | 89C CONTROL | DC | B209_BCU89C$CSWI1$CO$Pos:8 | Oper$ctlVal | √ | √
83 |  |  | 89CE1 CONTROL | DC | B209_BCU89CE1$CSWI1$CO$Pos:8 | Oper$ctlVal | √
84 |  |  | 89CE2 CONTROL | DC | B209_BCU89CE2$CSWI1$CO$Pos:8 | Oper$ctlVal | √
85 |  |  | CB CONTROL | DC | B209_BCUCB$CSWI1$CO$Pos:8 | Oper$ctlVal | √
86 |  |  | TRANSFER/NORMAL CONTROL | DC | B209_BCUDc8$CSWI1$CO$Pos:8 | Oper$ctlVal | √
87 |  |  | 86A TRIP RELAY RESET COMMAND | SC | B209_BCUUD1$RSLEDGAPC1$CO$SPC:8 | Oper$ctlVal | √
88 |  |  | 86B TRIP RELAY RESET COMMAND | SC | B209_BCUUD1$RSLEDGAPC1$CO$SPC1:8 | Oper$ctlVal | √
89 |  |  | CB MANUAL TRIP
90 |  |  | CB MANUAL CLOSE
91 |  |  | BUSBAR OPERATED
92 |  |  | BCU IN LOCAL/REMOTE
93 |  |  | SETTINGS CHANGED |  |  |  |  | √
94 |  |  | RELAY IN TEST MODE |  |  |  |  | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.