## LEGEND
SIEMENS SCADA GENERAL SIGNAL LIST FOR VARIOUS PROTECTION & CONTROL SIGNALS - REV03 (INDEX)
Sheet Ref. | IED MODEL | IED SYMBOLIC NAME(TYPICAL) | APPLICATION | IED NAME IN SCD | Additional Remarks
1 | 6MD66 | BCU | REACTOR BCU | STNM7XXBCU | BCU is for each bay so 7XX refers to Bay
2 | 7SJ80 | 7SJ8_64T.2B | REF RELAY PHASE B FOR ICT | STNM7XXTREFB | Bay No. 7XX will be always the main bay number for the ICT feeder
3 | 7SJ80 | 7SJ8_64T.2R | REF RELAY PHASE R FOR ICT | STNM7XXTREFR | Bay No. 7XX will be always the main bay number for the ICT feeder
4 | 7SJ80 | 7SJ8_64T.2Y | REF RELAY PHASE Y FOR ICT | STNM7XXTREFY | Bay No. 7XX will be always the main bay number for the ICT feeder
5 | 7SJ80 | 7SJ8_64T.2SP | REF RELAY PHASE SP FOR ICT | STNM7XXTREFS | Bay No. 7XX will be always the main bay number for the ICT feeder
6 | 7SA522 | 7SJ8_67_1 LV | REACTOR BACKUP IMPEDANCE | STNM7XXTLVBU | Bay No. 7XX will be always the main bay number for the ICT feeder
7 | 7UT613 | 7UT613_87T_99HV | ICT DIFFERENTIAL RELAY | STNM7XXTDIF | Bay No. 7XX will be always the main bay number for the ICT feeder
NOTE 1: The characters "STNM" stand for Substation Name with maximum 4 characters, this code will be given by POWERGRID for each project.
NOTE 2: The characters "7XX" stand for Bay name, example if the bay no 701 then same has to be implemented like STNM701BCU

## BCU
765kV BUS REACTOR (BCU)
Sr. No. | Voltage Level | Feeder Name | Source | Signal Decription
|  |  |  | NAME ( BAY-703 BUS REACTOR ) | INFORMATION TYPE | Telegram Address | POSITION | Event | Alarm
BINARY INPUT (Double Point)
1 | 765kV | 765kV BUS REACTOR | BCU | CB R-PH POSITION | DP | B703_BCUCBB$XCBR1$ST$Pos:2 | stVal | √
2 |  |  |  | CB Y-PH POSITION | DP | B703_BCUCBR$XCBR1$ST$Pos:2 | stVal | √
3 |  |  |  | CB B-PH POSITION | DP | B703_BCUCBY$XCBR1$ST$Pos:2 | stVal | √
4 |  |  |  | CB POSITION | DP | B703_BCUCB$CSWI1$ST$Pos:2 | stVal | √
5 |  |  |  | 89AE1 POSITION | DP | B703_BCU89AE1$CSWI3$ST$Pos:2 | stVal | √
6 |  |  |  | 89AE2 POSITION | DP | B703_BCU89AE2$CSWI6$ST$Pos:2 | stVal | √
7 |  |  |  | 89BE1 POSITION | DP | B703_BCU89BE1$CSWI5$ST$Pos:2 | stVal | √
8 |  |  |  | 89BE2 POSITION | DP | B703_BCU89BE2$CSWI7$ST$Pos:2 | stVal | √
9 |  |  |  | 89RE-B POSITION | DP | B703_BCU89REB$CSWI9$ST$Pos:2 | stVal | √
10 |  |  |  | 89RE-R POSITION | DP | B703_BCU89RER$CSWI9$ST$Pos:2 | stVal | √
11 |  |  |  | 89RE-Y POSITION | DP | B703_BCU89REY$CSWI9$ST$Pos:2 | stVal | √
12 |  |  |  | 89A POSITION | DP | B703_BCU89A$CSWI2$ST$Pos:2 | stVal | √
13 |  |  |  | 89B POSITION | DP | B703_BCU89B$CSWI4$ST$Pos:2 | stVal | √
14 |  |  |  | 89R-B POSITION | DP | B703_BCU89RB$CSWI8$ST$Pos:2 | stVal | √
15 |  |  |  | 89R-R POSITION | DP | B703_BCU89RR$CSWI8$ST$Pos:2 | stVal | √
16 |  |  |  | 89R-Y POSITION | DP | B703_BCU89RY$CSWI8$ST$Pos:2 | stVal | √
17 |  |  |  | S89RE2 POSITION
18 |  |  |  | S89R-R POSITION
19 |  |  |  | S89R-Y POSITION
20 |  |  |  | S89R-B POSITION
21 |  |  |  | BINARY INPUT (Single Point)
22
23 |  |  |  | BCU IN LOCAL/REMOTE | SP |  |  | √
24 |  |  |  | AUX POWER FAIL | SP | B703_BCUApplication$LPHD0$ST$AuxPwrFail | stVal | √ | √
25 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B703_BCUApplication$LMTS0$ST$TmSynErr | stVal | √
26 |  |  |  | BCU MODE | SP | B703_BCUApplication$LLN0$ST$LocKey | stVal | √ | √
27 |  |  |  | CB SF6 GAS PRESSURE REFILL LOW ALARM | SP | B703_BCUApplication$USER1$ST$SPS | stVal | √ | √
28 |  |  |  | CB SF6 GAS PRESSURE LOCKOUT | SP | B703_BCUApplication$USER1$ST$SPS1 | stVal | √ | √
29 |  |  |  | 89A POLE DESCREPENCY | SP | B703_BCUApplication$USER3$ST$SPS3 | stVal | √ | √
30 |  |  |  | 89B POLE DESCREPENCY | SP | B703_BCUApplication$USER3$ST$SPS4 | stVal | √ | √
31 |  |  |  | CB DC SUPPLY-1/2 FAIL | SP | B703_BCUApplication$USER3$ST$SPS1 | stVal | √
32 |  |  |  | CB SPRING CHARGED | SP | B703_BCUApplication$USER3$ST$SPS2 | stVal | √
33 |  |  |  | CB SF6 GAS PRESSURE LOCKOUT | SP | B703_BCUApplication$USER3$ST$SPS | stVal | √ | √
34 |  |  |  | EMERGENCY/MANUAL CB TRIP | SP | B703_BCUApplication$USER6$ST$SPS | stVal | √ | √
35 |  |  |  | MAIN TANK HIGH LEVEL ALARM B-PH | SP | B703_BCUApplication$USER6$ST$SPS15 | stVal | √ | √
36 |  |  |  | MAIN TANK HIGH LEVEL ALARM R-PH | SP | B703_BCUApplication$USER6$ST$SPS5 | stVal | √ | √
37 |  |  |  | MAIN TANK HIGH LEVEL ALARM Y-PH | SP | B703_BCUApplication$USER6$ST$SPS10 | stVal | √ | √
38 |  |  |  | MAIN TANK LOW LEVEL ALARM B-PH | SP | B703_BCUApplication$USER6$ST$SPS14 | stVal | √ | √
39 |  |  |  | MAIN TANK LOW LEVEL ALARM R-PH | SP | B703_BCUApplication$USER6$ST$SPS4 | stVal | √ | √
40 | 765kV | 765kV BUS REACTOR | BCU | MAIN TANK LOW LEVEL ALARM Y-PH | SP | B703_BCUApplication$USER6$ST$SPS9 | stVal | √ | √
41 |  |  |  | OTI ALARM B-PH | SP | B703_BCUApplication$USER6$ST$SPS13 | stVal | √ | √
42 |  |  |  | OTI ALARM R-PH | SP | B703_BCUApplication$USER6$ST$SPS3 | stVal | √ | √
43 |  |  |  | OTI ALARM Y-PH | SP | B703_BCUApplication$USER6$ST$SPS8 | stVal | √ | √
44 |  |  |  | PSD DEVICE HEALTHY | SP | B703_BCUApplication$USER6$ST$SPS19 | stVal | √
45 |  |  |  | PSD DEVICE IN SERVICE | SP | B703_BCUApplication$USER6$ST$SPS20 | stVal | √
46 |  |  |  | PSD ALARM | SP | B703_BCUApplication$USER6$ST$SPS21 | stVal | √ | √
47 |  |  |  | PSD SYNCH DATA ERROR | SP | B703_BCUApplication$USER6$ST$SPS22 | stVal | √ | √
48 |  |  |  | SURGE ARRESTER B-PH | SP | B703_BCUApplication$USER6$ST$SPS18 | stVal | √
49 |  |  |  | SURGE ARRESTER R-PH | SP | B703_BCUApplication$USER6$ST$SPS16 | stVal | √
50 |  |  |  | SURGE ARRESTER Y-PH | SP | B703_BCUApplication$USER6$ST$SPS17 | stVal | √
51 |  |  |  | WTI ALARM B-PH | SP | B703_BCUApplication$USER6$ST$SPS12 | stVal | √ | √
52 |  |  |  | WTI ALARM R-PH | SP | B703_BCUApplication$USER6$ST$SPS2 | stVal | √ | √
53 |  |  |  | WTI ALARM Y-PH | SP | B703_BCUApplication$USER6$ST$SPS7 | stVal | √ | √
54 |  |  |  | 86A TRIP RELAY SUPERVISION | SP | B703_BCUApplication$USER5$ST$SPS2 | stVal | √ | √
55 |  |  |  | 86A TRIP RELAY OPERATED | SP | B703_BCUApplication$USER5$ST$SPS1 | stVal | √ | √
56 |  |  |  | 86B TRIP RELAY SUPERVISION | SP | B703_BCUApplication$USER5$ST$SPS5 | stVal | √ | √
57 |  |  |  | 86B TRIP RELAY OPERATED | SP | B703_BCUApplication$USER5$ST$SPS4 | stVal | √ | √
58 |  |  |  | CB TC-1 R-PHASE FAULTY | SP | B703_BCUApplication$USER5$ST$SPS | stVal | √ | √
59 |  |  |  | CB TC-1 Y-PHASE FAULTY | SP |  | stVal | √ | √
60 |  |  |  | CB TC-1 B-PHASE FAULTY | SP |  | stVal | √ | √
61 |  |  |  | CB TC-2 R-PHASE FAULTY | SP | B703_BCUApplication$USER5$ST$SPS3 | stVal | √ | √
62 |  |  |  | CB TC-2 Y-PHASE FAULTY | SP |  | stVal | √ | √
63 |  |  |  | CB TC-2 B-PHASE FAULTY | SP |  | stVal | √ | √
64 |  |  |  | CB POLE DISCREPANCY | SP | B703_BCUApplication$USER2$ST$SPS1 | stVal | √ | √
65 |  |  |  | CB SF6 GAS PRESSURE REFILL LOW ALARM | SP | B703_BCUApplication$USER2$ST$SPS | stVal | √ | √ | repeated
66 |  |  |  | BUS-1 VT RESET | SP | B703_BCUApplication$USER7$ST$SPS1 | stVal | √
67 |  |  |  | BUS-2 VT RESET | SP | B703_BCUApplication$USER7$ST$SPS3 | stVal | √
68 |  |  |  | LINE VT RESET | SP | B703_BCUApplication$USER7$ST$SPS5 | stVal | √
69 |  |  |  | BUS-1 VT SELECTED | SP | B703_BCUApplication$USER7$ST$SPS | stVal | √
70 |  |  |  | BUS-2 VT SELECTED | SP | B703_BCUApplication$USER7$ST$SPS2 | stVal | √
71 |  |  |  | ICT LV VT SELECTED | SP | B703_BCUApplication$USER7$ST$SPS4 | stVal | √
72 |  |  |  | CB READY | SP | B703_BCUCB$XCBR1$ST$Rdy | stVal | √
73 |  |  |  | CB POSITION NO SYNC | SP | B703_BCUCB$CSWI1$ST$Pos | noSync | √
74 |  |  |  | DEVICE HEALTHY | SP | B703_BCUApplication$LPHD0$ST$PhyHealth:0 | stVal:1 | √
75 |  |  |  | S89RE2 OPEN INTERLOCK |  |  |  | √
76 |  |  |  | 64R.2R RELAY FAIL |  |  |  | √ | √
77 |  |  |  | 64R.2Y RELAY FAIL |  |  |  | √ | √
78 |  |  |  | 64R.2B RELAY FAIL |  |  |  | √ | √
79 |  |  |  | PSD SELECTOR SWITCH IN |  |  |  | √ | √
80 |  |  |  | PSD SELECTOR SWITCH OUT |  |  |  | √ | √
81 |  |  |  | 64R.2S relay Unhealthy |  |  |  | √ | √
82 |  |  |  | 87R.1 relay Unhealthy |  |  |  | √ | √
83 |  |  |  | 21R.1 relay Unhealthy |  |  |  | √
84 |  |  |  | Manual close |  |  |  | √
85 |  |  |  | CB CLOSE INTERLOCK | SP | B703_BCUCB$CILO1$ST$EnaCls | stVal | √
86 |  |  |  | 89AE1 OPEN INTERLOCK | SP | B703_BCU89AE1$CILO3$ST$EnaOpn | stVal | √
87 | 765kV | 765kV BUS REACTOR | BCU | 89AE2 OPEN INTERLOCK | SP | B703_BCU89AE2$CILO6$ST$EnaOpn | stVal | √
88 |  |  |  | 89BE1 OPEN INTERLOCK | SP | B703_BCU89BE1$CILO5$ST$EnaOpn | stVal | √
89 |  |  |  | 89BE2 OPEN INTERLOCK | SP | B703_BCU89BE2$CILO7$ST$EnaOpn | stVal | √
90 |  |  |  | 89RE-B-PH OPEN INTERLOCK | SP | B703_BCU89REB$CILO9$ST$EnaOpn | stVal | √
91 |  |  |  | 89RE-R-PH OPEN INTERLOCK | SP | B703_BCU89RER$CILO9$ST$EnaOpn | stVal | √
92 |  |  |  | 89RE-Y-PH OPEN INTERLOCK | SP | B703_BCU89REY$CILO9$ST$EnaOpn | stVal | √
93 |  |  |  | 89A OPEN INTERLOCK | SP | B703_BCU89A$CILO2$ST$EnaOpn | stVal | √
94 |  |  |  | 89B OPEN INTERLOCK | SP | B703_BCU89B$CILO4$ST$EnaOpn | stVal | √
95 |  |  |  | 89R-B-PH OPEN INTERLOCK | SP | B703_BCU89RB$CILO8$ST$EnaOpn | stVal | √
96 |  |  |  | 89R-R-PH OPEN INTERLOCK | SP | B703_BCU89RR$CILO8$ST$EnaOpn | stVal | √
97 |  |  |  | 89R-Y-PH OPEN INTERLOCK | SP | B703_BCU89RY$CILO8$ST$EnaOpn | stVal | √
98 |  |  |  | RELAY IN TEST MODE |  |  |  | √ | √
99 |  |  |  | SETTINGS CHANGED |  |  |  | √ | √
100 |  |  |  | REACTOR-n R PH OUT OF SERVICE |  |  |  | √
101 |  |  |  | REACTOR-n Y PH OUT OF SERVICE |  |  |  | √
102 |  |  |  | REACTOR-n B PH OUT OF SERVICE |  |  |  | √
103 |  |  |  | REACTOR SPARE PH IN SERVICE IN REACTOR-N |  |  |  | √
104 |  |  |  | CB MANUAL TRIP |  |  |  | √
105 |  |  |  | CB MANUAL CLOSE |  |  |  | √
106 |  |  |  | BUSBAR OPERATED |  |  |  | √ | √
107 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B703_BCUApplication$USER7$ST$SPS6 | stVal | √ | √
108 |  |  |  | MEASUREMENT
109
110 |  |  |  | POWER FACTOR | ME_FL | B703_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotPF:1 | mag$f
111 |  |  |  | FREQUENCY | ME_FL | B703_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$Hz:1 | mag$f
112 |  |  |  | ACTIVE POWER | ME_FL | B703_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotW:1 | mag$f
113 |  |  |  | REACTIVE POWER | ME_FL | B703_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVAr:1 | mag$f
114 |  |  |  | APPARENT POWER | ME_FL | B703_BCUVI3p1_OperationalValues$PPRE_MMXU1$MX$TotVA:1 | mag$f
115 |  |  |  | I-R-PH CURRENT | ME_FL | B703_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsA$cVal$mag$f
116 |  |  |  | I-Y-PH CURRENT | ME_FL | B703_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsB$cVal$mag$f
117 |  |  |  | I-B-PH CURRENT | ME_FL | B703_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$A:1 | phsC$cVal$mag$f
118 |  |  |  | R-Y VOLTAGE | ME_FL | B703_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsAB$cVal$mag$f
119 |  |  |  | Y-B VOLTAGE | ME_FL | B703_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsBC$cVal$mag$f
120 |  |  |  | B-R VOLYAGE | ME_FL | B703_BCUVI3p1_OperationalValues$RPRE_MMXU1$MX$PPV:1 | phsCA$cVal$mag$f
121
122 |  |  |  | CB-B-PH COUNTER | ME_I | B703_BCUCBB$XCBR1$ST$OpCnt | stVal
123 |  |  |  | CB-R-PH COUNTER | ME_I | B703_BCUCBR$XCBR1$ST$OpCnt | stVal
124 |  |  |  | CB-Y-PH COUNTER | ME_I | B703_BCUCBY$XCBR1$ST$OpCnt | stVal
125
126 |  |  |  | COMMANDS
127
128 |  |  |  | 89R-Y CONTROL | DC | B703_BCU89RY$CSWI8$CO$Pos:8 | Oper$ctlVal | √
129 |  |  |  | 89R-R CONTROL | DC | B703_BCU89RR$CSWI8$CO$Pos:8 | Oper$ctlVal | √
130 |  |  |  | 89R-B CONTROL | DC | B703_BCU89RB$CSWI8$CO$Pos:8 | Oper$ctlVal | √
131 |  |  |  | 89B CONTROL | DC | B703_BCU89B$CSWI4$CO$Pos:8 | Oper$ctlVal | √
132 |  |  |  | 89A CONTROL | DC | B703_BCU89A$CSWI2$CO$Pos:8 | Oper$ctlVal | √
133 |  |  |  | 89RE-Y CONTROL | DC | B703_BCU89REY$CSWI9$CO$Pos:8 | Oper$ctlVal | √
134 |  |  |  | 89RE-R CONTROL | DC | B703_BCU89RER$CSWI9$CO$Pos:8 | Oper$ctlVal | √
135 |  |  |  | 89RE-B CONTROL | DC | B703_BCU89REB$CSWI9$CO$Pos:8 | Oper$ctlVal | √
136 |  |  |  | 89BE2 CONTROL | DC | B703_BCU89BE2$CSWI7$CO$Pos:8 | Oper$ctlVal | √
137 |  |  |  | 89BE1 CONTROL | DC | B703_BCU89BE1$CSWI5$CO$Pos:8 | Oper$ctlVal | √
138 |  |  |  | 89AE2 CONTROL | DC | B703_BCU89AE2$CSWI6$CO$Pos:8 | Oper$ctlVal | √
139 |  |  |  | 89AE1 CONTROL | DC | B703_BCU89AE1$CSWI3$CO$Pos:8 | Oper$ctlVal | √
140 |  |  |  | CB CONTROL | DC | B703_BCUCB$CSWI1$CO$Pos:8 | Oper$ctlVal | √
141 |  |  |  | CB CONTROL NO SYNC | SC | B703_BCUCB$CSWI1$CO$Pos | Oper$noSync | √
142 |  |  |  | 86B TRIP RELAY RESET COMMAND | SC | B703_BCUApplication$USER2$CO$SPC1:8 | Oper$ctlVal | √
143 |  |  |  | 86A TRIP RELAY RESET COMMAND | SC | B703_BCUApplication$USER2$CO$SPC:8 | Oper$ctlVal | √
Note: 1. All the switchgear status signals as per the actual primary equipment status. 2. Additional signal for CB Trouble, etc as per scheme 3. 10 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 4. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 5. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 64R_ R_PH_7SJ802
765kV BUS REACTOR (7SJ80)- 64R-R-PH
Sr. No. | Voltage Level | Feeder Name | Source
Signal Decription
|  |  |  | NAME ( BAY-703 BUS REACTOR ) | INFORMATION TYPE | Telegram Address | POSITION | Event | Alarm
BINARY INPUT (Single Point)
1 | 765kV | 765kV BUS REACTOR | 7SJ80 | MAIN CB OPEN | SP | B703_64R_RphCTRL$GGIO1$ST$SPCSO1:0 | stVal | √
2 |  |  |  | TIE CB OPEN | SP | B703_64R_RphCTRL$GGIO1$ST$SPCSO2:0 | stVal | √
3 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B703_64R_RphCTRL$GGIO1$ST$SPCSO7:0 | stVal | √ | √
4 |  |  |  | OTI TRIP R-PH | SP | B703_64R_RphCTRL$GGIO1$ST$SPCSO4:0 | stVal | √ | √
5 |  |  |  | WTI TRIP R-PH | SP | B703_64R_RphCTRL$GGIO1$ST$SPCSO6:0 | stVal | √ | √
6 |  |  |  | PRV-1, 2 & 3 TRIP R-PH | SP | B703_64R_RphCTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
7 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B703_64R_RphEXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
8 |  |  |  | REF STAGE 1 TRIP | SP | B703_64R_RphPROT$PTOC16$ST$Op | general | √ | √
9 |  |  |  | REF STAGE 1 PICKUP | SP | B703_64R_RphPROT$PTOC16$ST$Str | general | √
10 |  |  |  | REF STAGE 2 TRIP | SP | B703_64R_RphPROT$PTOC17$ST$Op | general | √ | √
11 |  |  |  | REF STAGE 2 PICKUP | SP | B703_64R_RphPROT$PTOC17$ST$Str | general | √
12 |  |  |  | GENERAL TRIP | SP | B703_64R_RphPROT$PTRC1$ST$Tr | general | √ | √
13 |  |  |  | GENERAL PICKUP | SP | B703_64R_RphPROT$PTRC1$ST$Str | general | √
14 |  |  |  | MAIN TANK BUCHHOLZ-1&2 ALARM R-PH | SP | B703_64R_RphCTRL$GGIO1$ST$SPCSO5:0 | stVal | √ | √
15 |  |  |  | DEVICE HEALTHY | SP | B703_64R_RphPROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
16 |  |  |  | SETTINGS CHANGED |  |  |  | √
17 |  |  |  | RELAY IN TEST MODE |  |  |  | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 64R_ Y_PH_7SJ802
765kV BUS REACTOR (7SJ80)- 64R-Y-PH
Sr. No. | Voltage Level | Feeder Name | Source
Signal Decription
|  |  |  | NAME ( BAY-703 BUS REACTOR ) | INFORMATION TYPE | Telegram Address | POSITION | Event | Alarm
BINARY INPUT (Single Point)
1 | 765kV | 765kV BUS REACTOR | 7SJ80 | 21R RELAY UNHEALTHY | SP | B703_64R_YphCTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
2 |  |  |  | 87R RELAY UNHEALTHY | SP | B703_64R_YphCTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
3 |  |  |  | BCU UNHEALTHY | SP | B703_64R_YphCTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
4 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B703_64R_YphCTRL$GGIO1$ST$SPCSO4:0 | stVal | √ | √
5 |  |  |  | OTI TRIP Y-PH | SP | B703_64R_YphCTRL$GGIO1$ST$SPCSO6:0 | stVal | √ | √
6 |  |  |  | PRV-1, 2 & 3 TRIP Y-PH | SP | B703_64R_YphCTRL$GGIO1$ST$SPCSO5:0 | stVal | √ | √
7 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B703_64R_YphEXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
8 |  |  |  | REF STAGE 1 TRIP | SP | B703_64R_YphPROT$PTOC16$ST$Op | general | √ | √
9 |  |  |  | REF STAGE 1 PICKUP | SP | B703_64R_YphPROT$PTOC16$ST$Str | general | √
10 |  |  |  | REF STAGE 2 TRIP | SP | B703_64R_YphPROT$PTOC17$ST$Op | general | √ | √
11 |  |  |  | REF STAGE 2 PICKUP | SP | B703_64R_YphPROT$PTOC17$ST$Str | general | √
12 |  |  |  | GENERAL TRIP | SP | B703_64R_YphPROT$PTRC1$ST$Tr | general | √ | √
13 |  |  |  | GENERAL PICKUP | SP | B703_64R_YphPROT$PTRC1$ST$Str | general | √
14 |  |  |  | MAIN TANK BUCHHOLZ-1&2 ALARM Y-PH | SP | B703_64R_YphCTRL$GGIO1$ST$SPCSO7:0 | stVal | √ | √
15 |  |  |  | DEVICE HEALTHY | SP | B703_64R_YphPROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
16 |  |  |  | SETTINGS CHANGED |  |  |  | √
17 |  |  |  | RELAY IN TEST MODE |  |  |  | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 64R_ B_PH_7SJ802
765kV BUS REACTOR (7SJ80)- 64R-B-PH
Sr. No. | Voltage Level | Feeder Name | Source
Signal Decription
|  |  |  | NAME ( BAY-703 BUS REACTOR ) | INFORMATION TYPE | Telegram Address | POSITION | Event | Alarm
BINARY INPUT (Single Point)
1 | 765kV | 765kV BUS REACTOR | 7SJ80 | GOOSE RECEIPT FAIL/TROUBLE | SP | B703_64R_BphCTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
2 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B703_64R_BphEXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
3 |  |  |  | REF STAGE 1 TRIP | SP | B703_64R_BphPROT$PTOC16$ST$Op | general | √ | √
4 |  |  |  | REF STAGE 1 PICKUP | SP | B703_64R_BphPROT$PTOC16$ST$Str | general | √
5 |  |  |  | REF STAGE 2 TRIP | SP | B703_64R_BphPROT$PTOC17$ST$Op | general | √ | √
6 |  |  |  | REF STAGE 2 PICKUP | SP | B703_64R_BphPROT$PTOC17$ST$Str | general | √
7 |  |  |  | GENERAL TRIP | SP | B703_64R_BphPROT$PTRC1$ST$Tr | general | √ | √
8 |  |  |  | OTI TRIP B-PH | SP | B703_64R_BphCTRL$GGIO1$ST$SPCSO6:0 | stVal | √ | √
9 |  |  |  | PRV-1,2 & 3 TRIP B-PH | SP | B703_64R_BphCTRL$GGIO1$ST$SPCSO5:0 | stVal | √ | √
10 |  |  |  | DEVICE HEALTHY | SP | B703_64R_BphPROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
11 |  |  |  | MAIN TANK BUCHHOLZ-1&2 ALARM B-PH | SP | B703_64R_BphCTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
12 |  |  |  | MAIN TANK BUCHHOLZ-1&2 TRIP SP-PH | SP | B703_64R_BphCTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
13 |  |  |  | NGR THERMAL OVERLOAD TRIP | SP | B703_64R_BphPROT$PTTR1$ST$OP | stVal | √ | √
14 |  |  |  | 87R RELAY UNHEALTHY | SP | B703_64R_YphCTRL$GGIO1$ST$SPCSO7:0 | stVal | √ | √
15 |  |  |  | GENERAL PICKUP | SP | B703_64R_BphPROT$PTRC1$ST$Str | general | √
16 |  |  |  | SETTINGS CHANGED |  |  |  | √
17 |  |  |  | RELAY IN TEST MODE |  |  |  | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 64R_ SP_PH_7SJ802
765kV BUS REACTOR (7SJ80)- 64R-SP-PH
Sr. No. | Voltage Level | Feeder Name | Source
Signal Decription
|  |  |  | NAME ( BAY-703 BUS REACTOR ) | INFORMATION TYPE | Telegram Address | POSITION | Event | Alarm
BINARY INPUT (Single Point)
1 | 765kV | 765kV BUS REACTOR | 7SJ80 | GOOSE RECEIPT FAIL/TROUBLE | SP | B703_64R_SPCTRL$GGIO1$ST$SPCSO4:0 | stVal | √ | √
2 |  |  |  | OTI TRIP SP-PH | SP | B703_64R_SPCTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
3 |  |  |  | MAIN TANK BUCHHOLZ-1&2 ALARM SP-PH |  | B703_64R_SPCTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
4 |  |  |  | PRV-1, 2 & 3 TRIP SP-PH | SP | B703_64R_SPCTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
5 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B703_64R_SPEXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
6 |  |  |  | REF STAGE 1 TRIP | SP | B703_64R_SPPROT$PTOC16$ST$Op | general | √ | √
7 |  |  |  | REF STAGE 1 PICKUP | SP | B703_64R_SPPROT$PTOC16$ST$Str | general | √
8 |  |  |  | REF STAGE 2 TRIP | SP | B703_64R_SPPROT$PTOC17$ST$Op | general | √ | √
9 |  |  |  | REF STAGE 2 PICKUP | SP | B703_64R_SPPROT$PTOC17$ST$Str | general | √
10 |  |  |  | GENERAL TRIP | SP | B703_64R_SPPROT$PTRC1$ST$Tr | general | √ | √
11 |  |  |  | GENERAL PICKUP | SP | B703_64R_SPPROT$PTRC1$ST$Str | general | √
12 |  |  |  | DEVICE HEALTHY | SP | B703_64R_SPPROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
13 |  |  |  | SETTINGS CHANGED |  |  |  | √
14 |  |  |  | RELAY IN TEST MODE |  |  |  | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 21R_1_7SA522
765kV BUS REACTOR (7SA522)
Sr. No. | Voltage Level | Feeder Name | Source
Signal Decription
|  |  |  | NAME ( BAY-703 BUS REACTOR ) | INFORMATION TYPE | Telegram Address | POSITION | Event | Alarm
BINARY INPUT (Single Point)
1 | 765kV | 765kV BUS REACTOR | 7SA522 | GOOSE RECEIPT FAIL/TROUBLE | SP | B703_21R_1CTRL$GGIO1$ST$SPCSO1:0 | stVal | √ | √
2 |  |  |  | WTI TRIP B-PH | SP | B703_21R_1CTRL$GGIO1$ST$SPCSO4:0 | stVal | √ | √
3 |  |  |  | WTI TRIP Y-PH | SP | B703_21R_1CTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
4 |  |  |  | 64.2-R_Y_B SP RELAY UNHEALTHY | SP | B703_21R_1CTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
5 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B703_21R_1EXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
6 |  |  |  | BACKUP IMPEDENCE ZONE-1 START | SP | B703_21R_1PROT$PDIS1$ST$Str | general | √
7 |  |  |  | BACKUP IMPEDENCE ZONE-1 TRIP | SP | B703_21R_1PROT$PDIS1$ST$Op | general | √ | √
8 |  |  |  | BACKUP IMPEDENCE R-PH TRIP | SP | B703_21R_1PROT$PDIS1$ST$Op | phsA | √ | √
9 |  |  |  | BACKUP IMPEDENCE Y-PH TRIP | SP | B703_21R_1PROT$PDIS1$ST$Op | phsB | √ | √
10 |  |  |  | BACKUP IMPEDENCE B-PH TRIP | SP | B703_21R_1PROT$PDIS1$ST$Op | phsC | √ | √
11 |  |  |  | BACKUP IMPEDENCE BLOCKED | SP | B703_21R_1PROT$PDIS1$ST$Blk | stVal | √
12 |  |  |  | GENERAL TRIP | SP | B703_21R_1PROT$PTRC1$ST$Tr | general | √ | √
13 |  |  |  | NON-DIRECTIONAL OVERCURRENT TRIP | SP | B703_21R_1PROT$PTOC2$ST$Op | general | √ | √
14 |  |  |  | NON-DIRECTIONAL OVERCURRENT START | SP | B703_21R_1PROT$PTOC2$ST$Str | general | √
15 |  |  |  | DEVICE HEALTHY | SP | B703_21R_1PROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
16 |  |  |  | NO VOLTAGE IN LINE | SP | B703_21R_1EXT$pdGGIO3$ST$SPCSO40:0 | stVal | √ | √
17 |  |  |  | VT FUSE FAILURE | SP | B703_21R_1EXT$pdGGIO3$ST$SPCSO42:0 | stVal | √ | √
18 |  |  |  | SETTINGS CHANGED |  |  |  | √ | √
19 |  |  |  | RELAY IN TEST MODE |  |  |  | √ | √
20 |  |  |  | NON-DIRECTIONAL EARTHFAULT TRIP |  |  |  | √ | √
21 |  |  |  | NON-DIRECTIONAL EARTHFAULT START |  |  |  | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.

## 87_1_7UT613
765kV BUS REACTOR (7UT613)
Sr. No. | Voltage Level | Feeder Name | Source
Signal Decription
|  |  |  | NAME ( BAY-703 BUS REACTOR ) | INFORMATION TYPE | Telegram Address | POSITION | Event | Alarm
BINARY INPUT (Single Point)
1 |  |  |  | GOOSE RECEIPT FAIL/TROUBLE | SP | B703_87_1CTRL$GGIO1$ST$SPCSO5:0 | stVal | √ | √
2 |  |  |  | MAIN TANK BUCHHOLZ-1 TRIP B-PH | SP | B703_87_1CTRL$GGIO1$ST$SPCSO3:0 | stVal | √ | √
3 |  |  |  | MAIN TANK BUCHHOLZ-1 TRIP R-PH | SP | B703_87_1CTRL$GGIO1$ST$SPCSO4:0 | stVal | √ | √
4 |  |  |  | MAIN TANK BUCHHOLZ-1TRIP Y-PH | SP | B703_87_1CTRL$GGIO1$ST$SPCSO2:0 | stVal | √ | √
5 |  |  |  | REACTOR CB OPEN | SP | B703_87_1CTRL$GGIO1$ST$SPCSO1:0 | stVal | √
6 |  |  |  | WTI R-PH TRIP | SP
7 |  |  |  | WTI Y-PH TRIP | SP
8 |  |  |  | WTI B-PH TRIP | SP
9 |  |  |  | PRESSURE RELIF VALVE-2 TRIP R-PH | SP
10 |  |  |  | PRESSURE RELIF VALVE-2 TRIP Y-PH | SP
11 |  |  |  | PRESSURE RELIF VALVE-2 TRIP B-PH | SP
12 |  |  |  | BUCHHOLZ-1 SP PH TRIP | SP
13 |  |  |  | WTI SP PH TRIP | SP
14 |  |  |  | PRESSURE RELIF VALVE-2 SP PH TRIP | SP
15 |  |  |  | TIME SYNCHRONISATION ERROR | SP | B703_87_1EXT$pdGGIO2$ST$SPCSO4:0 | stVal | √ | √
16 |  |  |  | DIFFERENTIAL TRIP R-PH | SP | B703_87_1EXT$pdGGIO89$ST$SPCSO40:0 | stVal | √ | √
17 |  |  |  | DIFFERENTIAL TRIP Y-PH | SP | B703_87_1EXT$pdGGIO89$ST$SPCSO41:0 | stVal | √ | √
18 |  |  |  | DIFFERENTIAL TRIP B-PH | SP | B703_87_1EXT$pdGGIO89$ST$SPCSO42:0 | stVal | √ | √
19 |  |  |  | DIFFERENTIAL STAGE 1 TRIP | SP | B703_87_1PROT$PDIF1$ST$Op | general | √ | √
20 |  |  |  | DIFFERENTIAL STAGE 1 PICKUP | SP | B703_87_1PROT$PDIF1$ST$Str | general | √
21 |  |  |  | DIFFERENTIAL STAGE 2 TRIP | SP | B703_87_1PROT$PDIF2$ST$Op | general | √ | √
22 |  |  |  | DIFFERENTIAL STAGE 2 PICKUP | SP | B703_87_1PROT$PDIF2$ST$Str | general | √
23 |  |  |  | 21R RELAY UNHEALTHY
24 |  |  |  | GENERAL TRIP | SP | B703_87_1PROT$PTRC1$ST$Tr | general | √ | √
25 |  |  |  | DEVICE HEALTHY | SP | B703_87_1PROT$LPHD1$ST$PhyHealth:0 | stVal:1 | √
16 |  |  |  | SETTINGS CHANGED |  |  |  | √
17 |  |  |  | RELAY IN TEST MODE |  |  |  | √
Note: 1. Additional signal for CB Trouble, etc as per scheme & As per standard DR signal requirement the input not considered in HMI signal list 2. 5 Nos of GGIO signal need to be configured as SPARE till the SCADA Database 3. The Logical Device LD is for reference only and vendors may use the same as per their own stndardized way, however the logical nodes used are to be used only as specified. 4. If the logical nodes have been made more specific under the same logical node class by adding prefixes, same can be used as per the application. For example, PDIFF has been specified for all types of differential functions, but if some vendor, under the same logical node class, made the function more specific by adding prefix HZD1PDIFF for 1 phase High Impedance Differential function & T3WPDIFF for 3 winding Low Impedance differential protection, same may be used.