## Slide 1: Ethernet Network switch Configuration

## Slide 2: MAGNUM 6k 25 Fiber switch
Login into the Switch Through INETRNET EXPLORER by entering IP Address as shown in figure:-
Go to “system“ Enter IP Address & subnet mask & select boot mode as manual.
Mac address ands serial no. of switch Can be seen here.

## Slide 3
Under “ Bridge RSTP” Option select protocol as Normal RSTP & enable RSTP.
Set the priority as per the requirement. For root switch the priority will be 0(Maximum) and for 2nd Backup root switch the priority should be one step lower (ex.4096). For All other switch in the network, priority maybe kept same or One step further Lower (Ex. 8192).
Note: Inside the network, there can be a single “root switch” whose selection is done automatically by RSTP, based on Bridge priority. If the bridge priority is same, then selection is done on Lowest Mac address calculation.
Standard hello timer-2 sec., forward delay- 15 sec., Root max age- 20 sec.
Root port mac address can be seen here in “Designated root”.

## Slide 4
Under “Port RSTP” option, we can set the Port wise RSTP configuration.
We can enable/disable or can put the port in “Auto” for edge /P2P setting of the port.
For ex. RSTP works on P2P ports only (Only those port which are directly connected to ring, or RSTP speaking devices , we can say “switch to switch port”).
Edge port is only for Host/Hub IED’S (BCU/Relay, Non RSTP speaking switch). These port do not Participate in RSTP.
However, we can enable RSTP on these ports and set the Port properties (edge or P2P).
If edge and p2p port setting kept as auto , switch will automatically detect the neighbor switch by sending the BPDU On all the ports.

## Slide 5
RSTP setting on Ring formation ports.
RSTP setting on Host/hub ports/Where IED’s are connected.
Port no. | Enable/Disable | Edge Port | Point to Point
 | Enable | False/auto | True
Port no. | Enable/Disable | Edge Port | Point to Point
 | Enable | True | False/Auto

## Slide 7
Significance of Path Cost- There is always a cost associated bw link based on the medium of connection.
Inside the Network, Cost can be calculated in 2 ways:
1)Short method (STP-16 Bit Style)- The IEEE 802.1D specification assigns 16-bit (short) default port cost values to each port that is based on bandwidth.
2) Long method (RSTP-32 Bit style)- 802.1assigns 32-bit (long) default port cost values to each port using a formula that is based on the port bandwidth. The formula for obtaining default 32-bit port costs is to divide the bandwidth of the port by 200,000,000.
Port Speed | Default Cost Value
10 Mbps | 100
100 Mbps | 19
1 Gbps | 4
Port Speed | Default Cost Value
10 Mbps | 2000000
10 Mbps | 200000
100 Mbps | 20000
1 Gbps | 2000

## Slide 8
SNTP configuration for Time Synchronization.
Main SNTP server Ip address (GPS) & Secondary SNTP Server (Aux. BCU) should be entered here.

## Slide 9
Link layer discovery Protocol: LLDP enables a device to advertise its identification, configuration, and capabilities to neighboring devices. Under this protocol neighbor switch MAC address and their port no. can be seen (Which are directly connected to switch.)
LLDP State should be enabled.
Under “LLDP Port” we can set the LLDP Configuration on individual port
In Port status select -Tx and Rx. Management address- Enable
TLV (type-length-value) parameters – select All those parameter which is required to be transmitted from Device .(Ex. System description (SD), (PD)Port Description, (SN)System name, System Capabilities (SC).