Configuration Procedure for Ethernet Switches

Corporate Asset Management

Power Grid Corporation of India Ltd.

| Sl.No. | Pages | Revision | Remarks |
| --- | --- | --- | --- |
| 01 | All Pages | Rev_00 | Initial Release |

INDEX

| S.No | Topic | Page No. |
| --- | --- | --- |
| A | Procedure for Configuration of each Root Bridge/Switch | 03 |
| B | Procedure for Configuration of each Non-Root Bridge/Switch | 04 |
| C | Typical Configuration of Ethernet switches | 06 |

- Procedure for Configuration of each Root Bridge/Switch:

  - Unique IP address, subnet mask and SNTP to be configured.

  - RSTP (Rapid Spanning Tree Protocol) to be enabled only on Ring connected Ports.

  - RSTP protocol to be disabled on ports connected to end-user devices (e.g., computers, IP phones, etc.). These ports do not Participate in RSTP.

  - All the RSTP enabled ports should be configured as designated/forwarding ports only. Designated ports are responsible for forwarding traffic towards the root switch.

  - Settings for network connected Ports is to be kept as:

    - RSTP- Enabled

    - Edge Port – Auto.

    - Point to point - True.

  - Ports connected to end-user devices (e.g., computers, IP phones, etc.) must have following settings:

    - RSTP- Disabled

    - Edge Port – True.

    - Point to point- Auto.

  - Ports which are not used anywhere, must have (Labeling to be Provided for Disabled Ports):

    - RSTP- Disabled

    - Edge Port – Disabled.

    - Point to point- Auto.

  - Bridge priority of the:

    - Root Switch to be kept as: 0

    - 2nd Back-up root switch to be kept as: 4096 (one step lower)

  - Link Layer Discovery Protocol (LLDP) must be enabled.

- Procedure for Configuration of each Non-Root Bridge/Switch:

- Unique IP address, subnet mask and SNTP to be configured.

- RSTP (Rapid Spanning Tree Protocol) to be enabled only on Ring connected Ports.

- RSTP protocol to be disabled on Edge ports. As an Edge port is only for Host/Hub IED’S (BCU/Relay, Non RSTP speaking switch). These ports do not Participate in RSTP.

- Following configuration of RSTP enabled ports is to be done based on type of network ring:

  - For Dual-Ring system:

    - Total 04 (Four) no. ports must be enabled for RSTP, of which:

      - 02 no. ports to be configured as forward designated port.

      - 01 no. as discard alternate.

      - The remaining 01 no. as Root port.

  - For Single-Ring system

    - Only 02 (Two) no. ports must be enabled for RSTP.

- Settings for these 4 Ports is to be kept as:

  - RSTP- Enabled

  - Edge Port – Auto.

  - Point to point - True.

- Remaining ports, which are in use and connected to Host/IED must have following settings:

  - RSTP- Disabled

  - Edge Port – True.

  - Point to point- Auto.

- Ports which are not used anywhere, must have (Labeling to be Provided for Disabled Ports):

  - RSTP- Disabled.

  - Edge Port – Disabled.

  - Point to point- Auto.

- Bridge priority for all other switches (non-root switches) must be minimum one step lower than Back-up root switch (i.e. 8192 or lower).

- Link Layer Discovery Protocol (LLDP) must be enabled.

- Configuration procedure for Switches

      - Annexure – I - Hirchman Ethernet Network switch

      - Annexure – II - Magnum Ethernet Network switch

      - Annexure – III - Ruggedcom Ethernet Network switch