## AI_NEW (hidden)
Sl. | BAY NUM. | BAY NAME | DEVICE ID | SIGNAL DESCRIPTION | DATA TYPE | SCADA ID | REMARK
1 | BUS | BUS | BUS | VOLTAGE R-Y PHASE | AI | KVRY
2 | BUS |  | BUS | VOLTAGE Y-B PHASE | AI | KVYB
3 | BUS |  | BUS | VOLTAGE B-R PHASE | AI | KVBR
4 | BUS |  | BUS | FREQUENCY | AI | HZ
1 | ABC | LINE FEEDER | LINE | I (R-PHASE) | AI | IR
2 | ABC |  | LINE | I (Y-PHASE) | AI | IY
3 | ABC |  | LINE | I (B-PHASE) | AI | IB
4 | ABC |  | LINE | MW | AI | MW
5 | ABC |  | LINE | MVAR | AI | MX
6 | ABC |  | LINE | V (R-Y PHASE) | AI | KVRY
7 | ABC |  | LINE | V (Y-B PHASE) | AI | KVYB
8 | ABC |  | LINE | V (B-R PHASE) | AI | KVBR
9 | ABC |  | LINE | FREQUENCY | AI | HZ
10 | ABC |  | LINE | MAIN-1 FAULT IMPEDANCE | AI | FLZ1
11 | ABC |  | LINE | MAIN-1 FAULT DISTANCE | AI | FLD1
12 | ABC |  | LINE | MAIN-1 FAULT PERCENTAGE | AI | FLP1
13 | ABC |  | LINE | MAIN-2 FAULT IMPEDANCE | AI | FLZ2
14 | ABC |  | LINE | MAIN-2 FAULT DISTANCE | AI | FLD2
15 | ABC |  | LINE | MAIN-2 FAULT PERCENTAGE | AI | FLP2
1 | ABC | BUS REACTOR/ LINE REACTOR | RE | REACTOR I (R-PHASE) | AI | IR
2 | ABC |  | RE | REACTOR I (Y-PHASE) | AI | IY
3 | ABC |  | RE | REACTOR I (B-PHASE) | AI | IB
4 | ABC |  | RE | REACTOR MVAR | AI | MX
5 | ABC |  | RE | REACTOR V (R-Y PHASE) | AI | KVRY
6 | ABC |  | RE | REACTOR V (Y-B PHASE) | AI | KVYB
7 | ABC |  | RE | REACTOR V (B-R PHASE) | AI | KVBR
8 | ABC |  | RE | FREQUENCY | AI | HZ
9 | ABC |  | RE | WTI TEMP R PHASE | AI | WTI | ONLY ONE SIGNAL IN PLACE OF THREE SIGNALS APPLICABLE INDIVIDUALLY FOR R/Y/B PHASES TO BE CONSIDERED FOR 3 PHASE LINE REACTOR/ BUS REACTOR
12 | ABC |  | RE | OTI TEMP R PHASE | AI | OTI
15 | ABC |  | RE | DGA MOISTURE VALUE - R PHASE | AI | MOIS
16 | ABC |  | RE | DGA H2 VALUE - R PHASE | AI | DGH2
17 | ABC |  | RE | DGA C2H2 VALUE - R PHASE | AI | C2H2
18 | ABC |  | RE | DGA CO VALUE - R PHASE | AI | DGCO
19 | ABC |  | RE | DGA CO2 VALUE - R PHASE | AI | DCO2
20 | ABC |  | RE | DGA CH4 VALUE - R PHASE | AI | DCH4
21 | ABC |  | RE | DGA C2H6 VALUE - R PHASE | AI | C2H6
22 | ABC |  | RE | DGA C2H4 VALUE - R PHASE | AI | C2H4
23 | ABC |  | RE | DGA N2 VALUE - R PHASE | AI | DGO2
1 | ABC | TIE/ BUS COUPLER / BUS SECTION/TBC | TIE/ BC/ BS | I (R-PHASE) | AI | IR
2 | ABC |  | TIE/ BC/ BS | I (Y-PHASE) | AI | IY
3 | ABC |  | TIE/ BC/ BS | I (B-PHASE) | AI | IB
1 | ABC | ICT | XFMR_P | I (R-PHASE) | AI | IR
2 | ABC |  | XFMR_P | I (Y-PHASE) | AI | IY
3 | ABC |  | XFMR_P | I (B-PHASE) | AI | IB
4 | ABC |  | XFMR_P | MW | AI | MW
5 | ABC |  | XFMR_P | MVAR | AI | MX
6 | ABC |  | XFMR_P | V (R-Y PHASE) | AI | KVRY
7 | ABC |  | XFMR_P | V (Y-B PHASE) | AI | KVYB
8 | ABC |  | XFMR_P | V (B-R PHASE) | AI | KVBR
9 | ABC |  | XFMR_P | FREQUENCY | AI | HZ
10 | ABC |  | XFMR_P | HVWTI TEMP - R PHASE | AI | HVWT | ONLY ONE SIGNAL IN PLACE OF THREE SIGNALS APPLICABLE INDIVIDUALLY FOR R/Y/B PHASES TO BE CONSIDERED IN CASE OF 3-PHASE ICT
11 | ABC |  | XFMR_S | IVWTI TEMP - R PHASE | AI | IVWT
12 | ABC |  | XFMR_T | LVWTI TEMP - R PHASE | AI | LVWT
19 | ABC |  | XFMR_P | OTI TEMP R PHASE | AI | OTI
22 | ABC |  | XFMR_P | TAP POSITION INDICATOR - R PHASE | AI | TPI
25 | ABC |  | XFMR_P | DGA MOISTURE VALUE - R PHASE | AI | MOIS
26 | ABC |  | XFMR_P | DGA H2 VALUE - R PHASE | AI | DGH2
27 | ABC |  | XFMR_P | DGA C2H2 VALUE - R PHASE | AI | C2H2
28 | ABC |  | XFMR_P | DGA CO VALUE - R PHASE | AI | DGCO
29 | ABC |  | XFMR_P | DGA CO2 VALUE - R PHASE | AI | DCO2
30 | ABC |  | XFMR_P | DGA CH4 VALUE - R PHASE | AI | DCH4
31 | ABC |  | XFMR_P | DGA C2H6 VALUE - R PHASE | AI | C2H6
32 | ABC |  | XFMR_P | DGA C2H4 VALUE - R PHASE | AI | C2H4
33 | ABC |  | XFMR_P | DGA N2 VALUE | AI | DGO2
1 | 220VDC | DCDB | 220V_DCDB-1 | 220V DCDB -1 VOLTAGE | AI
2 | 220VDC |  | 220V_DCDB-1 | 220V BATTERY SET-1 CURRENT | AI
3 | 220VDC |  | 220V_DCDB-2 | 220V DCDB -2 VOLTAGE | AI
4 | 220VDC |  | 220V_DCDB-2 | 220V BATTERY SET-2 CURRENT | AI
5 | 48 VDC |  | 48V_DCDB-1 | 48V DCDB -1 VOLTAGE | AI
6 | 48 VDC |  | 48V_DCDB-1 | 48V BATTERY SET-1 CURRENT | AI
7 | 48 VDC |  | 48V_DCDB-2 | 48V DCDB -2 VOLTAGE | AI
8 | 48 VDC |  | 48V_DCDB-2 | 48V BATTERY SET-2 CURRENT | AI
9 | 220VDC | BCHRG | BATCHRG220V-1 | 220V BATTERY CHARGER-1 CURRENT | AI
10 | 220VDC |  | BATCHRG220V-2 | 220V BATTERY CHARGER-2 CURRENT | AI
11 | 48 VDC |  | BATCHRG48V-1 | 48V BATTERY CHARGER-1 CURRENT | AI
12 | 48 VDC |  | BATCHRG48V-2 | 48V BATTERY CHARGER-2 CURRENT | AI
13 | 415 V | FP | FIREPROTN | FIRE FIGHTING PRESSURE MONITORING | AI
14 | 415 V |  | DPUMP | DIESEL ENGINE BATTERY-1 VOLTAGE | AI
15 | 415 V |  | DPUMP | DIESEL ENGINE BATTERY-2 VOLTAGE | AI
19 | 415 V | AIRCON | G_KIOSK_1 | 765KV KIOSK-1 TEMP | AI
20 | 415 V |  | F_KIOSK_1 | 400KV KIOSK-1 TEMP | AI
21 | 415 V |  | TEMP_MON | CONTROL ROOM TEMPRATURE | AI
22 | 415 V |  | TEMP_MON | BATTERY ROOM TEMPRATURE | AI
23 | 415 V |  | TEMP_MON | AMBIENT TEMPERATURE OUTDOOR | AI
24 | 415 V |  | TEMP_MON | AMBIENT RELATIVE HUMIDITY OUTDOOR | AI
25 | 415 V | DG Set | DGSET-1 | VOLTAGE (R-Y PHASE) | AI
26 | 415 V |  | DGSET-1 | VOLTAGE (Y-B PHASE) | AI
27 | 415 V |  | DGSET-1 | VOLTAGE (B-R PHASE) | AI
28 | 415 V |  | DGSET-1 | CURRENT (R-PHASE) | AI
29 | 415 V |  | DGSET-1 | CURRENT (Y-PHASE) | AI
30 | 415 V |  | DGSET-1 | CURRENT (B-PHASE) | AI
31 | 415 V |  | DGSET-1 | DG SET BATTERY-1 VOLTAGE | AI
32 | 415 V |  | DGSET-1 | DG SET BATTERY-2 VOLTAGE | AI
33 | 415 V | LTSUP | MSB-1 | VOLTAGE (R-Y PHASE) | AI
34 | 415 V |  | MSB-1 | VOLTAGE (Y-B PHASE) | AI
35 | 415 V |  | MSB-1 | VOLTAGE (B-R PHASE) | AI
36 | 415 V |  | MSB-1 | CURRENT (R-PHASE) | AI
37 | 415 V |  | MSB-1 | CURRENT (Y-PHASE) | AI
38 | 415 V |  | MSB-1 | CURRENT (B-PHASE) | AI
39 | 415 V |  | MSB-2 | VOLTAGE (R-Y PHASE) | AI
40 | 415 V |  | MSB-2 | VOLTAGE (Y-B PHASE) | AI
41 | 415 V |  | MSB-2 | VOLTAGE (B-R PHASE) | AI
42 | 415 V |  | MSB-2 | CURRENT (R-PHASE) | AI
43 | 415 V |  | MSB-2 | CURRENT (Y-PHASE) | AI
44 | 415 V |  | MSB-2 | CURRENT (B-PHASE) | AI

## Digital_NEW (hidden)
Sl.NO | Device | DEVICE ID | SIGNAL DESCRIPTION | DATA TYPE | REMARKS | SCADA ID
1 | CB | CB | CB OPEN / CLOSE | DPS |  | STTS
2 |  | CB | CB R-PH OPEN / CLOSE | DPS |  | STTR
3 |  | CB | CB Y-PH OPEN / CLOSE | DPS |  | STTY
4 |  | CB | CB B-PH OPEN / CLOSE | DPS |  | STTB
5 |  | CB | CB OPEN / CLOSE COMMAND | DPC |  | DPC
6 |  | CB | CB CHECK SYNC BYPASS COMMAND | SPC |  | DLCC
7 |  | CB | CB MANUAL OPEN | SPS |  | MNOP
8 |  | CB | CB MANUAL CLOSE | SPS |  | MNCL
9 |  | CB | CB POLE DISCREPANCY OPERATED | SPS |  | PDIS
10 |  | CB | CB POLE DISCREPANCY WITH IN POLE OPERATED | SPS |  | PDIB
11 |  | CB | CB DC SUPPLY 1/2 FAIL | SPS |  | DC
12 |  | CB | CB AC SUPPLY FAIL | SPS |  | ACSP
13 |  | CB | CB SPRING DISCHARGE | SPS |  | SPRG
14 |  | CB | CB SF6 LOW ALARM | SPS |  | SF6L
15 |  | CB | CB TC1 Faulty | SPS |  | TC1F
16 |  | CB | CB TC2 Faulty | SPS |  | TC2F
17 |  | CB | CB IN LOCAL/REMOTE | SPS |  | CBLM
18 |  | CB | CB MCB TRIPPED ( Motor/Heating/Lighting) | SPS |  | MCBT
19 |  | CB | INTERLOCK ENABLED | SPS |  | INTL
20 |  | CB | LBB PROTECTION OPERATED | SPS |  | LBBO
21 |  | CB | OPERATION LOCKOUT | SPS |  | OPL
22 | ISOLATOR | Isolator | ISOLATOR OPEN / CLOSE | DPS |  | STTS
23 |  | Isolator | ISOLATOR OPEN / CLOSE | DPS |  | STTS
24 |  | Isolator | INTERLOCK ENABLED | SPS |  | INTL
25 |  | Isolator | ISOLATOR OPEN / CLOSE COMMAND | DPC |  | STTS
26 | Earth Switch | Earth Switch | EARTH SWITCH OPEN / CLOSE | DPS |  | STTS
27 |  | Earth Switch | INTERLOCK ENABLED | SPS |  | INTL
28 | BCU | BCU | BCU IN LOCAL / REMOTE | DPS |  | BCUR
29 |  | BCU | BCU UNHEALTHY | SPS |  | BCUH
30 |  | BCU | BCU TIME SYNC ERROR | SPS |  | BCUC
31 | Line | A/R | AUTO RECLOSE IN AUTO / NONAUTO | DPS |  | ARNA
32 |  | A/R | AUTO RECLOSE IN AUTO / NONAUTO COMMAND | DPC |  | ARNA
33 |  | A/R | Autoreclosure Block | SPS
34 |  | A/R | AUTORECLOSE LOCKOUT | SPS |  | ARLO
35 |  | A/R | AUTORECLOSE OPERATED | SPS |  | AROP
36 |  | A/R | AUTORECLOSE UNSUCCESFUL | SPS |  | ARFM
37 |  | A/R | A/R LOCK OUT RELAY RESET | SPC |  | ARLO
38 |  | Main-1 Distance | MAIN-1 PROTECTION OPERATED | SPS |  | M1OP
39 |  | Main-1 Distance | MAIN-1 DISTANCE PROTECTION ZONE1 TRIP | SPS |  | M1Z1
40 |  | Main-1 Distance | MAIN-1 DISTANCE PROTECTION ZONE2 TRIP | SPS |  | M1Z2
41 |  | Main-1 Distance | MAIN-1 DISTANCE PROTECTION ZONE3 TRIP | SPS |  | M1Z3
42 |  | Main-1 Distance | MAIN-1 DISTANCE PROTECTION REVERSE ZONE TRIP | SPS |  | M1RP
43 |  | Main-1 Distance | MAIN-1 A/R BLOCK | SPS |  | M1AR
44 |  | Main-1 Distance | MAIN-1 CVT FUSE FAILURE | SPS |  | M1FU
45 |  | Main-1 Distance | MAIN-1 RELAY FAULTY | SPS |  | M1UH
46 |  | Main-1 Distance | MAIN-1 DEF OPERATED | SPS |  | M1DE
47 |  | Main-1 Distance | MAIN-1 SOTF OPERATED | SPS |  | M1SO
48 |  | Main-1 Distance | MAIN-1 CARRIER SEND CH-1 | SPS |  | CAR7
49 |  | Main-1 Distance | MAIN-1 CARRIER SEND CH-2 | SPS |  | CAR8
50 |  | Main-1 Distance | MAIN-1 CARRIED RECD CH-1 | SPS |  | CAR3
51 |  | Main-1 Distance | MAIN-1 CARRIED RECD CH-2 | SPS |  | CAR5
52 |  | Main-1 Distance | MAIN-1 CARRIER AIDED TRIP | SPS |  | CAT1
53 |  | Main-1 Distance | MAIN-1 CARRIER SWITCH IN OUT OF SERVICE | SPS |  | CAS1
54 |  | Main-1 Distance | DIRECT TRIP SEND CHANNEL 1 | SPS |  | TRS1
55 |  | Main-1 Distance | DIRECT RECEIVED CHANNEL 1 | SPS |  | TRP1
56 |  | Main-1 Distance | MAIN-1 PSB DETECTED | SPS |  | PSB1
57 |  | Main-1 Distance | MAIN-1 STUB PROTN OPERATED | SPS |  | STUB
58 |  | Main-1 Distance | MAIN-1 O/V STAGE-1 TRIP | SPS |  | OV-1
59 |  | Main-1 Distance | 89L OPERATED FOR STUB M1 | SPS
60 |  | Main-1 Distance | MAIN-1 O/V STAGE-2 TRIP | SPS |  | OV-2
61 |  | Main-1 Distance | DIRECT TRIP SEND CHANNEL 2 | SPS |  | TRS2
62 |  | Main-1 Distance | DIRECT RECEIVED CHANNEL 2 | SPS |  | TRP2
63 |  | Main-1 Distance | CARRIER FAIL CH-1 | SPS |  | CAF1
64 |  | Main-1 Distance | DC SOURCE-1 FAIL | SPS |  | DC-1
65 |  | Main-1 Distance | DC SOURCE-2 FAIL | SPS |  | DC-2
66 |  | Main-1 Distance | CARRIER FAIL CH-2 | SPS |  | CAF2
67 |  | Busbar Relay | MAIN-1 BB PROTECTION OPTD | SPS |  | BB1P
68 |  | Busbar Relay | MAIN-2 BB PROTECTION OPTD | SPS |  | BB2P
69 |  | Busbar Relay | MAIN-1 BB PU UNIT FAULTY | SPS |  | B1UH
70 |  | Busbar Relay | MAIN-2 BB PU UNIT FAULTY | SPS |  | B2UH
71 |  | Master Trip | 86A TRIP RELAY OPERATED | SPS |  | 86AO
72 |  | Master Trip | 86B TRIP RELAY OPERATED | SPS |  | 86BO
73 |  | Master Trip | 86A TRIP RELAY FAULTY | SPS |  | 86AU
74 |  | Master Trip | 86B TRIP RELAY FAULTY | SPS |  | 86BU
75 |  | Master Trip | 86A TRIP RELAY RESET | SPC |  | 86AO
76 |  | Master Trip | 86B TRIP RELAY RESET | SPC |  | 86BO
77 |  | Line Differential Relay | MAIN-1 LINE DIFFERENTIAL PROTECTION OPERATED | SPS
78 |  | Line Differential Relay | MAIN-2 LINE DIFFERENTIAL PROTECTION OPERATED | SPS
79 |  | Line Differential Relay | MAIN-1 DIFFERENTIAL PROTN TRIP R PH | SPS
80 |  | Line Differential Relay | MAIN-1 DIFFERENTIAL PROTN TRIP Y PH | SPS
81 |  | Line Differential Relay | MAIN-1 DIFFERENTIAL PROTN TRIP B PH | SPS
82 |  | Line Differential Relay | MAIN-2 DIFFERENTIAL PROTN TRIP R PH | SPS
83 |  | Line Differential Relay | MAIN-2 DIFFERENTIAL PROTN TRIP Y PH | SPS
84 |  | Line Differential Relay | MAIN-2 DIFFERENTIAL PROTN TRIP B PH | SPS
85 |  | Line Differential Relay | MAIN-1 DIFFERENTIATED WAVE BLOCK | SPS
86 |  | Line Differential Relay | MAIN-1 DIFFERENTIATED HORMONICS BLOCK | SPS
87 |  | Line Differential Relay | MAIN-2 DIFFERENTIATED WAVE BLOCK | SPS
88 |  | Line Differential Relay | MAIN-2 DIFFERENTIATED HORMONICS BLOCK | SPS
89 |  | Line Differential Relay | MAIN-1 DIFFERENTIATED RESTRAIN TRIP | SPS
90 |  | Line Differential Relay | MAIN-2 DIFFERENTIATED RESTRAIN TRIP | SPS
91 |  | Line Differential Relay | MAIN-1 DIFFERENTIATED UNRESTRAIN TRIP | SPS
92 |  | Line Differential Relay | MAIN-2 DIFFERENTIATED UNRESTRAIN TRIP | SPS
93 |  | Line Differential Relay | MAIN-1 BROKEN CONDUCTOR ALARM | SPS
94 |  | Line Differential Relay | MAIN-2 BROKEN CONDUCTOR ALARM | SPS
95 | Reactor | Reactor Differential | DIFFERENTIAL RELAY OPTD. | SPS |  | REDI
96 |  | Reactor Differential | DIFFERENTIAL RELAY FAULTY | SPS |  | DIRU
97 |  | Backup Impedance | B/U IMPEDANCE OPTD | SPS |  | BUIO
98 |  | Backup Impedance | B/U RELAY FAULTY | SPS |  | BURF
99 |  | Backup Impedance | SELECTED VT FUSE FAIL ALARM | SPS |  | VTFU
100 |  | REF | REF OPTD | SPS |  | RERE
101 |  | REF | REF RELAY FAULTY | SPS |  | RERE
102 |  | ? | DC SOURCE-1 FAIL | SPS |  | DC-1
103 |  | ? | DC SOURCE-2 FAIL | SPS |  | DC-2
104 |  | ? | Oil level low alarm R phase | SPS | 3 PHASE STATUS IS REQUIRED IF LINE REACTOR/ BUS REACTOR IS 3 PHASE | REOL
105 |  | Buchholz | BUCHOLTZ ALARM_R PHASE | SPS |  | BUCA
106 |  | Buchholz | BUCHOLTZ TRIP_R PHASE | SPS |  | BUCT
107 |  | ?? | SHUT_OFF_VALVE TRIP R PHASE | SPS |  | VLVT
108 |  | WTI | WTI ALARM_R PHASE | SPS |  | WTIA
109 |  | WTI | WTI_TRIP_R PHASE | SPS |  | WTIT
110 |  | OTI | OTI_ALARM_R_PHASE | SPS |  | OTIA
111 |  | OTI | OTI_TRIP_R_PHASE | SPS |  | OTIT
112 |  | PRV | PRV_TRIP_1_R_PHASE | SPS |  | REPR
113 |  | PRV | PRV_TRIP_2_R_PHASE | SPS |  | PRV2
114 |  | Fire Protection | FIRE PROTN OPTD R PHASE | SPS |  | FRRR
115 |  | Fire Protection | DELUGE VALVE ON - R PHASE | SPS |  | DVRR
116 |  | Fire Protection | COMMAND FOR DELUGE VALVE | SPC |  | DVTR
117 |  | Spare selection | SPARE REACTOR SELECT FOR R PHASE | SPS |  | SPRE
118 |  | TEED Protection | TEED PROTECTION OPTD | SPS
119 |  | TEED Protection | TEED RELAY FAULTY | SPS
120 |  | CSD | CONTROL SWITCH DEVICE BYPASSED | SPS |  | BYSW
121 |  | CSD | CONTROL SWITCH DEVICE TROUBLE | SPS
122 |  | CSD | BYPASS CMD FOR CNTRL SWITCH DEVICE | SPC |  | BYSW
123 |  | Busbar Relay | MAIN-1 BB PROTECTION OPTD | SPS |  | BB1P
124 |  | Busbar Relay | MAIN-2 BB PROTECTION OPTD | SPS |  | BB2P
125 |  | Busbar Relay | MAIN-1 BB PU UNIT FAULTY | SPS |  | B1UH
126 |  | Busbar Relay | MAIN-2 BB PU UNIT FAULTY | SPS |  | B2UH
127 |  | Master Trip | 86A TRIP RELAY OPERATED | SPS |  | 86AO
128 |  | Master Trip | 86B TRIP RELAY OPERATED | SPS |  | 86BO
129 |  | Master Trip | 86A TRIP RELAY FAULTY | SPS |  | 86AU
130 |  | Master Trip | 86B TRIP RELAY FAULTY | SPS |  | 86BU
131 |  | Master Trip | 86A TRIP RELAY RESET | SPC |  | 86AO
132 |  | Master Trip | 86B TRIP RELAY RESET | SPC |  | 86BO
133 | NGR | NGR | BUCHHOLZ TRIP(NGR) | SPS
134 |  | NGR | REACTOR PRV TRIP(NGR) | SPS
135 |  | NGR | OTI TRIP(NGR) | SPS
136 |  | NGR | OTI ALARM(NGR) | SPS
137 |  | NGR | BUCHHOLZ ALARM(NGR) | SPS
138 |  | NGR | LOW OIL LEVEL ALARM(NGR) | SPS
139 | ICT (Primary) | Differential | DIFFERENTIAL RELAY OPTD. | SPS |  | TFDI
140 |  | Differential | DIFF RELAY UNHEALTHY | SPS |  | DIRU
141 |  | Overflux | OVERFLUX ALARM | SPS |  | OFLA
142 |  | Overflux | OVERFLUX TRIP OPTD | SPS |  | OFLP
143 |  | Backup O/C and E/F | BACKUP O/C, E/F OPTD (HV) | SPS |  | BUOC
144 |  | Backup O/C and E/F | BACKUP O/C E/F RELAY UNHEALTHY | SPS |  | CFRL
145 |  | Backup O/C and E/F | SELECTED VT FUSE FAIL ALARM | SPS |  | VTFU
146 |  | Backup O/C and E/F | INTERTRIP OPTD. | SPS |  | TRPO
147 |  | ? | DC SOURCE-1 FAIL | SPS |  | DC-1
148 |  | ? | DC SOURCE-2 FAIL | SPS |  | DC-2
149 |  | Busbar Relay | MAIN-1 BB PROTECTION OPTD | SPS |  | BB1P
150 |  | Busbar Relay | MAIN-2 BB PROTECTION OPTD | SPS |  | BB2P
151 |  | Busbar Relay | MAIN-1 BB PU UNIT FAULTY | SPS |  | B1UH
152 |  | Busbar Relay | MAIN-2 BB PU UNIT FAULTY | SPS |  | B2UH
153 |  | REF | REF OPTD R PHASE | SPS | 3 PHASE STATUS IS REQUIRED IF LINE REACTOR/ BUS REACTOR IS 3 PHASE | TFRF
154 |  | REF | REF RELAY FAULTY | SPS
155 |  | Buchholz | BUCHHOLZ ALARM R PHASE | SPS |  | BUCA
156 |  | Buchholz | BUCHHOLZ TRIP R PHASE | SPS |  | BUCT
157 |  | OTI | OTI ALARM R PHASE | SPS |  | OTIA
158 |  | OTI | OTI TRIP R PHASE | SPS |  | OTIT
159 |  | WTI | WTI ALARM (HV/IV/LV) R PHASE | SPS |  | WTIA
160 |  | WTI | WTI TRIP (HV/IV/LV) R PHASE | SPS |  | WTIT
161 |  | PRV | PRV-1 TRIP R-PHASE | SPS |  | TFPR
162 |  | PRV | PRV-2 TRIP R-PHASE | SPS |  | PRV2
163 |  | OLTC | OLTC OIL SURGE RELAY OPTD- R PHASE | SPS |  | OLTR
164 |  | OLTC | OLTC PRV TRIP OPTD- R PHASE | SPS |  | OLTP
165 |  | OLTC | OLTC OIL LEVEL ALARM R PHASE | SPS
166 |  | OLTC | OIL FLOW VALVE TRIP- R PHASE | SPS
167 |  | OLTC | OLTC DRIVE MOTOR FAULTY | SPS
168 |  | Cooling System | FANS FAIL TO START BANK A - R PHASE | SPS |  | FANF
169 |  | Cooling System | FANS FAIL TO START BANK B - R PHASE | SPS |  | FANB
170 |  | Cooling System | PUMPS FAIL TO START BANK A - R PHASE | SPS |  | PMPF
171 |  | Cooling System | PUMPS FAIL TO START BANK B - R PHASE | SPS |  | PMPB
172 |  | Cooling System | OIL FLOW LOW ALARM BANK R PHASE | SPS |  | TFOL
173 |  | ? | COMMON THERMAL O/L ALARM R PHASE | SPS |  | OLAL
174 |  | ? | COMMON THERMAL O/L TRIP R PHASE | SPS |  | CTTP
175 |  | ? | STANDBY SUPLY FAIL R PHASE | SPS |  | SBSF
176 |  | Fire Protection | FIRE IN TRANSFORMER R PHASE | SPS |  | FRTR
177 |  | Fire Protection | DELUGE VALVE OPTD - R PHASE | SPS |  | DVTR
178 |  | Fire Protection | DELGUE VALVE COMMAND ICT | SPC
179 |  | Spare selection | SPARE ICT SELECTED FOR R PHASE | SPS
180 |  | ? | AVR OPERATION FAIL | SPS
181 |  | Neutral O/C | NEUTRAL O/C PROTECTION OPTD | SPS
182 |  | Neutral O/C | NEUTRAL O/C RELAY UNHEALTHY | SPS
183 |  | ? | DIRECT WDG TEMP MONITORING TRIP R PHASE | SPS
184 |  | Backup Impedance | BACKUP IMPEDANCE TRIP Z1 | SPS |  | BUZ1
185 |  | Backup Impedance | BACKUP IMPEDANCE TRIP Z2 | SPS |  | BUZ2
186 |  | Backup Impedance | BACKUP IMPEDANCE TRIP Z3 | SPS |  | BUZ3
187 |  | Backup Impedance | BACKUP IMPEDANCE TRIP Z4 | SPS |  | BUZ4
188 |  | Backup Impedance | BU IMPEDANCE RELAY FAULTY | SPS
189 |  | Backup Impedance | VT FUSE FAIL ALARM | SPS |  | VTFU
190 |  | Backup Impedance | POWER SWING BLOCKING | SPS
191 |  | Busbar Relay | MAIN-1 BB PROTECTION OPTD | SPS |  | BB1P
192 |  | Busbar Relay | MAIN-2 BB PROTECTION OPTD | SPS |  | BB2P
193 |  | Busbar Relay | MAIN-1 BB PU UNIT FAULTY | SPS |  | B1UH
194 |  | Busbar Relay | MAIN-2 BB PU UNIT FAULTY | SPS |  | B2UH
195 |  | Master Trip | 86A TRIP RELAY OPERATED | SPS |  | 86AO
196 |  | Master Trip | 86B TRIP RELAY OPERATED | SPS |  | 86BO
197 |  | Master Trip | 86A TRIP RELAY FAULTY | SPS |  | 86AU
198 |  | Master Trip | 86B TRIP RELAY FAULTY | SPS |  | 86BU
199 |  | Master Trip | 86A TRIP RELAY RESET | SPC |  | 86AO
200 |  | Master Trip | 86B TRIP RELAY RESET | SPC |  | 86BO
201 | ICT (Secondary) | Overflux | LV - OVERFLUX ALARM | SPS |  | OFLA
202 |  | Overflux | LV - OVERFLUX OPTD | SPS |  | OFLP
203 |  | Backup O/C and E/F | LV - BACKUP O/C OPTD | SPS |  | BUOC
204 |  | Backup O/C and E/F | LV - BACKUP E/F OPTD | SPS |  | BUEF
205 |  | Backup O/C and E/F | SELECTED VT FUSE FAIL ALARM | SPS |  | VTFU
206 |  | Master Trip | 86A TRIP RELAY OPERATED | SPS |  | 86AO
207 |  | Master Trip | 86B TRIP RELAY OPERATED | SPS |  | 86BO
208 |  | Master Trip | 86A TRIP REALY UNHEALTHY | SPS |  | 86AU
209 |  | Master Trip | 86B TRIP REALY UNHEALTHY | SPS |  | 86BU
210 |  | Busbar Relay | MAIN-1 BB PROTECTION OPTD | SPS |  | BB1P
211 |  | Busbar Relay | MAIN-2 BB PROTECTION OPTD | SPS |  | BB2P
212 |  | Busbar Relay | MAIN-1 BB PU UNIT FAULTY | SPS |  | B1UH
213 |  | Busbar Relay | MAIN-2 BB PU UNIT FAULTY | SPS |  | B2UH
214 |  | ? | DC SOURCE-1 FAIL | SPS |  | DC-1
215 |  | ? | DC SOURCE-2 FAIL | SPS |  | DC-2
216 | Bus Bar | G_B1 | M1 BB Z1 operated | SPS |  | BB17
217 |  | G_B1 | M2 BB Z1 operated | SPS |  | BB18
218 |  | G_B1 | M1 BB Z1 out of service | SPS |  | BB9
219 |  | G_B1 | M2 BB Z1 out of service | SPS |  | BB30
220 |  | G_B1 | M1 BB Z1 CT Trouble | SPS |  | M1TB
221 |  | G_B1 | M2 BB Z1 CT Trouble | SPS |  | M2TB
222 |  | G_B1 | Main-1 BB relay Healthy | SPS |  | BBH
223 |  | G_B2 | M1 BB Z2 operated | SPS |  | BBH
224 |  | G_B2 | M2 BB Z2 operated | SPS
225 |  | G_B2 | M1 BB Z2 out of service | SPS
226 |  | G_B2 | M2 BB Z2 out of service | SPS
227 |  | G_B2 | M1 BB Z2 CT Trouble | SPS
228 |  | G_B2 | M2 BB Z2 CT Trouble | SPS
229 |  | G_B2 | Main-2 BB relay Healthy | SPS
230 |  | G_B1 | MAIN-1 BB BLOCK/FIBERCOM ERROR | SPS
231 |  | G_B2 | MAIN-2 BB BLOCK/FIBERCOM ERROR | SPS
232 | GIS Bay additional Signals | GIS Bay additional Signals | CB PUMP RUNTIME EXCEEDED | SPS
233 |  | GIS Bay additional Signals | DE DRIVE STATUS ALARM | SPS
234 |  | GIS Bay additional Signals | CRANK HANDLE INSERTED | SPS
235 |  | GIS Bay additional Signals | PARTIAL DISCHARGE HIGH ALARM | SPS
236 |  | GIS Bay additional Signals | LCC IN LOCAL MODE | SPS
237 |  | GIS Bay additional Signals | LCC IN REMOTE MODE | SPS
238 |  | GIS Bay additional Signals | BAY INTERLOCK BYPASS SELECTED | SPS
239 |  | GIS Bay additional Signals | GAS LKG R/Y/B STG1 REFILL | SPS |  | SF61
240 |  | GIS Bay additional Signals | GAS LKG R/Y/B STG2 LOW | SPS |  | SF62
241 |  | GIS Bay additional Signals | GAS LKG R/Y/B ZONE TRIP | SPS |  | SF6T
242 |  | GIS Bay additional Signals | GAS LKG R/Y/B CB LOCKOUT/CB OPERATION LOCKOUT | SPS |  | SF6T
243 | BCHRG & DCDB | BATCHRG220V-1 | 220V BATTERY CHARGER -1 ON FLOAT MODE | DPS
244 |  | BATCHRG220V-1 | 220V BATTERY CHARGER -1 ON BOOST MODE | DPS
245 |  | BATCHRG220V-2 | 220V BATTERY CHARGER -2 ON FLOAT MODE | DPS
246 |  | BATCHRG220V-2 | 220V BATTERY CHARGER -2 ON BOOST MODE | DPS
247 |  | BATCHRG48V-1 | 48V BATTERY CHARGER -1 ON FLOAT MODE | DPS
248 |  | BATCHRG48V-1 | 48V BATTERY CHARGER -1 ON BOOST MODE | DPS
249 |  | BATCHRG48V-2 | 48V BATTERY CHARGER -2 ON FLOAT MODE | DPS
250 |  | BATCHRG48V-2 | 48V BATTERY CHARGER -2 ON BOOST MODE | DPS
251 |  | 220V_DCDB-1 | 220V DCDB -1 EARTH FAULT | SPS
252 |  | 220V_DCDB-2 | 220V DCDB -2 EARTH FAULT | SPS
253 |  | BATCHRG220V-1 | 220V BATTERY CHARGER-1 TROUBLE | SPS
254 |  | BATCHRG220V-2 | 220V BATTERY CHARGER-2 TROUBLE | SPS
255 |  | BATCHRG48V-1 | 48V BATTERY CHARGER-1 TROUBLE | SPS
256 |  | BATCHRG48V-2 | 48V BATTERY CHARGER-2 TROUBLE | SPS
257 | DGSET | DGSET-1 | DG SET BREAKER OPEN | DPS
258 |  | DGSET-1 | DG SET BREAKER CLOSE | DPS
259 |  | DGSET-1 | DG SET START COMMAND | SPC
260 |  | DGSET-1 | DG SET STOP COMMAND | SPC
261 |  | DGSET-1 | ALTERNATOR ON | SPS
262 |  | DGSET-1 | CHARGER 1 ON | SPS
263 |  | DGSET-1 | CHARGER 2 ON | SPS
264 |  | DGSET-1 | ENGINE OVERHEATING | SPS
265 |  | DGSET-1 | HIGH COOLING WATER TEMP. | SPS
266 |  | DGSET-1 | LOW OIL PRESSURE TRIP | SPS
267 |  | DGSET-1 | DG SET FAILED TO START IN 30 SEC | SPS
268 |  | DGSET-1 | LACK OF FUEL | SPS
269 |  | DGSET-1 | LOW LEVEL IN DAILY SERVICE FUEL TANK | SPS
270 |  | DGSET-1 | HIGH SPEED DIESEL TANK LEVEL LOW | SPS
271 |  | DGSET-1 | OVERSPEED TRIP | SPS
272 |  | DGSET-1 | DG I/C PROTN OPTD(ALT FAULT,DIFF ETC) | SPS
273 |  | DGSET-1 | CONTROL SUPPLY FAIL | SPS
274 |  | DGSET-1 | DG PROTECTION OPERATED (O/C, E/F, DIFF.) | SPS
275 |  | DGSET-1 | DG PROTECTION U/V OPERATED | SPS
276 |  | DGSET-1 | AMF PANEL REMOTE SWITCH INDICATION | SPS
277 |  | DGSET-1 | DG OVERLOAD | SPS
278 |  | DGSET-1 | PHASE SEQUENCE NEGATIVE ALARM | SPS
279 | LTSUP | ACDB-1 | ACDB INCOMER-1 OPEN | DPS
280 |  | ACDB-1 | ACDB INCOMER-1 CLOSE | DPS
281 |  | ACDB-1 | ACDB INCOMER-1 O/C PROTN. RLY OPTD | SPS
282 |  | ACDB-1 | ACDB INCOMER-1 E/F PROTN. RLY OPTD | SPS
283 |  | ACDB-1 | ACDB INCOMER-1 U/V PROTN. RLY OPTD | SPS
284 |  | ACDB-BC | ACDB BUS COUPLER OPEN | DPS
285 |  | ACDB-BC | ACDB BUS COUPLER CLOSE | DPS
286 |  | ACDB-BC | SUPERVISION OF CONTROL SUPPLY | SPS
287 |  | ACDB-2 | ACDB INCOMER-2 OPEN | DPS
288 |  | ACDB-2 | ACDB INCOMER-2 CLOSE | DPS
289 |  | ACDB-2 | ACDB INCOMER-2 O/C PROTN. RLY OPTD | SPS
290 |  | ACDB-2 | ACDB INCOMER-2 E/F PROTN. RLY OPTD | SPS
291 |  | ACDB-2 | ACDB INCOMER-2 U/V PROTN. RLY OPTD | SPS
292 |  | MSB-1 | MSB-1 CB OPEN | DPS
293 |  | MSB-1 | MSB-1 CB CLOSE | DPS
294 |  | MSB-1 | AUX. TRAFO-1 BUCHHOLZ ALARM | SPS
295 |  | MSB-1 | AUX. TRAFO-1 WTI ALARM | SPS
296 |  | MSB-1 | AUX. TRAFO-1 OTI ALARM | SPS
297 |  | MSB-1 | AUX. TRAFO-1 BUCHHOLZ TRIP | SPS
298 |  | MSB-1 | AUX. TRAFO-1 WTI TRIP | SPS
299 |  | MSB-1 | AUX. TRAFO-1 OTI TRIP | SPS
300 |  | MSB-1 | I/C-1 O/C PROTECTION RELAY TRIP | SPS
301 |  | MSB-1 | I/C-1 E/F PROTECTION RELAY TRIP | SPS
302 |  | MSB-1 | MSB BUS-1 U/V OPTD | SPS
303 |  | MSB-1 | PHASE SEQUENCE NEGATIVE ALARM | SPS
304 |  | MSB_BC | MSB BUS COUPLER BREAKER OPEN | DPS
305 |  | MSB_BC | MSB BUS COUPLER BREAKER CLOSE | DPS
306 |  | MSB_BC | SUPERVISION OF CONTROL SUPPLY | SPS
307 |  | MSB-2 | MSB-2 CB OPEN | DPS
308 |  | MSB-2 | MSB- 2 CB CLOSE | DPS
309 |  | MSB-2 | AUX. TRAFO-2 BUCHHOLZ ALARM | SPS
310 |  | MSB-2 | AUX. TRAFO- 2 WTI ALARM | SPS
311 |  | MSB-2 | AUX. TRAFO-2 OTI ALARM | SPS
312 |  | MSB-2 | AUX. TRAFO-2 BUCHHOLZ TRIP | SPS
313 |  | MSB-2 | AUX. TRAFO-2 WTI TRIP | SPS
314 |  | MSB-2 | AUX. TRAFO-2 OTI TRIP | SPS
315 |  | MSB-2 | I/C-2 O/C PROTECTION RELAY TRIP | SPS
316 |  | MSB-2 | I/C-2 E/F PROTECTION RELAY TRIP | SPS
317 |  | MSB-2 | MSB BUS-2 U/V OPTD | SPS
318 |  | MSB-2 | PHASE SEQUENCE NEGATIVE ALARM | SPS
319 |  | TERTIARY | EARTH SWITCH OPEN | DPS
320 |  | TERTIARY | EARTH SWITCH CLOSE | DPS
321 |  | TERTIARY | CB OPEN | DPS
322 |  | TERTIARY | CB CLOSE | DPS
323 |  | TERTIARY | ISO OPEN | DPS
324 |  | TERTIARY | ISO CLOSE | DPS
325 |  | TERTIARY | CB INTERLOCK ENABLED | SPS
326 |  | TERTIARY | ISO INTERLOCK ENABLED | SPS
327 |  | TERTIARY | CB TRIPPED ON PROTN | SPS
328 | FP | EPUMP | ELECTRIC MOTOR FIRE WATER PUMP RUNNING | SPS
329 |  | EPUMP | ELECTRIC MOTOR FIRE WATER PUMP FAILS TO START | SPS
330 |  | EPUMP | ELECTRIC PUMP IN AUTO MODE | SPS
331 |  | EPUMP | CONTROL SUPPLY FAIL | SPS
332 |  | EPUMP | HVW ELECTRIC PUMP ACB ON | DPS
333 |  | EPUMP | HVW ELECTRIC PUMP ACB OFF | DPS
334 |  | EPUMP | EMER. START OF ELECTRIC MOTOR DRIVEN PUMP | SPC
335 |  | EPUMP | EMER. STOP OF ELECTRIC MOTOR DRIVEN PUMP | SPC
336 |  | DPUMP | DIESEL ENGINE FIRE WATER PUMP FAILS TO START | SPS
337 |  | DPUMP | DIESEL ENGINE FIRE WATER PUMP RUNNING | SPS
338 |  | DPUMP | DIESEL ENGINE PUMP IN AUTO MODE | SPS
339 |  | DPUMP | DIESEL ENGINE BATTERY CHARGER-1 ON | SPS
340 |  | DPUMP | DIESEL ENGINE BATTERY CHARGER-2 ON | SPS
341 |  | DPUMP | DIESEL ENGINE FUEL LEVEL LOW | SPS
342 |  | DPUMP | CONTROL SUPPLY FAIL | SPS
343 |  | DPUMP | DIESEL PUMP OVER SPEED TRIP | SPS
344 |  | DPUMP | DIESEL PUMP LOW OIL PRESSURE TRIP | SPS
345 |  | DPUMP | DIESEL ENGINE HIGH TEMPERATURE ALARM | SPS
346 |  | DPUMP | EMER. START OF DIESEL MOTOR DRIVEN PUMP | SPC
347 |  | DPUMP | EMER. STOP OF DIESEL MOTOR DRIVEN PUMP | SPC
348 |  | SMOKE ALARM | CONTROL ROOM ZONE-1 FIRE DETECTED | SPS
349 |  | SMOKE ALARM | CONTROL ROOM ZONE-2 FIRE DETECTED | SPS
350 |  | SMOKE ALARM | CONTROL ROOM ZONE-3 FIRE DETECTED | SPS
351 |  | SMOKE ALARM | CONTROL ROOM ZONE-4 FIRE DETECTED | SPS
352 |  | SMOKE ALARM | 765KV KIOSK-1 FIRE DETECTED | SPS
353 |  | SMOKE ALARM | 400kV KIOSK-1 FIRE DETECTED | SPS
354 |  | FIREPROTN | WATER STORAGE TANK-1 WATER LEVEL LOW | SPS
355 |  | FIREPROTN | WATER STORAGE TANK-2 WATER LEVEL LOW | SPS
356 |  | FIREPROTN | FIRE FIGHTING TANK HEADER PRESSURE LEVEL LOW | SPS
357 |  | FIREPROTN | FIRE ANNAUNCIATION PANEL FAULTY | SPS
358 |  | FIREPROTN | COMMON FIRE ALARM | SPS
359 |  | FIREPROTN | CONTROL SUPPLY FAIL | SPS
360 |  | JPUMP-1 | JOCKEY PUMP-1 RUNNING | SPS
361 |  | JPUMP-1 | JOCKEY PUMP-1 FAILS TO START | SPS
362 |  | JPUMP-1 | SUPERVISION OF CONTROL SUPPLY | SPS
363 |  | JPUMP-2 | JOCKEY PUMP-2 RUNNING | SPS
364 |  | JPUMP-2 | JOCKEY PUMP-2 FAILS TO START | SPS
365 |  | JPUMP-2 | SUPERVISION OF CONTROL SUPPLY | SPS
366 |  | G_703_ICT-1 | FIRE IN ICT/ REACTOR | SPS
367 |  | G_703_ICT-1 | DELUGE SYSTEM OPERATING FOR ICT/REACTOR | SPS
368 |  | G_703_ICT-1 | DELGUE VALVE ICT/REACTOR ON COMMAND | SPC
369 | SYSTEM | AUX_SYSTEM | SUBSTATION MAIN CONTROL ON NTAMC | SPS
370 |  | AUX_SYSTEM | SUBSTATION MAIN CONTROL ON RTAMC | SPS
371 |  | AUX_SYSTEM | SUBSTATION MAIN CONTROL ON BACK UP NTAMC | SPS
372 |  | AUX_SYSTEM | SUBSTATION AUX CONTROL ON NTAMC | SPS
373 |  | AUX_SYSTEM | SUBSTATION AUXCONTROL ON RTAMC | SPS
374 |  | AUX_SYSTEM | SUBSTATION AUX CONTROL ON BACK UP NTAMC | SPS
375 |  | AUX_SYSTEM | SUBSTATION COMMAND FOR MAIN CONTROL ON NTAMC | SPC
376 |  | AUX_SYSTEM | SUBSTATION COMMAND FOR MAIN CONTROL ON RTAMC | SPC
377 |  | AUX_SYSTEM | SUBSTATION COMMAND FOR MAIN CONTROL ON BACK UP NTAMC | SPC
378 |  | AUX_SYSTEM | SUBSTATION COMMAND FOR AUX CONTROL ON NTAMC | SPC
379 |  | AUX_SYSTEM | SUBSTATION COMMAND FOR AUXCONTROL ON RTAMC | SPC
380 |  | AUX_SYSTEM | SUBSTATION COMMAND FOR AUX CONTROL ON BACK UP NTAMC | SPC
381 | COMMON | PLCC | PLCC EXCHANGE FAIL | SPS
382 |  | GPS | TIME SYNCH. SIGNAL ABSENT | SPS
383 | AIRCON | G_KIOSK_1 | 765KV KIOSK-1 HIGH TEMP ALARM | SPS
384 |  | F_KIOSK_1 | 400KV KIOSK-1 HIGH TEMP ALARM | SPS
385 | SAS | GATEWAY | GATEWAY-1 FAIL | SPS
386 |  | GATEWAY | GATEWAY-2 FAIL | SPS
387 |  | LOCAL_HMI | LOCAL HMI-1 FAIL | SPS
388 |  | LOCAL_HMI | LOCAL HMI-2 FAIL | SPS

## ms (hidden)
400KV LINE with Non-Switched Reactor
S.No | BAY NO | RTU INPUT | TYPE | DATA |  | S.No | BAY NO | BCU INPUTS | TYPE | DATA |  | S.No | BAY NO | BCU OUTPUTS | TYPE | DATA
1 | 40X-52 | CB COMPRESSOR / PUMP ON | SPS | HARD |  | 1 | 40X-52 | CB OPEN | DPS | HARD |  | 1 | 40X-52 | CB OPEN COMMAND | DPC | HARD
2 | 40X-52 | CB AC SUPPLY FAIL | SPS | HARD |  | 2 | 40X-52 | CB CLOSE | DPS | HARD |  | 2 | 40X-52 | CB CLOSE COMMAND | DPC | HARD
3 | 40X-52 | CB LOSS OF SF6 | SPS | HARD |  | 3 | 40X-52 | CB MANUAL OPEN | SPS | HARD |  | 3 | 40X-89A | ISOLATOR OPEN COMMAND | DPC | HARD
4 | 40X-52 | CB TROUBLE ALARM | SPS | HARD |  | 4 | 40X-52 | CB MANUAL CLOSE | SPS | HARD |  | 4 | 40X-89A | ISOLATOR CLOSE COMMAND | DPC | HARD
5 | 40X | MAIN-1/2 -POWERSWING BLCK DETECTED | SPS | HARD |  | 5 | 40X-89A | ISOLATOR OPEN | DPS | HARD |  | 5 | 40X-89B | ISOLATOR OPEN COMMAND | DPC | HARD
6 | 40X | MAIN-1/2 STUB PROTECTION OPTD. | SPS | HARD |  | 6 | 40X-89A | ISOLATOR CLOSE | DPS | HARD |  | 6 | 40X-89B | ISOLATOR CLOSE COMMAND | DPC | HARD
7 | 40X | DIRECT TRIP RECEIVED- CH.-1/2 | SPS | HARD |  | 7 | 40X-89AE | EARTH SWITCH OPEN | DPS | HARD |  | 7 | 40X-89L | ISOLATOR OPEN COMMAND | DPC | HARD
8 | 40X | DIRECT TRIP SEND-CH-1/2 | SPS | HARD |  | 8 | 40X-89AE | EARTH SWITCH CLOSE | DPS | HARD |  | 8 | 40X-89L | ISOLATOR CLOSE COMMAND | DPC | HARD
9 | 40X | MAIN-1 INTER TRIP RECEIVED | SPS | HARD |  | 9 | 40X-89B | ISOLATOR OPEN | DPS | HARD |  | 9 | 40X-89R | ISOLATOR OPEN COMMAND | DPC | HARD
10 | 40X | MAIN-1 INTER TRIP SEND | SPS | HARD |  | 10 | 40X-89B | ISOLATOR CLOSE | DPS | HARD |  | 10 | 40X-89R | ISOLATOR CLOSE COMMAND | DPC | HARD
11 | 40X | MAIN-2 INTER TRIP RECEIVED | SPS | HARD |  | 11 | 40X-89BE | EARTH SWITCH OPEN | DPS | HARD |  | 11 | 40X-89NGR | ISOLATOR OPEN COMMAND | DPC | HARD | *
12 | 40X | MAIN-2 INTER TRIP SEND | SPS | HARD |  | 12 | 40X-89BE | EARTH SWITCH CLOSE | DPS | HARD |  | 12 | 40X-89NGR | ISOLATOR CLOSE COMMAND | DPC | HARD | *
13 | 40X | OVERVOLTAGE STAGE-1 OPTD. | SPS | HARD |  | 13 | 40X-89L | ISOLATOR OPEN | DPS | HARD |  | 13 | 40X | A/R AUTO COMMAND | DPC | HARD
14 | 40X | OVERVOLTAGE STAGE-2 OPTD. | SPS | HARD |  | 14 | 40X-89L | ISOLATOR CLOSE | DPS | HARD |  | 14 | 40X | A/R NON AUTO COMMAND | DPC | HARD
15 | 40X | A/R UNSUCCESSFUL | SPS | HARD |  | 15 | 40X-89LE | EARTH SWITCH OPEN | DPS | HARD |  | 15 | 40X | CB CHECK SYNC. BYPASS COMMAND | SPC | SOFT
16 | 40X | CARRIER FAIL CH-1/2 | SPS | HARD |  | 16 | 40X-89LE | EARTH SWITCH CLOSE | DPS | HARD
17 | 40X | SPEECH CHANNEL FAIL | SPS | HARD |  | 17 | 40X-89R | ISOLATOR OPEN | DPS | HARD |  | S.No | BAY NO | BCU ANALOGUE INPUTS | TYPE | DATA
18 | 40X | DIFFERENTIAL PROTN OPTD. | SPS | HARD |  | 18 | 40X-89R | ISOLATOR CLOSE | DPS | HARD |  | 1 | 40X | REACTOR OTI-TEMP | AI | HARD
19 | 40X | REF PROTECTION OPTD. | SPS | HARD |  | 19 | 40X-89RE | EARTH SWITCH OPEN | DPS | HARD |  | 2 | 40X | REACTOR WTI-TEMP | AI | HARD
20 | 40X | BACK-UP IMPEDANCE PROTN OPTD | SPS | HARD |  | 20 | 40X-89RE | EARTH SWITCH CLOSE | DPS | HARD |  | 3 | 40X | I (R-PHASE) | AI | SOFT
21 | 40X | BUCHHOLZ TRIP | SPS | HARD |  | 21 | 40X-89NGR | ISOLATOR OPEN | DPS | HARD | ** | 4 | 40X | I (Y-PHASE) | AI | SOFT
22 | 40X | REACTOR PRV TRIP | SPS | HARD |  | 22 | 40X-89NGR | ISOLATOR CLOSE | DPS | HARD | ** | 5 | 40X | I B-PHASE) | AI | SOFT
23 | 40X | OTI TRIP | SPS | HARD |  | 23 | 40X | A/R IN AUTO MODE | DPS | HARD |  | 6 | 40X | MVAR | AI | SOFT
24 | 40X | WTI TRIP | SPS | HARD |  | 24 | 40X | A/R IN NON AUTO MODE | DPS | HARD |  | 7 | 40X | MW | AI | SOFT
25 | 40X | OTI ALARM | SPS | HARD |  | 25 | 40X-52 | CB OPERATION LOCKOUT | SPS | HARD |  | 8 | 40X | V (B-R PHASE) | AI | SOFT
26 | 40X | WTI ALARM | SPS | HARD |  | 26 | 40X-52 | CB POLE DISCREPANCY OPTD. | SPS | HARD |  | 9 | 40X | V (R-Y PHASE) | AI | SOFT
27 | 40X | BUCHHOLZ ALARM | SPS | HARD |  | 27 | 40X | DC SOURCE-1 FAIL | SPS | HARD |  | 10 | 40X | V (Y-B PHASE) | AI | SOFT
28 | 40X | LOW OIL LEVEL ALARM | SPS | HARD |  | 28 | 40X | DC SOURCE-2 FAIL | SPS | HARD |  | 11 | 40X | FREQUENCY | AI | SOFT
29 | 40X | BUCHHOLZ TRIP(NGR) | SPS | HARD | * | 29 | 40X | MAIN CB TC-1 FAULTY | SPS | HARD |  | 12 | 40X | Reactor I (R-PHASE) | AI | SOFT
30 | 40X | REACTOR PRV TRIP(NGR) | SPS | HARD | * | 30 | 40X | MAIN CB TC-2 FAULTY | SPS | HARD |  | 13 | 40X | Reactor I (Y-PHASE) | AI | SOFT
31 | 40X | OTI TRIP(NGR) | SPS | HARD | * | 31 | 40X | 86A TRIP RELAY OPTD. | SPS | HARD |  | 14 | 40X | Reactor I B-PHASE) | AI | SOFT
32 | 40X | WTI TRIP(NGR) | SPS | HARD | * | 32 | 40X | 86B TRIP RELAY OPTD. | SPS | HARD |  | 15 | 40X | Reactor MVAR | AI | SOFT
33 | 40X | OTI ALARM(NGR) | SPS | HARD | * | 33 | 40X | 86LO A/R LOCKOUT RELAY OPTD. | SPS | HARD |  | 16 | 40X | Reactor V (B-R PHASE) | AI | SOFT
34 | 40X | WTI ALARM(NGR) | SPS | HARD | * | 34 | 40X | Main-1 BB PROTN. OPTD. | SPS | HARD |  | 17 | 40X | Reactor V (R-Y PHASE) | AI | SOFT
35 | 40X | BUCHHOLZ ALARM(NGR) | SPS | HARD | * | 35 | 40X | Main-2 BB PROTN. OPTD. | SPS | HARD |  | 18 | 40X | Reactor V (Y-B PHASE) | AI | SOFT
36 | 40X | LOW OIL LEVEL ALARM(NGR) | SPS | HARD | * | 36 | 40X | MAIN CB LBB OPTD. | SPS | HARD
37 | 40X | 86A TRIP RELAY UNHEALTHY | SPS | HARD |  | 37 | 40X | MAIN CB A/R OPTD. | SPS | HARD |  | S.No | BAY NO | RTU OUTPUT | TYPE | DATA
38 | 40X | 86B TRIP RELAY UNHEALTHY | SPS | HARD |  | 38 | 40X | CB A/R LOCKOUT | SPS | HARD |  | 1 | 40X | 86A TRIP RELAY RESET | SPC | HARD
39 | 40X | MAIN-1/2 WEAK END INFEED OPTD. | SPS | HARD |  | 39 | 40X | L/R SWITCH IN REMOTE | SPS | HARD |  | 2 | 40X | 86B TRIP RELAY RESET | SPC | HARD
40 | 40X | CB SPRING CHARGED/air/oil pr low | SPS | HARD |  | 40 | 40X | MAIN-1 DISTANCE PROTECTION OPTD. | SPS | HARD |  | 3 | 40X | 86LO A/R LOCKOUT RELAY RESET | SPC | HARD
41 | 40X | CB DC SUPPLY 1/2 FAIL | SPS | HARD |  | 41 | 40X | MAIN-1 ZONE-1 TRIP | SPS | HARD |  | 4 | 40X | REACTOR GR-A TRIP RESET | SPC | HARD
42 | 40X | BYPASS CMD FOR CNTRL SWITCH DEVICE | SPS | HARD |  | 42 | 40X | MAIN-1 CVT FUSE FAILURE | SPS | HARD |  | 5 | 40X | REACTOR GR-B TRIP RESET | SPC | HARD
43 | 40X | MAIN-1 CARRIER SWITCH OUT | SPS | HARD |  | 43 | 40X | MAIN-1 UNHEALTHY | SPS | HARD
44 | 40X | MAIN-2 CARRIER SWITCH OUT | SPS | HARD |  | 44 | 40X | MAIN-2 DISTANCE PROTECTION OPTD. | SPS | HARD
45 | 40X | Reactor Gr-A Trip Relay Unhealthy | SPS | HARD |  | 45 | 40X | MAIN-2 ZONE-1 TRIP | SPS | HARD |  | * | Applicable for NGR Only
46 | 40X | Reactor Gr-B Trip Relay Unhealthy | SPS | HARD |  | 46 | 40X | MAIN-2 CVT FUSE FAILURE | SPS | HARD
47 | 40XLA | R-PH LA LEAKAGE CURRENT HIGH | SPS | HARD |  | 47 | 40X | MAIN-2 UNHEALTHY | SPS | HARD
48 | 40XLA | Y-PH LA LEAKAGE CURRENT HIGH | SPS | HARD |  | 48 | 40X | MAIN-1/2 SOTF OPTD. | SPS | HARD
49 | 40XLA | B-PH LA LEAKAGE CURRENT HIGH | SPS | HARD |  | 49 | 40X-52 | INTERLOCK ENABLED | SPS | SOFT
50 | 40XRLA | R-PH REACTOR LA LEAKAGE CURRENT HIGH | SPS | HARD |  | 50 | 40X-89A | INTERLOCK ENABLED | SPS | SOFT
51 | 40XRLA | Y-PH REACTOR LA LEAKAGE CURRENT HIGH | SPS | HARD |  | 51 | 40X-89AE | INTERLOCK ENABLED | SPS | SOFT
52 | 40XRLA | B-PH REACTOR LA LEAKAGE CURRENT HIGH | SPS | HARD |  | 52 | 40X-89 | INTERLOCK ENABLED | SPS | SOFT
53 | 40X | REACTOR COOLING SYSTEM TROUBLE ALARM | SPS | HARD |  | 53 | 40X-89E | INTERLOCK ENABLED | SPS | SOFT
54 | 40X | CB R-Phase Close/Open | SPS | HARD |  | 54 | 40X-89L | INTERLOCK ENABLED | SPS | SOFT
55 | 40X | CB Y-Phase Close/Open | SPS | HARD |  | 55 | 40X-89LE | INTERLOCK ENABLED | SPS | SOFT
56 | 40X | CB B-Phase Close/Open | SPS | HARD |  | 56 | 40X-89R | INTERLOCK ENABLED | SPS | SOFT
[6 empty] | 57 | 40X-89RE | INTERLOCK ENABLED | SPS | SOFT
[6 empty] | 58 | 40X-89NGR | INTERLOCK ENABLED | SPS | SOFT
[6 empty] | 59 | 40X | MFT Healthy | SPS | SOFT
[6 empty] | 60 | 40X | MFT Healthy (Reactor) | SPS | SOFT
[6 empty] | 61 | 40X | BAY IN MAINTENANCE MODE | SPS | SOFT

## Summary-1
TYPICAL DATA LIST
IEC 60870-5-104 interoperability Profile for NTAMC Control centers
PROTOCOL SUMMARY
SL.No. | Description |  |  |  | Value |  | Remark
1 | ASDU Common Address |  |  |  | 1
2 | Common Address Size of ASDU |  |  |  | 2 Byte
3 | Information object Address Structure |  |  |  | 3 Byte
4 | Frame Max Length |  |  |  | 255
5 | MV Periodic Cycle |  |  |  | Periodic cycle 15Sec and Spontaneous transmission on 1% change of Current value. For Frequency 0.02% (i.e.0.01 Hz)
6 | Binary Time Stamp Size |  |  |  | 7 Byte |  | CP56 Time 2a
7 | T0: Connection Time Out |  |  |  | 30 Sec.
8 | T1: APDU Time Out |  |  |  | 15 Sec.
9 | T2: Acknowledge Time Out |  |  |  | 10 Sec.
10 | T3: Test Frame Time Out |  |  |  | 20 Sec.
11 | K: Send Acknowledgement Frames (APDU) |  |  |  | 12
12 | W: Acknowledgement Received Frame (APDU) |  |  |  | 8
13 | Time Synchronisation |  |  |  | NA |  | Locally through IRIG-B or SNTP
14 | Cause of Transmission |  |  |  | 2 Byte
DIGTAL STATUS SETTINGS PROFILE
SL.No. | Discription | Duration
1 | Debouncing Time | 4ms
2 | Filtering Delay | 5ms
IEC 60870-5-104 Digital Signal type
SL.No. | Discription |  | Status Signal type | CONTROL TYPE |  |  | TIME OUT DURATION
1(a) | Circuit Breaker (ON/OFF) |  | DPS | DPC |  | SBO | 3 Sec
1(b) | Circuit breaker (Check synch bypass) |  | SPS | SPC |  | SBO | 3 Sec
2 | Isolator |  | DPS | DPC |  | SBO | 20 Sec
3 | Trip Relay & L/O Relays reset |  | SPS | SPC |  | DIRECT OPERATE | 10 Sec
4 | Mode Selection (e.g. AR Auto/Non-auto, Protection Transfer etc.), Auxiliaries Motor, DG set & Diesel Engine, etc |  | DPS | DPC |  | SBO | 10 Sec
5 | Control Switching Device (CSD) BYPASS COMMAND & Status |  | SPS | SPC |  | SBO | 10 Sec
6 | Fire fighting tank Water level, Manual Open/Close status (One SPS for each level) |  | SPS | NA
7 | Auto/Manual, Local/Remote |  | DPS | NA
The abnormal state for SPS signals shall be the HIGH state for alarms like ALARM/NORMAL, UNHEALTHY/HEALTHY, LOW/NORMAL, FAIL/NORMAL, SET/RESET.
IEC 60870-5-104 ASDU TYPE
SL.No. | Description |  |  |  | ASDU TYPE ID |  | Remark
1 | Analog | Measured Valuse, Short Floating Point Value |  |  | 13
2 | SPS | Single Point Information with Time Tag |  |  | 30
3 | DPS | Double Point Information with Time Tag |  |  | 31
5 | SPC | Single Command |  |  | 45 |  | SET/RESET
6 | DPC | Double Command |  |  | 46 |  | OPEN/CLOSE
IEC 60870-5-104 IOA ADDRESS STRUCTURE
SL.No. | Description |  |  |  | Starting Address |  | Remark
1 | Single Point Status (SPS) |  |  |  | 1
2 | Double Point Status (DPS) |  |  |  | 5000
3 | Measurement Value (MV) or Analog Value (AI) |  |  |  | 10000
4 | Double Point Control (DPC) |  |  |  | 15000
5 | Single Point Control (SPC) |  |  |  | 17000

## CB ISO
NTAMC TYPICAL SIGNALS FOR SWITCHGEAR (CB,ISOLATOR & EARTH SWITCH)
CIRCUIT BREAKER SIGNALS |  |  | ISOLATOR SIGNALS
S.No | SIGNAL NAME | TYPE | S.No | SIGNAL NAME | TYPE
1 | CB OPENED / CLOSED | DPS | 1 | ISOLATOR OPENED / CLOSED | DPS
2 | CB R-PH OPENED / CLOSED | DPS | 2 | ISO INTERLOCK ENABLED | SPS
3 | CB Y-PH OPENED / CLOSED | DPS | 3 | ISOLATOR OPEN / CLOSE COMMAND | DPC
4 | CB B-PH OPENED / CLOSED | DPS | NOTE- 1. S.No. 1-3 Signals to be mapped for each isolator
5 | CB MANUAL OPEN | SPS
6 | CB MANUAL CLOSE | SPS
7 | POLE DISCREPANCY ALARM WITHIN PHASE. | SPS
8 | POLE DISCREPANCY ALARM ACROSS PHASE. | SPS
9 | CB DC SUPPLY 1/2 FAIL | SPS
10 | CB AC SUPPLY FAIL | SPS | EARTH SWITCH SIGNALS
11 | CB SPRING DISCHARGE | SPS | S.No | SIGNAL NAME | TYPE
12 | CB LOW AIR PRESSURE | SPS | 1 | EARTH SWITCH OPENED / CLOSED | DPS
13 | CB LOW HYDRAULIC PRESSURE | SPS | 2 | ES INTERLOCK ENABLED | SPS
14 | CB SF6 GAS PRESSURE FIRST STAGE LOW ALARM | SPS | NOTE- Signals to be mapped for each Earth Switch
15 | CB SF6 LOCK OUT ALARM ( SECOND STAGE ) | SPS
16 | CB TC1 Faulty | SPS
17 | CB TC2 Faulty | SPS
18 | CB TROUBLE ALARM
19 | CB MCB TRIPPED (Motor/Heating/Lighting) | SPS
20 | CB INTERLOCK ENABLED | SPS
21 | LBB PROTECTION OPERATED | SPS
22 | CB OPERATION LOCKOUT | SPS
23 | CB COMPRESSOR / PUMP ON | SPS
24 | CONTROL SWITCH DEVICE BYPASSED | SPS
25 | CONTROL SWITCH DEVICE TROUBLE | SPS
26 | BYPASS CMD FOR CNTRL SWITCH DEVICE | SPC
27 | CB OPEN / CLOSE COMMAND | DPC
28 | CB CHECK SYNC BYPASS COMMAND | SPC
NOTE-S.No. 11,12,13-One no. signal to be taken as per CB Operating Mechanism Type as applicable
NOTE- If any other signal is required for remote operation as per site condition, it needs to be incorporated in final signal list.

## LINE & OTHER
NTAMC TYPICAL SIGNALS FOR LINE BAY AND COMMON SIGNALS FOR OTHER BAYS
LINE DISTANCE PROTECTION SIGNALS |  |  | LINE DIFFERENTIAL PROTECTION SIGNALS |  |  | MASTER TRIP SIGNALS
S.No | SIGNAL NAME | TYPE | S.No | SIGNAL NAME | TYPE | S.No | SIGNAL NAME | TYPE
1 | MAIN-1 OPERATED | SPS | 1 | LINE DIFF PROT OPERATED | SPS | 1 | 86A TRIP RELAY OPERATED | SPS
2 | MAIN-1 ZONE1 TRIP | SPS | 2 | LINE DIFF PROT OPERATED R-PH | SPS | 2 | 86B TRIP RELAY OPERATED | SPS
3 | MAIN-1 ZONE2 TRIP | SPS | 3 | LINE DIFF PROT OPERATED Y-PH | SPS | 3 | 86A TRIP RELAY FAULTY | SPS
4 | MAIN-1 ZONE3 TRIP | SPS | 4 | LINE DIFF PROT OPERATED B-PH | SPS | 4 | 86B TRIP RELAY FAULTY | SPS
5 | MAIN-1 REVERSE ZONE TRIP | SPS | 5 | LINE DIFF COMM FAIL LOCAL | SPS | 5 | RESET 86A TRIP RELAY | SPC
6 | MAIN-1 PSB DETECTED | SPS | 6 | LINE DIFF COMM FAIL REMOTE | SPS | 6 | RESET 86B TRIP RELAY | SPC
7 | MAIN-1 CVT FUSE FAILURE | SPS | 7 | LINE DIFF PROT BLOCKED | SPS | NOTE- Applicable for master trip relays (86A/86B) of any element ( Main, Tie, Switchable reactor bays,ICT etc)
8 | MAIN-1 RELAY FAULTY | SPS | 8 | DIFFERENTIATED RESTRAIN TRIP | SPS
9 | MAIN-1 DEF OPERATED | SPS | 9 | DIFFERENTIATED UNRESTRAIN TRIP | SPS
10 | MAIN-1 SOTF OPERATED | SPS | 9 | DIFFERENTIAL RELAY UNHEALTHY | SPS
11 | MAIN-1 CARRIER SEND CH-1 | SPS | NOTE- Signal are to be taken as per Relay availability(Main-1/2) |  |  | BCU SIGNALS
12 | MAIN-1 CARRIER SEND CH-2 | SPS |  |  |  | S.No | SIGNAL NAME | TYPE
13 | MAIN-1 CARRIED RECD CH-1 | SPS | LINE ANALOG SIGNALS |  |  | 1 | BCU IN LOCAL / REMOTE | DPS
14 | MAIN-1 CARRIED RECD CH-2 | SPS | S.No | SIGNAL NAME | TYPE | 2 | BCU UNHEALTHY | SPS
15 | MAIN-1 O/V STAGE-1 TRIP | SPS | 1 | I (R-PHASE) | AI | 3 | BCU TIME SYNC ERROR | SPS
16 | MAIN-1 O/V STAGE-2 TRIP | SPS | 2 | I (Y-PHASE) | AI | NOTE-Applicable for all BCUs in each bay
17 | MAIN-1 STUB PROTN OPERATED | SPS | 3 | I (B-PHASE) | AI
18 | MAIN-1 STUB_ENABLED | SPS | 4 | MW | AI | PROCESS BUS SCHEME
19 | MAIN-1 CARRIER AIDED TRIP | SPS | 5 | MVAR | AI | S.No | SIGNAL NAME | TYPE
20 | MAIN-1 BROKEN CONDUCTOR ALARM | SPS | 6 | V (R-Y PHASE) | AI | 1 | Switchgear Control Unit Unhealthy(SU) | SPS
21 | MAIN-1 A/R BLOCK | SPS | 7 | V (Y-B PHASE) | AI | 2 | Merging Unit Unhealthy(MU) | SPS
22 | MAIN-1 CARRIER SWITCH IN OUT | SPS | 8 | V (B-R PHASE) | AI | 3 | Switchgear Control Unit Communication Fail | SPS
23 | MAIN-1 WEAK END INFEED OPTD. | SPS | 9 | FREQUENCY | AI | 4 | Merging Unit Communication Fail | SPS
24 | MAIN-1 OVERVOLTAGE START | SPS | NOTE-Applicable for each line feeder |  |  | 5 | Transformer Control Unit Communication Fail | SPS
25 | DIRECT TRIP SEND CHANNEL 1 | SPS |  |  |  | NOTE- 1)S. No. 1-4 are Applicable for each elelment 2) S.No. 5 is applicable for each ICT.
26 | DIRECT RECEIVED CHANNEL 1 | SPS | TRAVELLING WAVE FAULT LOCATOR SIGNALS
27 | DIRECT TRIP SEND CHANNEL 2 | SPS | S.No | SIGNAL NAME | TYPE
28 | DIRECT RECEIVED CHANNEL 2 | SPS | 1 | TWFL Trouble Alarm | SPS
29 | CARRIER FAIL CH-1 | SPS | 2 | TWFL Fault Distance | AI
30 | CARRIER FAIL CH-2 | SPS | NOTE- Signals Applicable as per availability of TWFL in line feeder |  |  | TIE BAY, TBC & BUS COUPLER CURRENTS
31 | DC SOURCE-1 FAIL | SPS |  |  |  | S.No | SIGNAL NAME | TYPE
32 | DC SOURCE-2 FAIL | SPS | CT- SF6 GAS |  |  | 1 | I (R-PHASE) | AI
NOTE- 1) S.No. 1 to 24 signal are to be taken for Main-2 Relay also 2) Sr No. 17 & 18 applicable as per bus bar scheme |  |  | S.No | SIGNAL NAME | TYPE | 2 | I (Y-PHASE) | AI
|  |  | 1 | CT LOSS SF6 R PH | SPS | 3 | I (B-PHASE) | AI
|  |  | 2 | CT LOSS SF6 Y PH | SPS | NOTE-Applicable for each tie bay, TBC and Bus Coupler
|  |  | 3 | CT LOSS SF6 B PH | SPS
AUTORECLOSURE SIGNALS |  |  | 4 | CT SF6 PR LOCKOUT | SPS
S.No | SIGNAL NAME | TYPE | NOTE-Applicable in case of SF6 CT |  |  | GIS BAYS SIGNALS
1 | A/R IN AUTO / NONAUTO MODE | DPS |  |  |  | S.No | SIGNAL NAME | TYPE
2 | A/R IN BLOCK MODE | SPS | SPECIAL PROTECTION |  |  | 1 | PARTIAL DISCHARGE HIGH ALARM | SPS
3 | AUTORECLOSE LOCKOUT | SPS | S.No | SIGNAL NAME | TYPE | 2 | LCC IN LOCAL MODE | SPS
4 | AUTORECLOSE OPERATED | SPS | 1 | df/dt OPERATION | SPS | 3 | LCC IN REMOTE MODE | SPS
5 | AUTORECLOSE UNSUCCESFUL | SPS | 2 | SPS Operated | SPS | 4 | GAS LEAKAGE R/Y/B STG1 REFILL | SPS
6 | CB NOT READY FOR A/R | SPS |  |  |  | 5 | GAS LEAKAGE R/Y/B STG2 LOW | SPS
7 | A/R/IN AUTO/NONAUTO COMMAND | DPC | PTS Signals |  |  | 6 | GAS LEAKAGE R/Y/B ZONE TRIP | SPS
8 | RESET A/R LOCKOUT RELAY | SPC | S.No | SIGNAL NAME | TYPE | 7 | GAS LEAKAGE R/Y/B CB LOCKOUT | SPS
NOTE-Applicable in case of Line and Respective Tie Bay |  |  | 1 | PTS Switch in Normal/Transfer Mode | DPS | NOTE- Sr. No. 4 to 7 signals are applicable for all gas compartment pertaining to each bay into one group. ( NTAMC IOM DTD. 05.10.2018 )
|  |  | 2 | PTS Switch in Normal/Transfer Mode Command | DPC
NOTE-Applicable for each element in case of Double Main Transfer Bus scheme
NOTE- If any other signal is required for remote operation as per site condition, it needs to be incorporated in final signal list.

## ICT REAC
NTAMC TYPICAL SIGNALS FOR ICT AND REACTOR BAYS
ICT/REACTOR SIGNALS |  |  | ICT/REACTOR PROTECTION SIGNALS |  |  | NGR BODY PROTECTION SIGNALS
S.No | SIGNAL NAME | TYPE | S.No | SIGNAL NAME | TYPE | S.No | SIGNAL NAME | TYPE
1 | LOW OIL LEVEL ALARM | SPS | 1 | BACKUP IMPEDANCE TRIP Z1 | SPS | 1 | BUCHHOLZ TRIP | SPS
2 | BUCHHOLZ ALARM | SPS | 2 | BACKUP IMPEDANCE TRIP Z2 | SPS | 2 | PRV TRIP | SPS
3 | BUCHHOLZ TRIP | SPS | 3 | BACKUP IMPEDANCE TRIP Z3 | SPS | 3 | OTI TRIP | SPS
4 | OTI ALARM | SPS | 4 | BACKUP IMPEDANCE TRIP Z4 | SPS | 4 | OTI ALARM | SPS
5 | OTI TRIP | SPS | 5 | POWER SWING BLOCKING | SPS | 5 | BUCHHOLZ ALARM | SPS
6 | WTI ALARM | SPS | 6 | HV - BACKUP O/C OPTD | SPS | 6 | LOW OIL LEVEL ALARM | SPS
7 | WTI TRIP | SPS | 7 | HV - BACKUP E/F OPTD | SPS | NOTE- 1) Applicable Only for oil filled NGR.
8 | PRV-1 TRIP | SPS | 8 | LV - BACKUP O/C OPTD | SPS
9 | PRV-2 TRIP | SPS | 9 | LV - BACKUP E/F OPTD | SPS
10 | SPARE REACTOR/TRANSFORMER SELECTED | SPS | 10 | LV - OVERFLUX ALARM | SPS
11 | SUDDEN PRESSURE RELAY TRIP | SPS | 11 | LV - OVERFLUX OPTD | SPS | ICT/REACTOR ANALOG SIGNALS
12 | OSR-1 Trip | SPS | 12 | HV-OVERFLUX ALARM | SPS | S.No | SIGNAL NAME | TYPE
13 | OSR-2 Trip | SPS | 13 | HV OVERFLUX TRIP | SPS | 1 | I (R-PHASE) | AI
14 | FIRE IN REACTOR/ICT | SPS | 14 | NEUTRAL O/C PROTECTION OPTD | SPS | 2 | I (Y-PHASE) | AI
15 | DELUGE VALVE OPTD | SPS | 15 | NEUTRAL O/C RELAY UNHEALTHY | SPS | 3 | I (B-PHASE) | AI
16 | DC SOURCE-1 FAIL | SPS | 16 | COMMON THERMAL O/L ALARM | SPS | 4 | MW | AI
17 | DC SOURCE-2 FAIL | SPS | 17 | COMMON THERMAL O/L TRIP | SPS | 5 | MVAR | AI
18 | SHUT OFF VALVE OPERATED | SPS | 18 | INTERTRIP OPTD. | SPS | 6 | V (R-Y PHASE) | AI
19 | OLTC PRV TRIP OPTD | SPS | 19 | BACKUP O/C E/F RELAY UNHEALTHY HV | SPS | 7 | V (Y-B PHASE) | AI
20 | OLTC OIL LEVEL ALARM | SPS | 20 | BACKUP O/C E/F RELAY UNHEALTHY LV | SPS | 8 | V (B-R PHASE) | AI
21 | OLTC DRIVE MOTOR FAULTY | SPS | 21 | REF OPERATED | SPS | 9 | FREQUENCY | AI
22 | DIRECT WDG TEMP MONITORING TRIP | SPS | 22 | REF BLOCK | SPS | 10 | HVWTI TEMP | AI
23 | FANS FAIL TO START BANK A | SPS | 23 | DIFFERENTIAL RELAY OPTD. | SPS | 11 | IVWTI TEMP | AI
24 | FANS FAIL TO START BANK B | SPS | 24 | BACKUP IMPEDANCE OPTD | SPS | 12 | LVWTI TEMP | AI
25 | PUMPS FAIL TO START BANK A | SPS | 25 | SELECTED VT FUSE FAIL ALARM (Combined signal for all selected VT Fuse fail) | SPS | 13 | OTI TEMP | AI
26 | PUMPS FAIL TO START BANK B | SPS | 26 | DIFF RELAY UNHEALTHY | SPS | 14 | TAP POSITION | AI
27 | OIL FLOW LOW ALARM BANK | SPS | 27 | REF RELAY UNHEALTHY | SPS | 15 | DGA MOISTURE VALUE | AI
28 | REACTOR COOLING SYSTEM TROUBLE | SPS | 28 | BACKUP IMPEDANCE RELAY UNHEALTHY | SPS | 16 | DGA H2 VALUE | AI
|  |  | 29 | TEED PROTECTION OPTD | SPS | 17 | DGA C2H2 VALUE | AI
NOTE- 1) Sr. no 1 to 18 - As applicable for ICT & Reactor. 2) Sr.no 19 to 27 - For ICTs. 3) Sr.no 28- for Reactor 4) As Applicable, above signal shall be required unit wise if individual phase units are existing. |  |  | 30 | TEED RELAY FAULTY | SPS | 18 | DGA CO VALUE | AI
|  |  | NOTE- 1) Sr. no 1 to 20 - As applicable for ICT. 2) Sr.no 21 to 28 - For ICTs & Reactor. 3) Sr.no 29 & 30 for Reactor if applicable as per scheme. 4) As Applicable, above signal shall be required unit wise if individual phase units are existing. |  |  | 19 | DGA CO2 VALUE | AI
[6 empty] | 20 | DGA CH4 VALUE | AI
[6 empty] | 21 | DGA C2H6 VALUE | AI
[6 empty] | 22 | DGA C2H4 VALUE | AI
[6 empty] | 23 | DGA N2 VALUE | AI
NOTE- 1) As Applicable, above signal(10-23) shall be required unit wise if individual phase units are existing. 2) ICT parameters needed at primary & secondary side(1-9) 3) Sr.No 14- TAP Position is applicable for ICT only. 4) 10,11,12 to be merged and single WTI to be taken for Reactor
NOTE- If any other signal is required for remote operation as per site condition, it needs to be incorporated in final signal list.

## BUS BAR AND CONTROL AUTH
NTAMC TYPICAL SIGNALS FOR BUSBAR AND CONTROL AUTHORITY
BUS BAR SIGNALS (BUS-I,II,TBC AS APPLICABLE) |  |  | BUS BAR PERIPHERAL UNITS- BAY WISE
S.No | SIGNAL NAME | TYPE | S.No | SIGNAL NAME | TYPE
1 | M1 BB Z1 OPERATED | SPS | 1 | MAIN-1 BB PU UNIT FAULTY | SPS
2 | M2 BB Z1 OPERATED | SPS | 2 | MAIN-2 BB PU UNIT FAULTY | SPS
3 | M1 BB Z2 OPERATED | SPS | 3 | MAIN-1 BB PROTECTION OPTD | SPS
4 | M2 BB Z2 OPERATED | SPS | 4 | MAIN-2 BB PROTECTION OPTD | SPS
5 | M1 BB Z1 OUT OF SERVICE | SPS | NOTE- 1) Signals to be taken for each bayas per availability of Bus Scheme .
6 | M2 BB Z1 OUT OF SERVICE | SPS
7 | M1 BB Z2 OUT OF SERVICE | SPS
8 | M2 BB Z2 OUT OF SERVICE | SPS
9 | Main-1 BB RELAY UNHEALTHY | SPS | CONTROL AUTHORITY SIGNALS
10 | Main-2 BB RELAY UNHEALTHY | SPS | S.No | SIGNAL NAME | TYPE
11 | M1 BB Z1 BLOCK (Circuitry fault, out of service, fibrecom and any other conditions etc to be grouped) | SPS | 1 | SUBSTATION MAIN CONTROL ON NTAMC | SPS
12 | M2 BB Z1 BLOCK(Circuitry fault, out of service, fibrecom and any other conditions etc to be grouped) | SPS | 2 | SUBSTATION MAIN CONTROL ON RTAMC | SPS
13 | M1 BB Z2 BLOCK(Circuitry fault, out of service, fibrecom and any other conditions etc to be grouped) | SPS | 3 | SUBSTATION MAIN CONTROL ON BACK UP | SPS
14 | M2 BB Z2 BLOCK(Circuitry fault, out of service, fibrecom and any other conditions etc to be grouped) | SPS | 4 | SUBSTATION AUX CONTROL ON NTAMC | SPS
15 | M1 BB Z1 CT TROUBLE | SPS | 5 | SUBSTATION AUX CONTROL ON RTAMC | SPS
16 | M2 BB Z1 CT TROUBLE | SPS | 6 | SUBSTATION AUX CONTROL ON BACKUP | SPS
17 | M1 BB Z2 CT TROUBLE | SPS
18 | M2 BB Z2 CT TROUBLE | SPS | 7 | COMMAND-MAIN CONTROL ON NTAMC | SPC
19 | MAIN-1 ZONE X AND ZONE Y MERGED/INTERCONNECTED | SPS | 8 | COMMAND-MAIN CONTROL ON RTAMC | SPC
20 | MAIN-2 ZONE X AND ZONE Y MERGED/INTERCONNECTED | SPS | 9 | COMMAND-MAIN CONTROL ON BACKUP | SPC
21 | CT SELECTION INCOMPLETE | SPS | 10 | COMMAND-AUX CONTROL ON NTAMC | SPC
22 | VOLTAGE R-Y PHASE | AI | 11 | COMMAND-AUX CONTROL ON RTAMC | SPC
23 | VOLTAGE Y-B PHASE | AI | 12 | COMMAND-AUX CONTROL ON BACKUP | SPC
24 | VOLTAGE B-R PHASE | AI | NOTE- 1) Applicable for each Substation.
25 | FREQUENCY | AI
26 | BUS BAR CHECK ZONE OPERATED | SPS
27 | BUS BAR CHECK ZONE CT SUPV ALARM | SPS
28 | BUS BAR CHECK ZONE OUT OF SERVICE | SPS
29 | BUS BAR CHECK ZONE RELAY UNHEALTHY | SPS
NOTE- 1) Signals to be taken as per availability of Bus Scheme(One and Half,Double Main, Double Main Transfer etc.) 2) S. No. 22 to 25- to be taken for each bus 3) Signal at S. No. 19 and 20 to be taken as per availability of Bus Interconnection combinations for DMT/DM/Bus Sectionalizer scheme 4) S. No. 21 Signal to be added for DMT and DM Scheme 5) S.No. 26 to 29 - to be taken for each Main-1, Main-2 relay separately as per scheme
NOTE- If any other signal is required for remote operation as per site condition, it needs to be incorporated in final signal list.

## AUX
NTAMC TYPICAL SIGNALS FOR AUXILIARY SYSTEM
LT SUPPLY SIGNALS-ACDB,MSB,TERTIARY |  |  | DG SET SIGNALS |  |  | FIRE FIGHTING
S.No | SIGNAL NAME | TYPE | S.No | SIGNAL NAME | TYPE | S.No | SIGNAL NAME | TYPE
1 | ACDB INCOMER-1 OPEN/CLOSE | DPS | 1 | DG SET BREAKER OPEN/CLOSE | DPS | 1 | ELECTRIC MOTOR FIRE WATER PUMP RUNNING | SPS
2 | ACDB INCOMER-1 U/V PROTN. RLY OPTD | SPS | 2 | ALTERNATOR ON | SPS | 2 | ELECTRIC MOTOR FIRE WATER PUMP FAILS TO START | SPS
3 | ACDB INCOMER-1 OPEN/CLOSE COMMAND | DPC | 3 | CHARGER 1 ON | SPS | 3 | ELECTRIC PUMP IN AUTO MODE | SPS
4 | ACDB BUS COUPLER OPEN/CLOSE | DPS | 4 | CHARGER 2 ON | SPS | 4 | EPUMP CONTROL SUPPLY FAIL | SPS
5 | ACDB BC SUPERVISION OF CONTROL SUPPLY | SPS | 5 | ENGINE OVERHEATING | SPS | 5 | HVW ELECTRIC PUMP ACB ON /OFF | DPS
6 | ACDB BC OPEN/CLOSE COMMAND | DPC | 6 | HIGH COOLING WATER TEMP. | SPS | 6 | DIESEL ENGINE FIRE WATER PUMP FAILS TO START | SPS
7 | MSB-1 CB OPEN/CLOSE | DPS | 7 | LOW OIL PRESSURE TRIP | SPS | 7 | DIESEL ENGINE FIRE WATER PUMP RUNNING | SPS
8 | AUX. TRAFO-1 BUCHHOLZ ALARM | SPS | 8 | DG SET FAILED TO START IN 30 SEC | SPS | 8 | DIESEL ENGINE PUMP IN AUTO MODE | SPS
9 | AUX. TRAFO-1 WTI ALARM | SPS | 9 | LACK OF FUEL | SPS | 9 | DIESEL ENGINE BATTERY CHARGER-1 ON | SPS
10 | AUX. TRAFO-1 OTI ALARM | SPS | 10 | LOW LEVEL IN DAILY SERVICE FUEL TANK | SPS | 10 | DIESEL ENGINE BATTERY CHARGER-2 ON | SPS
11 | AUX. TRAFO-1 BUCHHOLZ TRIP | SPS | 11 | HIGH SPEED DIESEL TANK LEVEL LOW | SPS | 11 | DIESEL ENGINE FUEL LEVEL LOW | SPS
12 | AUX. TRAFO-1 WTI TRIP | SPS | 12 | OVERSPEED TRIP | SPS | 12 | DPUMP CONTROL SUPPLY FAIL | SPS
13 | AUX. TRAFO-1 OTI TRIP | SPS | 13 | DG I/C PROTN OPTD(ALT FAULT,DIFF ETC) | SPS | 13 | DIESEL PUMP OVER SPEED TRIP | SPS
14 | I/C-1 O/C PROTECTION RELAY TRIP | SPS | 14 | CONTROL SUPPLY FAIL | SPS | 14 | DIESEL PUMP LOW OIL PRESSURE TRIP | SPS
15 | I/C-1 E/F PROTECTION RELAY TRIP | SPS | 15 | DG PROTECTION OPERATED (O/C, E/F, DIFF.) | SPS | 15 | DIESEL ENGINE HIGH TEMPERATURE ALARM | SPS
16 | MSB BUS-1 U/V OPTD | SPS | 16 | DG PROTECTION U/V OPERATED | SPS | 16 | CONTROL ROOM ZONE-1 FIRE DETECTED | SPS
17 | MSB-1 PHASE SEQUENCE NEGATIVE ALARM | SPS | 17 | AMF PANEL REMOTE SWITCH INDICATION | SPS | 17 | CONTROL ROOM ZONE-2 FIRE DETECTED | SPS
18 | MSB INCOMER-1 OPEN/CLOSE COMMAND | DPC | 18 | DG OVERLOAD | SPS | 18 | CONTROL ROOM ZONE-3 FIRE DETECTED | SPS
19 | MSB-1 VOLTAGE (R-Y PHASE) | AI | 19 | PHASE SEQUENCE NEGATIVE ALARM | SPS | 19 | CONTROL ROOM ZONE-4 FIRE DETECTED | SPS
20 | MSB-1 VOLTAGE (Y-B PHASE) | AI | 20 | ALTERNATOR FAULT | SPS | 20 | 765KV KIOSK-1 FIRE DETECTED | SPS
21 | MSB-1 VOLTAGE (B-R PHASE) | AI | 21 | ACTIVE POWER(KW) | AI | 21 | 400kV KIOSK-1 FIRE DETECTED | SPS
22 | MSB-1 CURRENT (R-PHASE) | AI | 22 | REACTIVE POWER(KVAR) | AI | 22 | WATER STORAGE TANK-1 WATER LEVEL LOW | SPS
23 | MSB-1 CURRENT (Y-PHASE) | AI | 23 | VOLTAGE (R-Y PHASE) | AI | 23 | WATER STORAGE TANK-2 WATER LEVEL LOW | SPS
24 | MSB-1 CURRENT (B-PHASE) | AI | 24 | VOLTAGE (Y-B PHASE) | AI | 24 | FIRE FIGHTING TANK HEADER PRESSURE LEVEL LOW | SPS
25 | MSB-1 ACTIVE POWER(KW) | AI | 25 | VOLTAGE (B-R PHASE) | AI | 25 | FIRE ANNAUNCIATION PANEL FAULTY | SPS
26 | MSB-1 REACTIVE POWER(KVAR) | AI | 26 | CURRENT (R-PHASE) | AI | 26 | COMMON FIRE ALARM | SPS
27 | MSB BUS COUPLER BREAKER OPEN/CLOSE | DPS | 27 | CURRENT (Y-PHASE) | AI | 27 | JOCKEY PUMP-1 RUNNING | SPS
28 | MSB_BC SUPERVISION OF CONTROL SUPPLY | SPS | 28 | CURRENT (B-PHASE) | AI | 28 | JOCKEY PUMP-1 FAILS TO START | SPS
29 | MSB BC OPEN/CLOSE COMMAND | DPC | 29 | DG SET BREAKER OPEN/CLOSE COMMAND | DPC | 29 | JPUMP-1 SUPERVISION OF CONTROL SUPPLY | SPS
30 | TERTIARY-EARTH SWITCH OPEN/CLOSE | DPS | 30 | DG SET START COMMAND | SPC | 30 | JOCKEY PUMP-2 RUNNING | SPS
31 | TERTIARY-CB OPEN /CLOSE | DPS | 31 | DG SET STOP COMMAND | SPC | 31 | JOCKEY PUMP-2 FAILS TO START | SPS
32 | TERTIARY-ISO OPEN /CLOSE | DPS |  |  |  | 32 | JPUMP-2 SUPERVISION OF CONTROL SUPPLY | SPS
33 | TERTIARY-CB INTERLOCK ENABLED | SPS |  |  |  | 33 | FIRE FIGHTING PRESSURE MONITORING | AI
34 | TERTIARY-ISO INTERLOCK ENABLED | SPS | DCDB & BATTERY CHARGER |  |  | NOTE- FIRE DETECTED Alarms to be taken as per applicability.
35 | TERTIARY-CB TRIPPED ON PROTN | SPS | S.No | SIGNAL NAME | TYPE
36 | TERTIARY-CB OPEN /CLOSE COMMAND | DPC | 1 | 220V BATTERY CHARGER -1 ON FLOAT/BOOST MODE | DPS
37 | TERTIARY-ISO OPEN /CLOSE COMMAND | DPC | 2 | 220V BATTERY CHARGER -2 ON FLOAT/BOOST MODE | DPS
NOTE- 1) S.No. 1 to 3 same signals to be taken for ACDB-2 also 2) S.No. 7 to 26 same signals to be taken for MSB-2 also |  |  | 3 | 48V BATTERY CHARGER -1 ON FLOAT/BOOST MODE | DPS | OTHER SIGNALS
|  |  | 4 | 48V BATTERY CHARGER -2 ON FLOAT/BOOST MODE | DPS | S.No | SIGNAL NAME | TYPE
|  |  | 5 | 220V DCDB -1 EARTH FAULT | SPS | 1 | TIME SYNCH. SIGNAL ABSENT | SPS
|  |  | 6 | 220V DCDB -2 EARTH FAULT | SPS | 2 | 765KV KIOSK-1 TEMP | AI
|  |  | 7 | 220V BATTERY CHARGER-1 TROUBLE | SPS | 3 | 400KV KIOSK-1 TEMP | AI
|  |  | 8 | 220V BATTERY CHARGER-2 TROUBLE | SPS | 4 | CONTROL ROOM TEMPRATURE | AI
|  |  | 9 | 48V BATTERY CHARGER-1 TROUBLE | SPS | 5 | BATTERY ROOM TEMPRATURE | AI
|  |  | 10 | 48V BATTERY CHARGER-2 TROUBLE | SPS | 6 | AMBIENT TEMPERATURE OUTDOOR | AI
|  |  | 11 | 220V DCDB -1 VOLTAGE | AI | 7 | AMBIENT RELATIVE HUMIDITY OUTDOOR | AI
|  |  | 12 | 220V BATTERY SET-1 CURRENT | AI | 8 | WIND SPEED | AI
|  |  | 13 | 220V DCDB -2 VOLTAGE | AI | 9 | SUBSTATION IN LOCAL/REMOTE | DPS
|  |  | 14 | 220V BATTERY SET-2 CURRENT | AI | NOTE- 1) S.No. 2,3 to be taken as per availability of no. of Kiosks
|  |  | 15 | 48V DCDB -1 VOLTAGE | AI
|  |  | 16 | 48V BATTERY SET-1 CURRENT | AI
|  |  | 17 | 48V DCDB -2 VOLTAGE | AI
|  |  | 18 | 48V BATTERY SET-2 CURRENT | AI
|  |  | 19 | 220V BATTERY CHARGER-1 CURRENT | AI
|  |  | 20 | 220V BATTERY CHARGER-2 CURRENT | AI
|  |  | 21 | 48V BATTERY CHARGER-1 CURRENT | AI
|  |  | 22 | 48V BATTERY CHARGER-2 CURRENT | AI
NOTE- 1) 110V DCDB Signals to be taken as per availability of DC source 2) Instantaneous alaram may be used for DC Earth Fault
NOTE- If any other signal is required for remote operation as per site condition, it needs to be incorporated in final signal list.

## FSC (hidden)
FSC
Distance Relay |  |  |  | Differential Relay |  |  |  | Master Trip Relay
S.No | BAY NO | Signal name | TYPE | S.No | BAY NO | Signal name | TYPE | S.No | BAY NO | Signal name | TYPE
1 | 52BBR | BPCB OPEN/CLOSE STATUS | DPS | 1 | ABC | MAIN-1 LINE DIFFERENTIAL PROTECTION OPERATED | SPS | 1 | ABC | 86A TRIP RELAY OPERATED | SPS
2 | 52BBR-RPh | BPCB R PHASE OPEN/CLOSE STATUS | DPS | 2 | ABC | MAIN-2 LINE DIFFERENTIAL PROTECTION OPERATED | SPS | 2 | ABC | 86B TRIP RELAY OPERATED | SPS
3 | 52BBR-YPh | BPCB Y PHASE OPEN/CLOSE STATUS | DPS | 3 | ABC | MAIN-2 DIFFERENTIAL PROTN TRIP R PH | SPS | 3 | ABC | 86A TRIP RELAY FAULTY | SPS
4 | 52BBR-Bph | BPCB B PHASE OPEN/CLOSE STATUS | DPS | 4 | ABC | MAIN-2 DIFFERENTIAL PROTN TRIP Y PH | SPS | 4 | ABC | 86B TRIP RELAY FAULTY | SPS
5 | 89MBS | BYPASS MBS ISOLATOR OPEN/CLOSE STATUS | DPS | 5 | ABC | MAIN-2 DIFFERENTIAL PROTN TRIP B PH | SPS | 5 | ABC | 86A TRIP RELAY RESET | SPC
6 | 89DS1 | ISOLATOR 1 OPEN/CLOSE STATUS | DPS | 6 | ABC | MAIN-1 DIFFERENTIATED WAVE BLOCK | SPS | 6 | ABC | 86B TRIP RELAY RESET | SPC
7 | 89DS2 | ISOLATOR 2 OPEN/CLOSE STATUS | DPS | 7 | ABC | MAIN-1 DIFFERENTIATED HORMONICS BLOCK | SPS
8 | 89ES1 | EARTH SWITCH 1 OPEN/CLOSE STATUS | DPS | 8 | ABC | MAIN-2 DIFFERENTIATED WAVE BLOCK | SPS | * Master Trip relay signals are required in All Bays and Switchable Reactors
9 | 89ES2 | EARTH SWITCH 2 OPEN/CLOSE STATUS | DPS | 9 | ABC | MAIN-2 DIFFERENTIATED HORMONICS BLOCK | SPS
10 | 52BBR | BPCB OPEN/CLOSE CMD | DPC | 10 | ABC | MAIN-1 DIFFERENTIATED RESTRAIN TRIP | SPS
11 | 89MBS | BYPASS MBS OPEN/CLOSE CMD | DPC | 11 | ABC | MAIN-2 DIFFERENTIATED RESTRAIN TRIP | SPS
12 | 89DS1 | BYPASS CAP ISO 1 OPEN/CLOSE CMD | DPC | 12 | ABC | MAIN-1 DIFFERENTIATED UNRESTRAIN TRIP | SPS | Auto Reclosure Signals
13 | 89DS2 | BYPASS CAP ISO 2 OPEN/CLOSE CMD | DPC | 13 | ABC | MAIN-2 DIFFERENTIATED UNRESTRAIN TRIP | SPS | S.No | BAY NO | Signal name | TYPE
14 |  | MASTER TRIP RST | SPC | 14 | ABC | MAIN-1 BROKEN CONDUCTOR ALARM | SPS | 1 | ABC | A/R IN AUTO / NONAUTO | DPS
|  | MOV TEMPERATURE R PHASE | AI | 15 | ABC | MAIN-2 BROKEN CONDUCTOR ALARM | SPS | 2 | ABC | A/R/IN AUTO/NONAUTO COMMAND | DPC
|  | MOV TEMPERATURE Y PHASE | AI | 16 | ABC | MAIN-1 BROKEN CONDUCTOR ALARM | SPS | 3 | ABC | A/R BLOCK | SPS
|  | MOV TEMPERATURE B PHASE | AI | 17 | ABC | MAIN-2 BROKEN CONDUCTOR ALARM | SPS | 4 | ABC | AUTORECLOSE LOCKOUT | SPS
|  | CAPACITOR R PHASE CURRENT | AI |  |  |  |  | 5 | ABC | AUTORECLOSE OPERATED | SPS
|  | CAPACITOR Y PHASE CURRENT | AI |  |  |  |  | 6 | ABC | AUTORECLOSE UNSUCCESFUL | SPS
|  | CAPACITOR B PHASE CURRENT | AI |  |  |  |  | 7 | ABC | A/R LOCK OUT RELAY RESET | SPC
|  | CAPACITOR R PHASE UNBALANCED CURRENT | AI | Busbar PU
|  | CAPACITOR Y PHASE UNBALANCED CURRENT | AI | S.No | BAY NO | Signal name | TYPE
|  | CAPACITOR B PHASE UNBALANCED CURRENT | AI | 1 | ABC | MAIN-1 BB PROTECTION OPTD | SPS
|  | LINE CT CURRENT R-PH | AI | 2 | ABC | MAIN-2 BB PROTECTION OPTD | SPS
|  | LINE CT CURRENT Y-PH | AI | 3 | ABC | MAIN-1 BB PU UNIT FAULTY | SPS | Analog Signals
|  | LINE CT CURRENT B-PH | AI | 4 | ABC | MAIN-2 BB PU UNIT FAULTY | SPS | S.No | BAY NO | Signal name | TYPE
|  | KIOSK TEMP | AI |  |  |  |  | 1 | ABC | I (R-PHASE) | AI
[8 empty] | 2 | ABC | I (Y-PHASE) | AI
[8 empty] | 3 | ABC | I (B-PHASE) | AI
[8 empty] | 4 | ABC | MW | AI
|  |  |  | BCU |  |  |  | 5 | ABC | MVAR | AI
|  |  |  | S.No | BAY NO | Signal name | TYPE | 6 | ABC | V (R-Y PHASE) | AI
|  |  |  | 1 | ABC | BCU IN LOCAL / REMOTE | DPS | 7 | ABC | V (Y-B PHASE) | AI
|  |  |  | 2 | ABC | BCU UNHEALTHY | SPS | 8 | ABC | V (B-R PHASE) | AI
|  |  |  | 3 | ABC | BCU TIME SYNC ERROR | SPS | 9 | ABC | FREQUENCY | AI
[8 empty] | 10 | ABC | MAIN-1 FAULT IMPEDANCE | AI
[8 empty] | 11 | ABC | MAIN-1 FAULT DISTANCE | AI
[8 empty] | 12 | ABC | MAIN-1 FAULT PERCENTAGE | AI
[8 empty] | 13 | ABC | MAIN-2 FAULT IMPEDANCE | AI
[8 empty] | 14 | ABC | MAIN-2 FAULT DISTANCE | AI
[8 empty] | 15 | ABC | MAIN-2 FAULT PERCENTAGE | AI

## DPS (hidden)
Sl.NO | BAY NUM. | BAY NAME | DEVICE ID | SIGNAL DESCRIPTION | DATA TYPE | SCADA ID | REMARK
LINE FEEDER (ONE AND HALF BREAKER SCHEME)
1 | ABC | LINE FEEDER | CB | CB OPEN / CLOSE | DPS | STTS
2 | ABC | LINE FEEDER | CB | CB R-PH OPEN / CLOSE | DPS | STTR
3 | ABC | LINE FEEDER | CB | CB Y-PH OPEN / CLOSE | DPS | STTY
4 | ABC | LINE FEEDER | CB | CB B-PH OPEN / CLOSE | DPS | STTB
5 | ABC | LINE FEEDER | 89A | ISOLATOR OPEN / CLOSE | DPS | STTS
6 | ABC | LINE FEEDER | 89B | ISOLATOR OPEN / CLOSE | DPS | STTS
7 | ABC | LINE FEEDER | 89L | ISOLATOR OPEN / CLOSE | DPS | STTS
8 | ABC | LINE FEEDER | 89AE1 | EARTH SWITCH OPEN / CLOSE | DPS | STTS | Bus Side Earth Switch
9 | ABC | LINE FEEDER | 89AE2 | EARTH SWITCH OPEN / CLOSE | DPS | STTS
10 | ABC | LINE FEEDER | 89BE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
11 | ABC | LINE FEEDER | 89LE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
12 | ABC | LINE FEEDER | BCU | BCU IN LOCAL / REMOTE | DPS | BCUR
13 | ABC | LINE FEEDER | CB | AUTO RECLOSE IN AUTO / NONAUTO | DPS | ARNA
SWITCHEABLE LINE REACTOR
1 | ABC | LINE REACTOR | 52R | REACTOR CB OPEN/CLOSE | DPS | STTS
2 | ABC | LINE REACTOR | 52R | REACTOR CB R-PH OPEN / CLOSE | DPS | STTR
3 | ABC | LINE REACTOR | 52R | REACTOR CB Y-PH OPEN / CLOSE | DPS | STTY
4 | ABC | LINE REACTOR | 52R | REACTOR CB B-PH OPEN / CLOSE | DPS | STTB
5 | ABC | LINE REACTOR | 89RR | ISOLATOR OPEN / CLOSE | DPS | STTS | 3 PHASE STATUS IS REQUIRED IF REACTOR IS 3 PHASE
6 | ABC | LINE REACTOR | 89RY | ISOLATOR OPEN / CLOSE | DPS | STTS
7 | ABC | LINE REACTOR | 89RB | ISOLATOR OPEN / CLOSE | DPS | STTS
8 | ABC | LINE REACTOR | 89RS1R | ISOLATOR OPEN / CLOSE | DPS | STTS | NOT APPLICABLE IF REACTOR IS 3 PHASE
9 | ABC | LINE REACTOR | 89RS1Y | ISOLATOR OPEN / CLOSE | DPS | STTS
10 | ABC | LINE REACTOR | 89RS1B | ISOLATOR OPEN / CLOSE | DPS | STTS
11 | ABC | LINE REACTOR | 89RER | EARTH SWITCH OPEN / CLOSE | DPS | STTS
12 | ABC | LINE REACTOR | 89REY | EARTH SWITCH OPEN / CLOSE | DPS | STTS
13 | ABC | LINE REACTOR | 89REB | EARTH SWITCH OPEN / CLOSE | DPS | STTS
14 | ABC | LINE REACTOR | RE-BCU | BCU IN LOCAL / REMOTE | DPS | BCUR
NGR
1 | ABC | LINE FEEDER WITH SW REACTOR | NGR | BYPASS CB OPEN / CLOSE | DPS | STTS | ISOLATOR STATUS REQUIRED IF BYPASS ISOLATOR IS AVAILABLE
TIE BAY/ BUS SECTION
1 | ABC | TIE/ BS | CB | CB OPEN / CLOSE | DPS | STTS
2 | ABC | TIE/ BS | CB | CB R-PH OPEN / CLOSE | DPS | STTR
3 | ABC | TIE/ BS | CB | CB Y-PH OPEN / CLOSE | DPS | STTY
4 | ABC | TIE/ BS | CB | CB B-PH OPEN / CLOSE | DPS | STTB
5 | ABC | TIE/ BS | 89A | ISOLATOR OPEN/CLOSE | DPS | STTS
6 | ABC | TIE/ BS | 89B | ISOLATOR OPEN/CLOSE | DPS | STTS
7 | ABC | TIE/ BS | 89AE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
8 | ABC | TIE/ BS | 89BE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
9 | ABC | TIE/ BS | BCU | BCU IN LOCAL / REMOTE | DPS | BCUR
10 | ABC | TIE/ BS | CB | AUTO RECLOSE IN AUTO / NONAUTO | DPS | ARNA
LINE SERIES REACTOR/ BUS SERIES REACTOR
1 | ABC | LSR / BSR | CB | CB OPEN / CLOSE | DPS | STTS
2 | ABC | LSR / BSR | CB | CB R-PH OPEN / CLOSE | DPS | STTR
3 | ABC | LSR / BSR | CB | CB Y-PH OPEN / CLOSE | DPS | STTY
4 | ABC | LSR / BSR | CB | CB B-PH OPEN / CLOSE | DPS | STTB
5 | ABC | LSR / BSR | 89A | ISOLATOR OPEN/CLOSE | DPS | STTS
6 | ABC | LSR / BSR | 89B | ISOLATOR OPEN/CLOSE | DPS | STTS
7 | ABC | LSR / BSR | 89AE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
8 | ABC | LSR / BSR | 89BE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
9 | ABC | LSR / BSR | 89L/ 89BSR | ISOLATOR OPEN / CLOSE | DPS | STTS
10 | ABC | LSR / BSR | 89LE/ 89BSRE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
11 | ABC | LSR | 89LSR | ISOLATOR OPEN/CLOSE | DPS | STTS | In case of Line Series Reactor
13 | ABC | LSR | 89LSR1 | ISOLATOR OPEN/CLOSE | DPS | STTS
15 | ABC | LSR | 89LSR2 | ISOLATOR OPEN/CLOSE | DPS | STTS
17 | ABC | LSR | 89LSR2- ES | EARTH SWITCH OPEN / CLOSE | DPS | STTS
BUS BAR
1 |  | BUS-X VT | 89 | ISOLATOR OPEN/CLOSE | STTS
2 |  | BUS-X VT | 89E | EARTH SWITCH OPEN / CLOSE | STTS
FUTURE BAY
1 | ABC | FUTURE LINE | 89A | ISOLATOR OPEN / CLOSE | DPS | STTS
2 | ABC | FUTURE LINE | 89AE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
3 | ABC | FUTURE LINE | BCU | BCU IN LOCAL / REMOTE | DPS | BCUR
765 KV BUS REACTOR (ONE AND HALF BREAKER SCHEME)
1 | ABC | BUS REACTOR | CB | CB OPEN / CLOSE | DPS | STTS
2 | ABC | BUS REACTOR | CB | CB R-PH OPEN / CLOSE | DPS | STTR
3 | ABC | BUS REACTOR | CB | CB Y-PH OPEN / CLOSE | DPS | STTY
4 | ABC | BUS REACTOR | CB | CB B-PH OPEN / CLOSE | DPS | STTB
5 | ABC | BUS REACTOR | 89A | ISOLATOR OPEN/CLOSE | DPS | STTS
6 | ABC | BUS REACTOR | 89B | ISOLATOR OPEN/CLOSE | DPS | STTS
7 | ABC | BUS REACTOR | 89AE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
8 | ABC | BUS REACTOR | 89BE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
9 | ABC | BUS REACTOR | 89RR | ISOLATOR OPEN / CLOSE | DPS | STTS | 3 PHASE STATUS IS REQUIRED IF REACTOR IS 3 PHASE
10 | ABC | BUS REACTOR | 89RY | ISOLATOR OPEN / CLOSE | DPS | STTS
11 | ABC | BUS REACTOR | 89RB | ISOLATOR OPEN / CLOSE | DPS | STTS
12 | ABC | BUS REACTOR | 89RS1R | ISOLATOR OPEN / CLOSE | DPS | STTS | NOT APPLICABLE IF REACTOR IS 3 PHASE
13 | ABC | BUS REACTOR | 89RS1Y | ISOLATOR OPEN / CLOSE | DPS | STTS
14 | ABC | BUS REACTOR | 89RS1B | ISOLATOR OPEN / CLOSE | DPS | STTS
15 | ABC | BUS REACTOR | 89RER | EARTH SWITCH OPEN / CLOSE | DPS | STTS
16 | ABC | BUS REACTOR | 89REY | EARTH SWITCH OPEN / CLOSE | DPS | STTS
17 | ABC | BUS REACTOR | 89REB | EARTH SWITCH OPEN / CLOSE | DPS | STTS
18 | ABC | BUS REACTOR | RE-BCU | BCU IN LOCAL / REMOTE | DPS | BCUR
ICT
1 | ABC | ICT | CB | CB OPEN / CLOSE | DPS | STTS
2 | ABC | ICT | CB | CB R-PH OPEN / CLOSE | DPS | STTR
3 | ABC | ICT | CB | CB Y-PH OPEN / CLOSE | DPS | STTY
4 | ABC | ICT | CB | CB B-PH OPEN / CLOSE | DPS | STTB
5 | ABC | ICT | 89A | ISOLATOR OPEN/CLOSE | DPS | STTS
6 | ABC | ICT | 89B | ISOLATOR OPEN/CLOSE | DPS | STTS
7 | ABC | ICT | 89AE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
8 | ABC | ICT | 89BE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
9 | ABC | ICT | 89TR | ISOLATOR OPEN / CLOSE | DPS | STTS | 3 PHASE STATUS IS REQUIRED INSTEAD OF SINGLE PHASE ISOLATOR IN CASE OF 3 PHASE ICT
10 | ABC | ICT | 89TY | ISOLATOR OPEN / CLOSE | DPS | STTS
11 | ABC | ICT | 89TB | ISOLATOR OPEN / CLOSE | DPS | STTS
12 | ABC | ICT | 89TS1R | ISOLATOR OPEN / CLOSE | DPS | STTS | NOT APPLICABLE FOR 3 PHASE ISOLATOR
13 | ABC | ICT | 89TS1Y | ISOLATOR OPEN / CLOSE | DPS | STTS
14 | ABC | ICT | 89TS1B | ISOLATOR OPEN / CLOSE | DPS | STTS
15 | ABC | ICT | 89TER | EARTH SWITCH OPEN / CLOSE | DPS | STTS
16 | ABC | ICT | 89TEY | EARTH SWITCH OPEN / CLOSE | DPS | STTS
17 | ABC | ICT | 89TEB | EARTH SWITCH OPEN / CLOSE | DPS | STTS
18 | ABC | ICT | 89TS2EB | EARTH SWITCH OPEN / CLOSE | DPS | STTS
19 | ABC | ICT | BCU | BCU IN LOCAL / REMOTE | DPS | BCUR
LINE FEEDER (DOUBLE MAIN )
1 | ABC | LINE FEEDER | CB | CB OPEN / CLOSE | DPS | STTS
2 | ABC | LINE FEEDER | CB | CB R-PH OPEN / CLOSE | DPS | STTR
3 | ABC | LINE FEEDER | CB | CB Y-PH OPEN / CLOSE | DPS | STTY
4 | ABC | LINE FEEDER | CB | CB B-PH OPEN / CLOSE | DPS | STTB
5 | ABC | LINE FEEDER | 89A | ISOLATOR OPEN/CLOSE | DPS | STTS
6 | ABC | LINE FEEDER | 89B | ISOLATOR OPEN/CLOSE | DPS | STTS
7 | ABC | LINE FEEDER | 89AE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
8 | ABC | LINE FEEDER | 89L | ISOLATOR OPEN / CLOSE | DPS | STTS
9 | ABC | LINE FEEDER | 89LE1 | EARTH SWITCH OPEN / CLOSE | DPS | STTS
10 | ABC | LINE FEEDER | 89LE2 | EARTH SWITCH OPEN / CLOSE | DPS | STTS
11 | ABC | LINE FEEDER | BCU | BCU IN LOCAL / REMOTE | DPS | BCUR
ICT (DOUBLE MAIN )
1 | ABC | ICT | CB | CB OPEN / CLOSE | DPS | STTS
2 | ABC | ICT | CB | CB R-PH OPEN / CLOSE | DPS | STTR
3 | ABC | ICT | CB | CB Y-PH OPEN / CLOSE | DPS | STTY
4 | ABC | ICT | CB | CB B-PH OPEN / CLOSE | DPS | STTB
5 | ABC | ICT | 89A | ISOLATOR OPEN/CLOSE | DPS | STTS
6 | ABC | ICT | 89B | ISOLATOR OPEN/CLOSE | DPS | STTS
7 | ABC | ICT | 89AE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
8 | ABC | ICT | 89T | ISOLATOR OPEN / CLOSE | DPS | STTS
9 | ABC | ICT | 89TE1 | EARTH SWITCH OPEN / CLOSE | DPS | STTS
10 | ABC | ICT | 89TE2 | EARTH SWITCH OPEN / CLOSE | DPS | STTS
11 | ABC | ICT | BCU | BCU IN LOCAL / REMOTE | DPS | BCUR
220 KV ICT (DMT SCHEME)
1 | ABC | ICT | CB | CB OPEN / CLOSE | DPS | STTS
2 | ABC | ICT | 89A | ISOLATOR OPEN/CLOSE | DPS | STTS
3 | ABC | ICT | 89B | ISOLATOR OPEN/CLOSE | DPS | STTS
4 | ABC | ICT | 89T | ISOLATOR OPEN / CLOSE | DPS | STTS
5 | ABC | ICT | 89L | EARTH SWITCH OPEN / CLOSE | DPS | STTS
6 | ABC | ICT | 89AE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
7 | ABC | ICT | 89LE1 | EARTH SWITCH OPEN / CLOSE | DPS | STTS
8 | ABC | ICT | 89LE2 | EARTH SWITCH OPEN / CLOSE | DPS | STTS
9 | ABC | ICT | BCU | BCU IN LOCAL / REMOTE | DPS | BCUR
220 KV LINE FEEDER (DMT SCHEME)
1 | ABC | LINE FEEDER | CB | CB OPEN / CLOSE | DPS | STTS
2 | ABC | LINE FEEDER | CB | CB R-PH OPEN / CLOSE | DPS | STTR
3 | ABC | LINE FEEDER | CB | CB Y-PH OPEN / CLOSE | DPS | STTY
4 | ABC | LINE FEEDER | CB | CB B-PH OPEN / CLOSE | DPS | STTB
5 | ABC | LINE FEEDER | 89A | ISOLATOR OPEN / CLOSE | DPS | STTS
6 | ABC | LINE FEEDER | 89B | ISOLATOR OPEN / CLOSE | DPS | STTS
7 | ABC | LINE FEEDER | 89T | ISOLATOR OPEN / CLOSE | DPS | STTS
8 | ABC | LINE FEEDER | 89L | ISOLATOR OPEN / CLOSE | DPS | STTS
9 | ABC | LINE FEEDER | 89AE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
10 | ABC | LINE FEEDER | 89LE1 | EARTH SWITCH OPEN / CLOSE | DPS | STTS
11 | ABC | LINE FEEDER | 89LE2 | EARTH SWITCH OPEN / CLOSE | DPS | STTS
12 | ABC | LINE FEEDER | BCU | BCU IN LOCAL / REMOTE | DPS | BCUR
13 | ABC | LINE FEEDER | CB | AUTO RECLOSE IN AUTO / NONAUTO | DPS | ARNA
14 | ABC | LINE FEEDER | CB | TRANSFER SWITCH NORMAL/TRANSFER | DPS | TSWN
220 KV BUS COUPLER (DMT SCHEME)
1 | ABC | BUS COUPLER | CB | CB OPEN / CLOSE | DPS | STTS
2 | ABC | BUS COUPLER | 89A | ISOLATOR OPEN / CLOSE | DPS | STTS
3 | ABC | BUS COUPLER | 89B | ISOLATOR OPEN / CLOSE | DPS | STTS
4 | ABC | BUS COUPLER | 89AE1 | EARTH SWITCH OPEN / CLOSE | DPS | STTS
5 | ABC | BUS COUPLER | 89AE2 | EARTH SWITCH OPEN / CLOSE | DPS | STTS
6 | ABC | BUS COUPLER | 89BE1 | EARTH SWITCH OPEN / CLOSE | DPS | STTS
7 | ABC | BUS COUPLER | 89BE2 | EARTH SWITCH OPEN / CLOSE | DPS | STTS
8 | ABC | BUS COUPLER | BCU | BCU IN LOCAL / REMOTE | DPS | BCUR
220 KV TRANSFER BUS COUPLER (DMT SCHEME)
1 | ABC | TRANSFER BUS COUPLER | CB | CB OPEN / CLOSE | DPS | STTS
2 | ABC | TRANSFER BUS COUPLER | CB | CB R-PH OPEN / CLOSE | DPS | STTR
3 | ABC | TRANSFER BUS COUPLER | CB | CB Y-PH OPEN / CLOSE | DPS | STTY
4 | ABC | TRANSFER BUS COUPLER | CB | CB B-PH OPEN / CLOSE | DPS | STTB
5 | ABC | TRANSFER BUS COUPLER | 89A | ISOLATOR OPEN / CLOSE | DPS | STTS
6 | ABC | TRANSFER BUS COUPLER | 89B | ISOLATOR OPEN / CLOSE | DPS | STTS
7 | ABC | TRANSFER BUS COUPLER | 89T | ISOLATOR OPEN / CLOSE | DPS | STTS
8 | ABC | TRANSFER BUS COUPLER | 89AE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
9 | ABC | TRANSFER BUS COUPLER | 89TE1 | EARTH SWITCH OPEN / CLOSE | DPS | STTS
10 | ABC | TRANSFER BUS COUPLER | 89TE2 | EARTH SWITCH OPEN / CLOSE | DPS | STTS
11 | ABC | TRANSFER BUS COUPLER | BCU | BCU IN LOCAL / REMOTE | DPS | BCUR
12 | ABC | TRANSFER BUS COUPLER | CB | AUTO RECLOSE IN AUTO / NONAUTO | DPS | ARNA
132 KV ICT (SINGLE MAIN AND TRANSFER)
1 | ABC | ICT | CB | CB OPEN / CLOSE | DPS | STTS
2 | ABC | ICT | 89A | ISOLATOR OPEN/CLOSE | DPS | STTS
3 | ABC | ICT | 89L | ISOLATOR OPEN/CLOSE | DPS | STTS
4 | ABC | ICT | 89T | ISOLATOR OPEN / CLOSE | DPS | STTS
5 | ABC | ICT | BCU | BCU IN LOCAL / REMOTE | DPS | BCUR
132 KV BUS COUPLER (SINGLE MAIN AND TRANSFER)
1 | ABC | BUS COUPLER | CB | CB OPEN / CLOSE | DPS | STTS
2 | ABC | BUS COUPLER | 89A | ISOLATOR OPEN/CLOSE | DPS | STTS
3 | ABC | BUS COUPLER | 89L | ISOLATOR OPEN/CLOSE | DPS | STTS
4 | ABC | BUS COUPLER | 89T | ISOLATOR OPEN / CLOSE | DPS | STTS
5 | ABC | BUS COUPLER | BCU | BCU IN LOCAL / REMOTE | DPS | BCUR
132 KV LINE FEEDER (SINGLE MAIN AND TRANSFER)
1 | ABC | LINE FEEDER | CB | CB OPEN / CLOSE | DPS | STTS
2 | ABC | LINE FEEDER | 89A | ISOLATOR OPEN/CLOSE | DPS | STTS
3 | ABC | LINE FEEDER | 89T | ISOLATOR OPEN/CLOSE | DPS | STTS
4 | ABC | LINE FEEDER | 89L | EARTH SWITCH OPEN / CLOSE | DPS | STTS
5 | ABC | LINE FEEDER | 89LE | EARTH SWITCH OPEN / CLOSE | DPS | STTS
6 | ABC | LINE FEEDER | BCU | BCU IN LOCAL / REMOTE | DPS | BCUR
FIXED SERIES CAPACITOR (FSC)
1 | ABC | FSC | 52BBR | BPCB OPEN/CLOSE STATUS | DPS
2 | ABC | FSC | 52BBR-RPh | BPCB R PHASE OPEN/CLOSE STATUS | DPS
3 | ABC | FSC | 52BBR-YPh | BPCB Y PHASE OPEN/CLOSE STATUS | DPS
4 | ABC | FSC | 52BBR-Bph | BPCB B PHASE OPEN/CLOSE STATUS | DPS
5 | ABC | FSC | 89MBS | BYPASS MBS ISOLATOR OPEN/CLOSE STATUS | DPS
6 | ABC | FSC | 89DS1 | ISOLATOR 1 OPEN/CLOSE STATUS | DPS
7 | ABC | FSC | 89DS2 | ISOLATOR 2 OPEN/CLOSE STATUS | DPS
8 | ABC | FSC | 89ES1 | EARTH SWITCH 1 OPEN/CLOSE STATUS | DPS
9 | ABC | FSC | 89ES2 | EARTH SWITCH 2 OPEN/CLOSE STATUS | DPS
AUXILLIARY SYSTEM
1 | 220VDC | BCHRG | BATCHRG220V-1 | 220V BATTERY CHARGER -1 ON FLOAT MODE | DPS
2 | 220VDC | BCHRG | BATCHRG220V-1 | 220V BATTERY CHARGER -1 ON BOOST MODE | DPS
3 | 220VDC | BCHRG | BATCHRG220V-2 | 220V BATTERY CHARGER -2 ON FLOAT MODE | DPS
4 | 220VDC | BCHRG | BATCHRG220V-2 | 220V BATTERY CHARGER -2 ON BOOST MODE | DPS
5 | 48 VDC | BCHRG | BATCHRG48V-1 | 48V BATTERY CHARGER -1 ON FLOAT MODE | DPS
6 | 48 VDC | BCHRG | BATCHRG48V-1 | 48V BATTERY CHARGER -1 ON BOOST MODE | DPS
7 | 48 VDC | BCHRG | BATCHRG48V-2 | 48V BATTERY CHARGER -2 ON FLOAT MODE | DPS
8 | 48 VDC | BCHRG | BATCHRG48V-2 | 48V BATTERY CHARGER -2 ON BOOST MODE | DPS
9 | 415 V | FP | EPUMP | HVW ELECTRIC PUMP ACB ON | DPS
10 | 415 V | FP | EPUMP | HVW ELECTRIC PUMP ACB OFF | DPS
11 | 415 V | DG Set | DGSET-1 | DG SET BREAKER OPEN | DPS
12 | 415 V | DG Set | DGSET-1 | DG SET BREAKER CLOSE | DPS
13 | 415 V | LTSUP | ACDB-1 | ACDB INCOMER-1 OPEN | DPS
14 | 415 V | LTSUP | ACDB-1 | ACDB INCOMER-1 CLOSE | DPS
15 | 415 V | LTSUP | ACDB-BC | ACDB BUS COUPLER OPEN | DPS
16 | 415 V | LTSUP | ACDB-BC | ACDB BUS COUPLER CLOSE | DPS
17 | 415 V | LTSUP | ACDB-2 | ACDB INCOMER-2 OPEN | DPS
18 | 415 V | LTSUP | ACDB-2 | ACDB INCOMER-2 CLOSE | DPS
19 | 415 V | LTSUP | MSB-1 | MSB-1 CB OPEN | DPS
20 | 415 V | LTSUP | MSB-1 | MSB-1 CB CLOSE | DPS
21 | 415 V | LTSUP | MSB_BC | MSB BUS COUPLER BREAKER OPEN | DPS
22 | 415 V | LTSUP | MSB_BC | MSB BUS COUPLER BREAKER CLOSE | DPS
23 | 415 V | LTSUP | MSB-2 | MSB-2 CB OPEN | DPS
24 | 415 V | LTSUP | MSB-2 | MSB- 2 CB CLOSE | DPS
25 | 33 KV | LTSUP | TERTIARY | EARTH SWITCH OPEN | DPS
26 | 33 KV | LTSUP | TERTIARY | EARTH SWITCH CLOSE | DPS
27 | 33 KV | LTSUP | TERTIARY | CB OPEN | DPS
28 | 33 KV | LTSUP | TERTIARY | CB CLOSE | DPS
29 | 33 KV | LTSUP | TERTIARY | ISO OPEN | DPS
30 | 33 KV | LTSUP | TERTIARY | ISO CLOSE | DPS
STATCOM (SIEMENS)
1 | ABC | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-89A | HV Main Bay 89A Isolator Open | DPS
2 | ABC | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-89A | HV Main Bay 89A Isolator Close | DPS
3 | ABC | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-89B | HV Main Bay 89B Isolator Open | DPS
4 | ABC | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-89B | HV Main Bay 89B Isolator Close | DPS
5 | ABC | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-89AE | HV Main Bay 89AE Earth Switch Open | DPS
6 | ABC | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-89AE | HV Main Bay 89AE Earth Switch Close | DPS
7 | ABC | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-89BE | HV Main Bay 89BE Earth Switch Open | DPS
8 | ABC | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-89BE | HV Main Bay 89BE Earth Switch Close | DPS
9 | ABC | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-52 | HV Main Bay CB Open | DPS
10 | ABC | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-52 | HV Main Bay CB Close | DPS
11 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q2 R PH | ISOLATOR OPEN | DPS
12 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q2 R PH | ISOLATOR CLOSED | DPS
13 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q2 Y PH | ISOLATOR OPEN | DPS
14 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q2 Y PH | ISOLATOR CLOSED | DPS
15 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q2 B PH | ISOLATOR OPEN | DPS
16 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q2 B PH | ISOLATOR CLOSED | DPS
17 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q3 R PH | ISOLATOR OPEN | DPS
18 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q3 R PH | ISOLATOR CLOSED | DPS
19 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q3 Y PH | ISOLATOR OPEN | DPS
20 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q3 Y PH | ISOLATOR CLOSED | DPS
21 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q3 B PH | ISOLATOR OPEN | DPS
22 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q3 B PH | ISOLATOR CLOSED | DPS
23 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q51 R PH | EARTH SWITCH OPEN | DPS
24 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q51 R PH | EARTH SWITCH CLOSED | DPS
25 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q51 Y PH | EARTH SWITCH OPEN | DPS
26 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q51 Y PH | EARTH SWITCH CLOSED | DPS
27 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q51 B PH | EARTH SWITCH OPEN | DPS
28 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q51 B PH | EARTH SWITCH CLOSED | DPS
29 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q52 | EARTH SWITCH OPEN | DPS
30 | ABC | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q52 | EARTH SWITCH CLOSED | DPS
31 | ABC | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-89A | ISOLATOR OPEN | DPS
32 | ABC | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-89A | ISOLATOR CLOSE | DPS
33 | ABC | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-89B | ISOLATOR OPEN | DPS
34 | ABC | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-89B | ISOLATOR CLOSE | DPS
35 | ABC | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-89AE | EARTH SWITCH OPEN | DPS
36 | ABC | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-89AE | EARTH SWITCH CLOSE | DPS
37 | ABC | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-89BE | EARTH SWITCH OPEN | DPS
38 | ABC | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-89BE | EARTH SWITCH CLOSE | DPS
39 | ABC | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-52 | CB OPEN | DPS
40 | ABC | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-52 | CB CLOSE | DPS
41 | ABC | FUTURE |  | HV Future Bay 89A Isolator Open | DPS
42 | ABC | FUTURE |  | HV Future Bay 89A Isolator Close | DPS
43 | ABC | FUTURE |  | HV Future Bay 89AE Earth Switcr Open | DPS
44 | ABC | FUTURE |  | HV Future Bay 89AE Earth Switcr Close | DPS
45 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q1 R PH | MV ISOLATOR OPEN | DPS
46 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q1 R PH | MV ISOLATOR CLOSED | DPS
47 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q1 Y PH | MV ISOLATOR OPEN | DPS
48 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q1 Y PH | MV ISOLATOR CLOSED | DPS
49 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q1 B PH | MV ISOLATOR OPEN | DPS
50 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q1 B PH | MV ISOLATOR CLOSED | DPS
51 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q2 R PH | MV ISOLATOR OPEN | DPS
52 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q2 R PH | MV ISOLATOR CLOSED | DPS
53 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q2 Y PH | MV ISOLATOR OPEN | DPS
54 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q2 Y PH | MV ISOLATOR CLOSED | DPS
55 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q2 B PH | MV ISOLATOR OPEN | DPS
56 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q2 B PH | MV ISOLATOR CLOSED | DPS
57 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q12 R PH | MV ISOLATOR OPEN | DPS
58 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q12 R PH | MV ISOLATOR CLOSED | DPS
59 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q12 Y PH | MV ISOLATOR OPEN | DPS
60 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q12 Y PH | MV ISOLATOR CLOSED | DPS
61 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q12 B PH | MV ISOLATOR OPEN | DPS
62 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q12 B PH | MV ISOLATOR CLOSED | DPS
63 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q13 R PH | MV ISOLATOR OPEN | DPS
64 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q13 R PH | MV ISOLATOR CLOSED | DPS
65 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q13 Y PH | MV ISOLATOR OPEN | DPS
66 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q13 Y PH | MV ISOLATOR CLOSED | DPS
67 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q13 B PH | MV ISOLATOR OPEN | DPS
68 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q13 B PH | MV ISOLATOR CLOSED | DPS
69 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER J01-Q52 | BUSBAR EARTHING SWITCH OPEN | DPS
70 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER J01-Q52 | BUSBAR EARTHING SWITCH CLOSED | DPS
71 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER J01-Q0 | AUXILIARY SUPPLY CIRCUIT BREAKER OPEN | DPS
72 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER J01-Q0 | AUXILIARY SUPPLY CIRCUIT BREAKER CLOSED | DPS
73 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER J01-Q1 | AUXILIARY SUPPLY ISOLATOR OPEN | DPS
74 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER J01-Q1 | AUXILIARY SUPPLY ISOLATOR CLOSED | DPS
75 | J11 | STATCOM VSC-1 BAY | MSC-2 MV-J32 | CIRCUIT BREAKER OPEN | DPS
76 | J11 | STATCOM VSC-1 BAY | VSC-1 J11 Q0 | CIRCUIT BREAKER CLOSED | DPS
77 | J11 | STATCOM VSC-1 BAY | VSC-1 J11 Q5 | EARTHING SWITCH OPEN | DPS
78 | J11 | STATCOM VSC-1 BAY | VSC-1 J11 Q5 | EARTHING SWITCH CLOSED | DPS
79 | J11 | STATCOM VSC-1 BAY | VSC-1 J11 Q1 | ISOLATOR SWITCH OPEN | DPS
80 | J11 | STATCOM VSC-1 BAY | VSC-1 J11 Q1 | ISOLATOR SWITCH CLOSED | DPS
81 | J12 | STATCOM VSC-2 BAY | VSC-2 J12 Q0 | CIRCUIT BREAKER OPEN | DPS
82 | J12 | STATCOM VSC-2 BAY | VSC-2 J12 Q0 | CIRCUIT BREAKER CLOSED | DPS
83 | J12 | STATCOM VSC-2 BAY | VSC-2 J12 Q5 | EARTHING SWITCH OPEN | DPS
84 | J12 | STATCOM VSC-2 BAY | VSC-2 J12 Q5 | EARTHING SWITCH CLOSED | DPS
85 | J12 | STATCOM VSC-2 BAY | VSC-2 J12 Q1 | ISOLATOR SWITCH OPEN | DPS
86 | J12 | STATCOM VSC-2 BAY | VSC-2 J12 Q1 | ISOLATOR SWITCH CLOSED | DPS
87 | J21 | STATCOM MSR-1 BAY | MSR-1 J21 Q0 | CIRCUIT BREAKER OPEN | DPS
88 | J21 | STATCOM MSR-1 BAY | MSR-1 J21 Q0 | CIRCUIT BREAKER CLOSED | DPS
89 | J21 | STATCOM MSR-1 BAY | MSR-1 J21 Q1 | ISOLATOR SWITCH OPEN | DPS
90 | J21 | STATCOM MSR-1 BAY | MSR-1 J21 Q1 | ISOLATOR SWITCH CLOSED | DPS
91 | J21 | STATCOM MSR-1 BAY | MSR-1 J21 Q5 | EARTHING SWITCH OPEN | DPS
92 | J21 | STATCOM MSR-1 BAY | MSR-1 J21 Q5 | EARTHING SWITCH CLOSED | DPS
93 | J22 | STATCOM MSR-2 BAY | MSR-2 J22 Q0 | CIRCUIT BREAKER OPEN | DPS
94 | J22 | STATCOM MSR-2 BAY | MSR-2 J22 Q0 | CIRCUIT BREAKER CLOSED | DPS
95 | J22 | STATCOM MSR-2 BAY | MSR-2 J22 Q1 | ISOLATOR SWITCH OPEN | DPS
96 | J22 | STATCOM MSR-2 BAY | MSR-2 J22 Q1 | ISOLATOR SWITCH CLOSED | DPS
97 | J22 | STATCOM MSR-2 BAY | MSR-2 J22 Q5 | EARTHING SWITCH OPEN | DPS
98 | J22 | STATCOM MSR-2 BAY | MSR-2 J22 Q5 | EARTHING SWITCH CLOSED | DPS
99 | J31 | STATCOM MSC-1 BAY | MSC-1 J31 Q0 | CIRCUIT BREAKER OPEN | DPS
100 | J31 | STATCOM MSC-1 BAY | MSC-1 J31 Q0 | CIRCUIT BREAKER CLOSED | DPS
101 | J31 | STATCOM MSC-1 BAY | MSC-1 J31 Q1 | ISOLATOR SWITCH OPEN | DPS
102 | J31 | STATCOM MSC-1 BAY | MSC-1 J31 Q1 | ISOLATOR SWITCH CLOSED | DPS
103 | J31 | STATCOM MSC-1 BAY | MSC-1 J31 Q5 | EARTHING SWITCH OPEN | DPS
104 | J31 | STATCOM MSC-1 BAY | MSC-1 J31 Q5 | EARTHING SWITCH CLOSED | DPS
105 | J32 | STATCOM MSC-2 BAY | MSC-2 J32 Q0 | CIRCUIT BREAKER OPEN | DPS
106 | J32 | STATCOM MSC-2 BAY | MSC-2 J32 Q0 | CIRCUIT BREAKER CLOSED | DPS
107 | J32 | STATCOM MSC-2 BAY | MSC-2 J32 Q1 | ISOLATOR SWITCH OPEN | DPS
108 | J32 | STATCOM MSC-2 BAY | MSC-2 J32 Q1 | ISOLATOR SWITCH CLOSED | DPS
109 | J32 | STATCOM MSC-2 BAY | MSC-2 J32 Q5 | EARTHING SWITCH OPEN | DPS
110 | J32 | STATCOM MSC-2 BAY | MSC-2 J32 Q5 | EARTHING SWITCH CLOSED | DPS
111 | STATCOM | STATCOM | STATCOM OPERATION | STATCOM AUTOMATIC CONTROL STATUS | DPS
112 | STATCOM | STATCOM | STATCOM OPERATION | STATCOM MANUAL CONTROL STATUS | DPS
113 | STATCOM | STATCOM | STATCOM OPERATION | REACTIVE POWER CONTROL MODE ENABLE | DPS
114 | STATCOM | STATCOM | STATCOM OPERATION | REACTIVE POWER CONTROL MODE DISABLE | DPS
115 | STATCOM | STATCOM | STATCOM OPERATION | GAIN ADJUSTMENT AUTOMATIC | DPS
116 | STATCOM | STATCOM | STATCOM OPERATION | GAIN ADJUSTMENT MANUAL | DPS
117 | STATCOM | STATCOM | STATCOM OPERATION | NPS ON | DPS
118 | STATCOM | STATCOM | STATCOM OPERATION | NPS OFF | DPS
119 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICES HV AUTOMATIC | DPS
120 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICES HV OFF | DPS
121 | STATCOM | STATCOM | STATCOM OPERATION | AUTO-RESTART ON SELECTED | DPS
122 | STATCOM | STATCOM | STATCOM OPERATION | AUTO-RESTART OFF SELECTED | DPS
123 | STATCOM | STATCOM | STATCOM OPERATION | SELECT SYSTEM 1 ACTIVE | DPS
124 | STATCOM | STATCOM | STATCOM OPERATION | SELECT SYSTEM 2 ACTIVE | DPS
125 | STATCOM | STATCOM | STATCOM OPERATION | UNEQUAL LOAD SHARING MODE ON | DPS
126 | STATCOM | STATCOM | STATCOM OPERATION | UNEQUAL LOAD SHARING MODE OFF | DPS
127 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICE LV1 PSD BYPASS | DPS
128 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICE LV1 PSD ON | DPS
129 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICE LV2 PSD BYPASS | DPS
130 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICE LV2 PSD ON | DPS
131 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICE LV3 PSD BYPASS | DPS
132 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICE LV3 PSD ON | DPS
133 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICE LV4 PSD BYPASS | DPS
134 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICE LV4 PSD ON | DPS
135 | STATCOM AUX | STATCOM AUX | MSB-1 | A-AC SUPPLY -CB1 OPEN POSITION | DPS
136 | STATCOM AUX | STATCOM AUX | MSB-1 | A-AC SUPPLY -CB1 CLOSED POSITION | DPS
137 | STATCOM AUX | STATCOM AUX | MSB-2 | B-AC SUPPLY -CB2 OPEN POSITION | DPS
138 | STATCOM AUX | STATCOM AUX | MSB-2 | B-AC SUPPLY -CB2 CLOSED POSITION | DPS
139 | STATCOM AUX | STATCOM AUX | MSB-BC | AC TIE-BREAKER -CB3 OPEN POSITION | DPS
140 | STATCOM AUX | STATCOM AUX | MSB-BC | AC TIE-BREAKER -CB3 CLOSED POSITION | DPS
141 | STATCOM AUX | STATCOM AUX | ACDB-2A | ACDB- 2A AC SUPPLY - INCOMER -1 CB OPEN POSITION | DPS
142 | STATCOM AUX | STATCOM AUX | ACDB-2A | ACDB- 2A AC SUPPLY -- INCOMER -1 CB CLOSED POSITION | DPS
143 | STATCOM AUX | STATCOM AUX | ACDB-2A | ACDB- 2A AC SUPPLY - INCOMER -2 CB OPEN POSITION | DPS
144 | STATCOM AUX | STATCOM AUX | ACDB-2A | ACDB- 2A AC SUPPLY -- INCOMER -2 CB CLOSED POSITION | DPS
145 | STATCOM AUX | STATCOM AUX | ACDB-2A | ACDB- 2A AC SUPPLY - DG INCOMER CB OPEN POSITION | DPS
146 | STATCOM AUX | STATCOM AUX | ACDB-2A | ACDB- 2A AC SUPPLY -- DG INCOMER CB CLOSED POSITION | DPS
147 | STATCOM AUX | STATCOM AUX | ACDB-2A | ACDB- 2A AC TIE-BREAKER -CB OPEN POSITION | DPS
148 | STATCOM AUX | STATCOM AUX | ACDB-2A | ACDB- 2A AC TIE-BREAKER -CB CLOSED POSITION | DPS
STATCOM (RXPE)
1 | ABC | FUTURE BAY | 89A | HV Future Bay 89A Isolator Open | DPS
2 | ABC | FUTURE BAY | 89A | HV Future Bay 89A Isolator Close | DPS
3 | ABC | FUTURE BAY | 89AE | HV Future Bay 89AE Earth Switch Open | DPS
4 | ABC | FUTURE BAY | 89AE | HV Future Bay 89AE Earth Switch Close | DPS
5 | ABC | FUTURE& COUPLING T/F-1 TIE | 52 | CB R-PHASE OPEN | DPS
6 | ABC | FUTURE& COUPLING T/F-1 TIE | 52 | CB R-PHASE CLOSE | DPS
7 | ABC | FUTURE& COUPLING T/F-1 TIE | 52 | CB Y-PHASE OPEN | DPS
8 | ABC | FUTURE& COUPLING T/F-1 TIE | 52 | CB Y-PHASE CLOSE | DPS
9 | ABC | FUTURE& COUPLING T/F-1 TIE | 52 | CB B-PHASE OPEN | DPS
10 | ABC | FUTURE& COUPLING T/F-1 TIE | 52 | CB B-PHASE CLOSE | DPS
11 | ABC | FUTURE& COUPLING T/F-1 TIE | 52 | CB OPEN | DPS
12 | ABC | FUTURE& COUPLING T/F-1 TIE | 52 | CB CLOSE | DPS
13 | ABC | FUTURE& COUPLING T/F-1 TIE | 89A | ISOLATOR OPEN | DPS
14 | ABC | FUTURE& COUPLING T/F-1 TIE | 89A | ISOLATOR CLOSE | DPS
15 | ABC | FUTURE& COUPLING T/F-1 TIE | 89AE | EARTH SWITCH OPEN | DPS
16 | ABC | FUTURE& COUPLING T/F-1 TIE | 89AE | EARTH SWITCH CLOSE | DPS
17 | ABC | FUTURE& COUPLING T/F-1 TIE | 89B | ISOLATOR OPEN | DPS
18 | ABC | FUTURE& COUPLING T/F-1 TIE | 89B | ISOLATOR CLOSE | DPS
19 | ABC | FUTURE& COUPLING T/F-1 TIE | BCU | BCU IN LOCAL | DPS
20 | ABC | FUTURE& COUPLING T/F-1 TIE | BCU | BCU IN REMOTE | DPS
21 | ABC | COUPLING TRANSFORMER (HV) | 52 | CB OPEN | DPS
22 | ABC | COUPLING TRANSFORMER (HV) | 52 | CB CLOSE | DPS
23 | ABC | COUPLING TRANSFORMER (HV) | 89A | ISOLATOR OPEN | DPS
24 | ABC | COUPLING TRANSFORMER (HV) | 89A | ISOLATOR CLOSE | DPS
25 | ABC | COUPLING TRANSFORMER (HV) | 89AE | EARTH SWITCH OPEN | DPS
26 | ABC | COUPLING TRANSFORMER (HV) | 89AE | EARTH SWITCH CLOSE | DPS
27 | ABC | COUPLING TRANSFORMER (HV) | 89B | ISOLATOR OPEN | DPS
28 | ABC | COUPLING TRANSFORMER (HV) | 89B | ISOLATOR CLOSE | DPS
29 | ABC | COUPLING TRANSFORMER (HV) | 89BE | EARTH SWITCH OPEN | DPS
30 | ABC | COUPLING TRANSFORMER (HV) | 89BE | EARTH SWITCH CLOSE | DPS
31 | ABC | COUPLING TRANSFORMER (HV) | 89TR | ISOLATOR OPEN | DPS
32 | ABC | COUPLING TRANSFORMER (HV) | 89TR | ISOLATOR CLOSE | DPS
33 | ABC | COUPLING TRANSFORMER (HV) | 89TRE | EARTH SWITCH OPEN | DPS
34 | ABC | COUPLING TRANSFORMER (HV) | 89TRE | EARTH SWITCH CLOSE | DPS
35 | ABC | COUPLING TRANSFORMER (HV) | 89TSR | ISOLATOR OPEN | DPS
36 | ABC | COUPLING TRANSFORMER (HV) | 89TSR | ISOLATOR CLOSE | DPS
37 | ABC | COUPLING TRANSFORMER (HV) | 89TY | ISOLATOR OPEN | DPS
38 | ABC | COUPLING TRANSFORMER (HV) | 89TY | ISOLATOR CLOSE | DPS
39 | ABC | COUPLING TRANSFORMER (HV) | 89TYE | EARTH SWITCH OPEN | DPS
40 | ABC | COUPLING TRANSFORMER (HV) | 89TYE | EARTH SWITCH CLOSE | DPS
41 | ABC | COUPLING TRANSFORMER (HV) | 89TSY | ISOLATOR OPEN | DPS
42 | ABC | COUPLING TRANSFORMER (HV) | 89TSY | ISOLATOR CLOSE | DPS
43 | ABC | COUPLING TRANSFORMER (HV) | 89TB | ISOLATOR OPEN | DPS
44 | ABC | COUPLING TRANSFORMER (HV) | 89TB | ISOLATOR CLOSE | DPS
45 | ABC | COUPLING TRANSFORMER (HV) | 89TBE | EARTH SWITCH OPEN | DPS
46 | ABC | COUPLING TRANSFORMER (HV) | 89TBE | EARTH SWITCH CLOSE | DPS
47 | ABC | COUPLING TRANSFORMER (HV) | 89TSB | ISOLATOR OPEN | DPS
48 | ABC | COUPLING TRANSFORMER (HV) | 89TSB | ISOLATOR CLOSE | DPS
49 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TR1 | ISOLATOR OPEN/CLOSE | DPS
50 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TR2 | ISOLATOR OPEN/CLOSE | DPS
51 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TY1 | ISOLATOR OPEN/CLOSE | DPS
52 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TY2 | ISOLATOR OPEN/CLOSE | DPS
53 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TB1 | ISOLATOR OPEN/CLOSE | DPS
54 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TB2 | ISOLATOR OPEN/CLOSE | DPS
55 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSR1 | ISOLATOR OPEN/CLOSE | DPS
56 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSR2 | ISOLATOR OPEN/CLOSE | DPS
57 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSY1 | ISOLATOR OPEN/CLOSE | DPS
58 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSY2 | ISOLATOR OPEN/CLOSE | DPS
59 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSB1 | ISOLATOR OPEN/CLOSE | DPS
60 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSB2 | ISOLATOR OPEN/CLOSE | DPS
61 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TR1E | EARTH SWITCH OPEN/CLOSE | DPS
62 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TR2E | EARTH SWITCH OPEN/CLOSE | DPS
63 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TY1E | EARTH SWITCH OPEN/CLOSE | DPS
64 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TY2E | EARTH SWITCH OPEN/CLOSE | DPS
65 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TB1E | EARTH SWITCH OPEN/CLOSE | DPS
66 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TB2E | EARTH SWITCH OPEN/CLOSE | DPS
67 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSR1E | EARTH SWITCH OPEN/CLOSE | DPS
68 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSR2E | EARTH SWITCH OPEN/CLOSE | DPS
69 | 38.5KV | MV BUS BAR | 60089E | EARTH SWITCH OPEN/CLOSE | DPS
70 | 38.5KV | STATCOM- 1 | STATCOM VSC 60152 | CB OPEN/CLOSE | DPS
71 | 38.5KV | STATCOM- 1 | STATCOM VSC 60152BP | BYPASS CB OPEN/CLOSE | DPS
72 | 38.5KV | STATCOM- 1 | STATCOM VSC 60189A | ISOLATOR OPEN/CLOSE | DPS
73 | 38.5KV | STATCOM- 1 | STATCOM VSC 60189AE | EARTH SWITCH OPEN/CLOSE | DPS
74 | 38.5KV | STATCOM- 2 | STATCOM VSC 60252 | CB OPEN/CLOSE | DPS
75 | 38.5KV | STATCOM- 2 | STATCOM VSC 60252BP | BYPASS CB OPEN/CLOSE | DPS
76 | 38.5KV | STATCOM- 2 | STATCOM VSC 60289A | ISOLATOR OPEN/CLOSE | DPS
77 | 38.5KV | STATCOM- 2 | STATCOM VSC 60289AE | EARTH SWITCH OPEN/CLOSE | DPS
78 | 38.5KV | MSC | 60352 | CB OPEN/CLOSE | DPS
79 | 38.5KV | MSC | 60389A | ISOLATOR OPEN/CLOSE | DPS
80 | 38.5KV | MSC | 60389AE | EARTH SWITCH OPEN/CLOSE | DPS
81 | 38.5KV | MSR- 1 | 60452 | CB OPEN/CLOSE | DPS
82 | 38.5KV | MSR- 1 | 60489A | ISOLATOR OPEN/CLOSE | DPS
83 | 38.5KV | MSR- 1 | 60489AE | EARTH SWITCH OPEN/CLOSE | DPS
84 | 38.5KV | MSR- 2 | 60552 | CB OPEN/CLOSE | DPS
85 | 38.5KV | MSR- 2 | 60589A | ISOLATOR OPEN/CLOSE | DPS
86 | 38.5KV | MSR- 2 | 60589AE | EARTH SWITCH OPEN/CLOSE | DPS
87 | 38.5KV | AUX T/F | 60652 | CB OPEN/CLOSE | DPS
88 | 38.5KV | AUX T/F | 60689A | ISOLATOR OPEN/CLOSE | DPS
89 | 38.5KV | AUX T/F | 60689AE | EARTH SWITCH OPEN/CLOSE | DPS
90 | 33KV | AUX | TERTIARY 33KV ISOLATOR | ISOLATOR OPEN/CLOSE | DPS
91 | 33KV | AUX | TERTIARY 33KV CB | CB OPEN/CLOSE | DPS
92 | 415 V | AUX | MSB INCOMER-1 | INCOMER-1 ON/OFF | DPS
93 | 415 V | AUX | MSB BUS COUPLER | BUS COUPLER ON/OFF | DPS
94 | 415 V | AUX | MSB INCOMER-2 | INCOMER-2 ON/OFF | DPS
95 | 415 V | AUX | ACDB INCOMER-1 | INCOMER-1 ON/OFF | DPS
96 | 415 V | AUX | ACDB BUS COUPLER | BUS COUPLER ON/OFF | DPS
97 | 415 V | AUX | ACDB INCOMER-2 | INCOMER-2 ON/OFF | DPS
98 | 415 V | AUX | DG SET | DG INCOMER CB ON/OFF | DPS
STATCOM (HYOSUNG)
1 | ABC | COUPLING TRANSFORMER (HV) | 52 | CB OPEN/CLOSE | DPS
2 | ABC | COUPLING TRANSFORMER (HV) | 89A | ISOLATOR OPEN/CLOSE | DPS
3 | ABC | COUPLING TRANSFORMER (HV) | 89AE | EARTH SWITCH OPEN/CLOSE | DPS
4 | ABC | COUPLING TRANSFORMER (HV) | 89B | ISOLATOR OPEN/CLOSE | DPS
5 | ABC | COUPLING TRANSFORMER (HV) | 89BE | EARTH SWITCH OPEN/CLOSE | DPS
6 | ABC | COUPLING TRANSFORMER (HV) | 89TR | ISOLATOR OPEN/CLOSE | DPS
7 | ABC | COUPLING TRANSFORMER (HV) | 89TRE | EARTH SWITCH OPEN/CLOSE | DPS
8 | ABC | COUPLING TRANSFORMER (HV) | 89TSR | ISOLATOR OPEN/CLOSE | DPS
9 | ABC | COUPLING TRANSFORMER (HV) | 89TY | ISOLATOR OPEN/CLOSE | DPS
10 | ABC | COUPLING TRANSFORMER (HV) | 89TYE | EARTH SWITCH OPEN/CLOSE | DPS
11 | ABC | COUPLING TRANSFORMER (HV) | 89TSY | ISOLATOR OPEN/CLOSE | DPS
12 | ABC | COUPLING TRANSFORMER (HV) | 89TB | ISOLATOR OPEN/CLOSE | DPS
13 | ABC | COUPLING TRANSFORMER (HV) | 89TBE | EARTH SWITCH OPEN/CLOSE | DPS
14 | ABC | COUPLING TRANSFORMER (HV) | 89TSB | ISOLATOR OPEN/CLOSE | DPS
15 | ABC | COUPLING TRANSFORMER (HV) | 89TSBE | EARTH SWITCH OPEN/CLOSE | DPS
16 | 20KV | COUPLING TRANSFORMER (MV) | 89TR | ISOLATOR OPEN/CLOSE | DPS
17 | 20KV | COUPLING TRANSFORMER (MV) | 89TY | ISOLATOR OPEN/CLOSE | DPS
18 | 20KV | COUPLING TRANSFORMER (MV) | 89TB | ISOLATOR OPEN/CLOSE | DPS
19 | 20KV | COUPLING TRANSFORMER (MV) | 89TSR | ISOLATOR OPEN/CLOSE | DPS
20 | 20KV | COUPLING TRANSFORMER (MV) | 89TSY | ISOLATOR OPEN/CLOSE | DPS
21 | 20KV | COUPLING TRANSFORMER (MV) | 89TSB | ISOLATOR OPEN/CLOSE | DPS
22 | 20KV | COUPLING TRANSFORMER (MV) | 89TER | EARTH SWITCH OPEN/CLOSE | DPS
23 | 20KV | COUPLING TRANSFORMER (MV) | 89TEY | EARTH SWITCH OPEN/CLOSE | DPS
24 | 20KV | COUPLING TRANSFORMER (MV) | 89TEB | EARTH SWITCH OPEN/CLOSE | DPS
25 | 20KV | COUPLING TRANSFORMER (MV) | TSER | EARTH SWITCH OPEN/CLOSE | DPS
26 | 20KV | STATCOM-1 | VSC-1 52 | CB OPEN/CLOSE | DPS
27 | 20KV | STATCOM-1 | VSC-1 89A | ISOLATOR OPEN/CLOSE | DPS
28 | 20KV | STATCOM-1 | VSC-1 89AE | EARTH SWITCH OPEN/CLOSE | DPS
29 | 20KV | STATCOM-1 | VSC-1 89B | ISOLATOR OPEN/CLOSE | DPS
30 | 20KV | STATCOM-1 | VSC-1 89BE1 | EARTH SWITCH OPEN/CLOSE | DPS
31 | 20KV | STATCOM-1 | VSC-1 89BE2 | EARTH SWITCH OPEN/CLOSE | DPS
32 | 20KV | STATCOM-2 | VSC-2 52 | CB OPEN/CLOSE | DPS
33 | 20KV | STATCOM-2 | VSC-2 89A | ISOLATOR OPEN/CLOSE | DPS
34 | 20KV | STATCOM-2 | VSC-2 89AE | EARTH SWITCH OPEN/CLOSE | DPS
35 | 20KV | STATCOM-2 | VSC-2 89B | ISOLATOR OPEN/CLOSE | DPS
36 | 20KV | STATCOM-2 | VSC-2 89BE1 | EARTH SWITCH OPEN/CLOSE | DPS
37 | 20KV | STATCOM-2 | VSC-2 89BE2 | EARTH SWITCH OPEN/CLOSE | DPS
38 | 20KV | GND T/F | 89 | ISOLATOR OPEN/CLOSE | DPS
39 | 20KV | GND T/F | 89E | EARTH SWITCH OPEN/CLOSE | DPS
40 | 20KV | BUS PT | 89E1 | EARTH SWITCH OPEN/CLOSE | DPS
41 | 20KV | BUS PT | 89 | ISOLATOR OPEN/CLOSE | DPS
42 | 20KV | BUS PT | 89E2 | EARTH SWITCH OPEN/CLOSE | DPS
43 | 20KV | AUX.T/F | 89 | ISOLATOR OPEN/CLOSE | DPS
44 | 20KV | AUX.T/F | 89E | EARTH SWITCH OPEN/CLOSE | DPS
45 | 20KV | AUX.T/F | 52 | CB OPEN/CLOSE | DPS
46 | 33KV | AUX.T/F | TERTIARY 52 | CB OPEN / CLOSE | DPS
47 | 33KV | AUX.T/F | TERTIARY 89 | 89 OPEN / CLOSE | DPS
48 | 415 V | LTSUP | MSB-1 | INCOMER-1 OPEN/CLOSE | DPS
49 | 415 V | LTSUP | MSB-2 | INCOMER-2 OPEN/CLOSE | DPS
50 | 415 V | LTSUP | MSB-BC | BUS COUPLER OPEN/CLOSE | DPS
51 | 415 V | LTSUP | ACDB-1 | INCOMER-1 OPEN/CLOSE | DPS
52 | 415 V | LTSUP | ACDB-2 | INCOMER-2 OPEN/CLOSE | DPS
53 | 415 V | LTSUP | DGSET | DG SET CB OPEN | DPS
54 | 415 V | LTSUP | ACDB-BC | BUS COUPLER OPEN/CLOSE | DPS
55 | 20KV | MSR-1 | 89A | ISOLATOR OPEN/CLOSE | DPS
56 | 20KV | MSR-1 | 89AE | EARTH SWITCH OPEN/CLOSE | DPS
57 | 20KV | MSR-1 | 52 | CB OPEN/CLOSE | DPS
58 | 20KV | MSR-1 | 89B | ISOLATOR OPEN/CLOSE | DPS
59 | 20KV | MSR-1 | 89BE1 | EARTH SWITCH OPEN/CLOSE | DPS
60 | 20KV | MSR-1 | 89BE2 | EARTH SWITCH OPEN/CLOSE | DPS
61 | 20KV | MSR-2 | 89A | ISOLATOR OPEN/CLOSE | DPS
62 | 20KV | MSR-2 | 89AE | EARTH SWITCH OPEN/CLOSE | DPS
63 | 20KV | MSR-2 | 52 | CB OPEN/CLOSE | DPS
64 | 20KV | MSR-2 | 89B | ISOLATOR OPEN/CLOSE | DPS
65 | 20KV | MSR-2 | 89BE1 | EARTH SWITCH OPEN/CLOSE | DPS
66 | 20KV | MSR-2 | 89BE2 | EARTH SWITCH OPEN/CLOSE | DPS
67 | 20KV | MSC | 89A | ISOLATOR OPEN/CLOSE | DPS
68 | 20KV | MSC | 89AE | EARTH SWITCH OPEN/CLOSE | DPS
69 | 20KV | MSC | 52 | CB OPEN/CLOSE | DPS
70 | 20KV | MSC | 89B | ISOLATOR OPEN/CLOSE | DPS
71 | 20KV | MSC | 89BE1 | EARTH SWITCH OPEN/CLOSE | DPS
72 | 20KV | MSC | 89BE2 | EARTH SWITCH OPEN/CLOSE | DPS
73 | ABC | FUTURE | 89A | ISOLATOR OPEN/CLOSE | DPS
74 | ABC | FUTURE | 89AE | EARTH SWITCH OPEN/CLOSE | DPS
75 | ABC | FUTURE & STATCOM TIE | 52 | CB OPEN/CLOSE | DPS
76 | ABC | FUTURE & STATCOM TIE | 89A | ISOLATOR OPEN/CLOSE | DPS
77 | ABC | FUTURE & STATCOM TIE | 89AE | EARTH SWITCH OPEN/CLOSE | DPS
78 | ABC | FUTURE & STATCOM TIE | 89B | ISOLATOR OPEN/CLOSE | DPS
79 | ABC | FUTURE & STATCOM TIE | 89BE | EARTH SWITCH OPEN/CLOSE | DPS

## DPC (hidden)
Sl.NO | BAY NUM. | BAY NAME | DEVICE ID | SIGNAL DESCRIPTION | SCADA ID | DATA TYPE | REMARK
LINE FEEDER (ONE AND HALF BREAKER SCHEME)
1 | ABC | LINE FEEDER | CB | CB OPEN / CLOSE COMMAND | STTS | DPC
2 | ABC | LINE FEEDER | CB | AUTO RECLOSE TO AUTO / NON-AUTO MODE | ARNA | DPC
3 | ABC | LINE FEEDER | 89A | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
4 | ABC | LINE FEEDER | 89B | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
5 | ABC | LINE FEEDER | 89L | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
SWITCHEABLE LINE REACTOR
1 | ABC | LINE FEEDER WITH SW REACTOR | 52R | CB OPEN/CLOSE COMMAND | STTS | DPC
2 | ABC | LINE FEEDER WITH SW REACTOR | 89RR | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
3 | ABC | LINE FEEDER WITH SW REACTOR | 89RY | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
4 | ABC | LINE FEEDER WITH SW REACTOR | 89RB | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
5 | ABC | LINE FEEDER WITH SW REACTOR | 89RS1R | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
6 | ABC | LINE FEEDER WITH SW REACTOR | 89RS1Y | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
7 | ABC | LINE FEEDER WITH SW REACTOR | 89RS1B | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
NGR
1 | ABC | LINE FEEDER WITH SW REACTOR | NGR | BYPASS CB OPEN / CLOSE COMMAND | STTS | DPC
TIE/ BUS SECTION
1 | ABC | TIE/ BS | CB | CB OPEN / CLOSE / CLOSE COMMAND | STTS | DPC
2 | ABC | TIE/ BS | CB | AUTO RECLOSE TO AUTO / NON-AUTO MODE | ARNA | DPC
3 | ABC | TIE/ BS | 89A | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
4 | ABC | TIE/ BS | 89B | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
FUTURE BAY
1 | ABC | FUTURE LINE | 89A | ISOLATOR OPEN/CLOSE COMMAND | STTS | DPC
765 KV BUS REACTOR (ONE AND HALF BREAKER SCHEME)
1 | ABC | BUS REACTOR | 89A | ISOLATOR OPEN/CLOSE COMMAND | STTS | DPC
2 | ABC | BUS REACTOR | 89B | ISOLATOR OPEN/CLOSE COMMAND | STTS | DPC
3 | ABC | BUS REACTOR | 89RR | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
4 | ABC | BUS REACTOR | 89RY | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
5 | ABC | BUS REACTOR | 89RB | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
6 | ABC | BUS REACTOR | 89RS1R | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
7 | ABC | BUS REACTOR | 89RS1Y | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
8 | ABC | BUS REACTOR | 89RS1B | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
ICT (ONE & HALF BREAKER SCHEME)
1 | ABC | ICT | CB | CB OPEN / CLOSE COMMAND | STTS | DPC
2 | ABC | ICT | 89A | ISOLATOR OPEN/CLOSE COMMAND | STTS | DPC
3 | ABC | ICT | 89B | ISOLATOR OPEN/CLOSE COMMAND | STTS | DPC
4 | ABC | ICT | 89TR | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
5 | ABC | ICT | 89TY | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
6 | ABC | ICT | 89TB | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
7 | ABC | ICT | 89TS1R | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
8 | ABC | ICT | 89TS1Y | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
9 | ABC | ICT | 89TS1B | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
LINE SERIES REACTOR/ BUS SERIES REACTOR
1 | ABC | LSR/BSR | CB | CB OPEN / CLOSE / CLOSE COMMAND | STTS | DPC
2 | ABC | LSR/BSR | 89A | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
3 | ABC | LSR/BSR | 89B | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
4 | ABC | LSR/BSR | 89L/ 89BSR | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
5 | ABC | LSR | 89LSR | ISOLATOR OPEN/CLOSE COMMAND | STTS | DPC
6 | ABC | LSR | 89LSR1 | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
7 | ABC | LSR | 89LSR2 | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
FIXED SERIES CAPACITOR (FSC)
1 | ABC | FSC | 52BBR | BPCB OPEN/CLOSE CMD |  | DPC
2 | ABC | FSC | 89MBS | BYPASS MBS OPEN/CLOSE CMD |  | DPC
3 | ABC | FSC | 89DS1 | BYPASS CAP ISO 1 OPEN/CLOSE CMD |  | DPC
4 | ABC | FSC | 89DS2 | BYPASS CAP ISO 2 OPEN/CLOSE CMD |  | DPC
ICT (DOUBLE MAIN SCHEME)
1 | ABC | ICT | CB | CB OPEN / CLOSE COMMAND | STTS | DPC
2 | ABC | ICT | 89A | ISOLATOR OPEN/CLOSE COMMAND | STTS | DPC
3 | ABC | ICT | 89B | ISOLATOR OPEN/CLOSE COMMAND | STTS | DPC
4 | ABC | ICT | 89T | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
5 | ABC | ICT | CB | CB OPEN / CLOSE COMMAND | STTS | DPC
6 | ABC | ICT | 89A | ISOLATOR OPEN/CLOSE COMMAND | STTS | DPC
7 | ABC | ICT | 89B | ISOLATOR OPEN/CLOSE COMMAND | STTS | DPC
8 | ABC | ICT | 89T | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
LINE FEEDER (DOUBLE MAIN SCHEME)
1 | ABC | LINE FEEDER | CB | CB OPEN / CLOSE COMMAND | STTS | DPC
2 | ABC | LINE FEEDER | 89A | ISOLATOR OPEN/CLOSE COMMAND | STTS | DPC
3 | ABC | LINE FEEDER | 89B | ISOLATOR OPEN/CLOSE COMMAND | STTS | DPC
4 | ABC | LINE FEEDER | 89L | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
5 | ABC | LINE FEEDER | CB | CB OPEN / CLOSE COMMAND | STTS | DPC
6 | ABC | LINE FEEDER | 89A | ISOLATOR OPEN/CLOSE COMMAND | STTS | DPC
7 | ABC | LINE FEEDER | 89B | ISOLATOR OPEN/CLOSE COMMAND | STTS | DPC
8 | ABC | LINE FEEDER | 89L | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
ICT (DOUBLE MAIN & TRANSFER SCHEME)
1 | ABC | ICT | CB | CB OPEN / CLOSE / CLOSE COMMAND | STTS | DPC
2 | ABC | ICT | 89A | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
3 | ABC | ICT | 89B | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
4 | ABC | ICT | 89T | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
5 | ABC | ICT | 89L | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
LINE FEEDER (DOUBLE MAIN & TRANSFER SCHEME)
1 | ABC | LINE FEEDER | CB | CB OPEN / CLOSE / CLOSE COMMAND | STTS | DPC
2 | ABC | LINE FEEDER | CB | AUTO RECLOSE TO AUTO / NON-AUTO MODE |  | DPC
3 | ABC | LINE FEEDER | 89A | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
4 | ABC | LINE FEEDER | 89B | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
5 | ABC | LINE FEEDER | 89T | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
6 | ABC | LINE FEEDER | 89L | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
BUS COUPLER ( DMT SCHEME)
1 | ABC | BUS COUPLER | CB | CB OPEN / CLOSE / CLOSE COMMAND | STTS | DPC
2 | ABC | BUS COUPLER | 89A | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
3 | ABC | BUS COUPLER | 89B | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
TRANSFER BUS COUPLER
1 | ABC | TRANSFER BUS COUPLER | CB | CB OPEN / CLOSE / CLOSE COMMAND |  | DPC
2 | ABC | TRANSFER BUS COUPLER | 89A | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
3 | ABC | TRANSFER BUS COUPLER | 89B | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
4 | ABC | TRANSFER BUS COUPLER | 89T | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
ICT (SINGLE MAIN & TRANSFER SCHEME)
1 | ABC | ICT | CB | CB OPEN / CLOSE / CLOSE COMMAND | STTS | DPC
2 | ABC | ICT | 89A | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
3 | ABC | ICT | 89B | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
4 | ABC | ICT | 89T | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
5 | ABC | ICT | 89L | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
BUS COUPLER ( SINGLE MAIN & TRANSFER SCHEME)
1 | ABC | BUS COUPLER | CB | CB OPEN / CLOSE / CLOSE COMMAND | STTS | DPC
2 | ABC | BUS COUPLER | 89A | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
3 | ABC | BUS COUPLER | 89B | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
4 | ABC | BUS COUPLER | 89T | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
5 | ABC | BUS COUPLER | 89L | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
LINE FEEDER ( SINGLE MAIN & TRANSFER SCHEME)
1 | ABC | LINE FEEDER | CB | CB OPEN / CLOSE / CLOSE COMMAND | STTS | DPC
2 | ABC | LINE FEEDER | 89A | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
3 | ABC | LINE FEEDER | 89B | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
4 | ABC | LINE FEEDER | 89T | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
5 | ABC | LINE FEEDER | 89L | ISOLATOR OPEN / CLOSE COMMAND | STTS | DPC
AUXILIARY SYSTEM
1 | 415 V | RTU | I/O_RACK-1 | DUMMY BREAKER OPEN COMMAND |  | DPC
2 | 415 V | RTU | I/O_RACK-1 | DUMMY BREAKER CLOSE COMMAND |  | DPC
3 | 415 V | DG Set | DGSET-1 | DG SET CB OPEN COMMAND |  | DPC
4 | 415 V | DG Set | DGSET-1 | DG SET CB CLOSE COMMAND |  | DPC
5 | 33 KV | LTSUP | TERTIARY | CB OPEN COMMAND |  | DPC
6 | 33 KV | LTSUP | TERTIARY | CB CLOSE COMMAND |  | DPC
7 | 33 KV | LTSUP | TERTIARY | ISO OPEN COMMAND |  | DPC
8 | 33 KV | LTSUP | TERTIARY | ISO CLOSE COMMAND |  | DPC
STATCOM (SIEMENS)
1 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-89A | HV Main Bay 89A Isolator Open |  | DPC
2 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-89A | HV Main Bay 89A Isolator Close |  | DPC
3 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-89B | HV Main Bay 89B Isolator Open |  | DPC
4 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-89B | HV Main Bay 89B Isolator Close |  | DPC
5 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-52 | HV Main Bay CB Open |  | DPC
6 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-52 | HV Main Bay CB Close |  | DPC
7 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q2 R PH | ISOLATOR OPEN |  | DPC
8 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q2 R PH | ISOLATOR CLOSED |  | DPC
9 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q2 Y PH | ISOLATOR OPEN |  | DPC
10 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q2 Y PH | ISOLATOR CLOSED |  | DPC
11 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q2 B PH | ISOLATOR OPEN |  | DPC
12 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q2 B PH | ISOLATOR CLOSED |  | DPC
13 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q3-R-PH | ISOLATOR OPEN |  | DPC
14 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q3-R-PH | ISOLATOR CLOSED |  | DPC
15 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q3-Y-PH | ISOLATOR OPEN |  | DPC
16 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q3-Y-PH | ISOLATOR CLOSED |  | DPC
17 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q3-B-PH | ISOLATOR OPEN |  | DPC
18 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q3-B-PH | ISOLATOR CLOSED |  | DPC
19 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-89A | ISOLATOR OPEN |  | DPC
20 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-89A | ISOLATOR CLOSE |  | DPC
21 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-89B | ISOLATOR OPEN |  | DPC
22 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-89B | ISOLATOR CLOSE |  | DPC
23 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-52 | CB OPEN |  | DPC
24 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-52 | CB CLOSE |  | DPC
25 | 4ZZ | FUTURE |  | HV Future Bay 89A Isolator Open |  | DPC
26 | 4ZZ | FUTURE |  | HV Future Bay 89A Isolator Close |  | DPC
27 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q1 R PH | MV ISOLATOR OPEN |  | DPC
28 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q1 R PH | MV ISOLATOR CLOSED |  | DPC
29 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q1 Y PH | MV ISOLATOR OPEN |  | DPC
30 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q1 Y PH | MV ISOLATOR CLOSED |  | DPC
31 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q1 B PH | MV ISOLATOR OPEN |  | DPC
32 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q1 B PH | MV ISOLATOR CLOSED |  | DPC
33 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q2 R PH | MV ISOLATOR OPEN |  | DPC
34 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q2 R PH | MV ISOLATOR CLOSED |  | DPC
35 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q2 Y PH | MV ISOLATOR OPEN |  | DPC
36 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q2 Y PH | MV ISOLATOR CLOSED |  | DPC
37 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q2 B PH | MV ISOLATOR OPEN |  | DPC
38 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q2 B PH | MV ISOLATOR CLOSED |  | DPC
39 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q12 R PH | MV ISOLATOR OPEN |  | DPC
40 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q12 R PH | MV ISOLATOR CLOSED |  | DPC
41 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q12 Y PH | MV ISOLATOR OPEN |  | DPC
42 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q12 Y PH | MV ISOLATOR CLOSED |  | DPC
43 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q12 B PH | MV ISOLATOR OPEN |  | DPC
44 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q12 B PH | MV ISOLATOR CLOSED |  | DPC
45 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q13 R PH | MV ISOLATOR OPEN |  | DPC
46 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q13 R PH | MV ISOLATOR CLOSED |  | DPC
47 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q13 Y PH | MV ISOLATOR OPEN |  | DPC
48 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q13 Y PH | MV ISOLATOR CLOSED |  | DPC
49 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q13 B PH | MV ISOLATOR OPEN |  | DPC
50 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q13 B PH | MV ISOLATOR CLOSED |  | DPC
51 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER J01-Q0 | AUXILIARY SUPPLY CIRCUIT BREAKER OPEN |  | DPC
52 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER J01-Q0 | AUXILIARY SUPPLY CIRCUIT BREAKER CLOSED |  | DPC
53 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER J01-Q1 | AUXILIARY SUPPLY ISOLATOR OPEN |  | DPC
54 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER J01-Q1 | AUXILIARY SUPPLY ISOLATOR CLOSED |  | DPC
55 | J11 | STATCOM VSC-1 BAY | VSC-2 MV-J12 | CIRCUIT BREAKER OPEN |  | DPC
56 | J11 | STATCOM VSC-1 BAY | MSR-1 MV-J21 | CIRCUIT BREAKER CLOSED |  | DPC
57 | J11 | STATCOM VSC-1 BAY | MSR-2 MV-J22 | ISOLATOR SWITCH OPEN |  | DPC
58 | J11 | STATCOM VSC-1 BAY | MSC-1 MV-J31 | ISOLATOR SWITCH CLOSED |  | DPC
59 | J12 | STATCOM VSC-2 BAY | MSR-1 MV-J21 | CIRCUIT BREAKER OPEN |  | DPC
60 | J12 | STATCOM VSC-2 BAY | MSR-2 MV-J22 | CIRCUIT BREAKER CLOSED |  | DPC
61 | J12 | STATCOM VSC-2 BAY | MSC-1 MV-J31 | ISOLATOR SWITCH OPEN |  | DPC
62 | J12 | STATCOM VSC-2 BAY | MSC-2 MV-J32 | ISOLATOR SWITCH CLOSED |  | DPC
63 | J21 | STATCOM MSR-1 BAY | MSR-2 MV-J22 | CIRCUIT BREAKER OPEN |  | DPC
64 | J21 | STATCOM MSR-1 BAY | MSC-1 MV-J31 | CIRCUIT BREAKER CLOSED |  | DPC
65 | J21 | STATCOM MSR-1 BAY | MSC-2 MV-J32 | ISOLATOR SWITCH OPEN |  | DPC
66 | J21 | STATCOM MSR-1 BAY | MSR-1 J21 Q1 | ISOLATOR SWITCH CLOSED |  | DPC
67 | J22 | STATCOM MSR-2 BAY | MSR-2 J22 Q0 | CIRCUIT BREAKER OPEN |  | DPC
68 | J22 | STATCOM MSR-2 BAY | MSR-2 J22 Q0 | CIRCUIT BREAKER CLOSED |  | DPC
69 | J22 | STATCOM MSR-2 BAY | MSR-2 J22 Q1 | ISOLATOR SWITCH OPEN |  | DPC
70 | J22 | STATCOM MSR-2 BAY | MSR-2 J22 Q1 | ISOLATOR SWITCH CLOSED |  | DPC
71 | J31 | STATCOM MSC-1 BAY | MSC-1 J31 Q0 | CIRCUIT BREAKER OPEN |  | DPC
72 | J31 | STATCOM MSC-1 BAY | MSC-1 J31 Q0 | CIRCUIT BREAKER CLOSED |  | DPC
73 | J31 | STATCOM MSC-1 BAY | MSC-1 J31 Q1 | ISOLATOR SWITCH OPEN |  | DPC
74 | J31 | STATCOM MSC-1 BAY | MSC-1 J31 Q1 | ISOLATOR SWITCH CLOSED |  | DPC
75 | J32 | STATCOM MSC-2 BAY | MSC-2 J32 Q0 | CIRCUIT BREAKER OPEN |  | DPC
76 | J32 | STATCOM MSC-2 BAY | MSC-2 J32 Q0 | CIRCUIT BREAKER CLOSED |  | DPC
77 | J32 | STATCOM MSC-2 BAY | MSC-2 J32 Q1 | ISOLATOR SWITCH OPEN |  | DPC
78 | J32 | STATCOM MSC-2 BAY | MSC-2 J32 Q1 | ISOLATOR SWITCH CLOSED |  | DPC
79 | STATCOM | STATCOM | STATCOM OPERATION | STATCOM AUTOMATIC CONTROL CMD |  | DPC
80 | STATCOM | STATCOM | STATCOM OPERATION | STATCOM MANUAL CONTROL CMD |  | DPC
81 | STATCOM | STATCOM | STATCOM OPERATION | REACTIVE POWER CONTROL MODE ENABLE CMD |  | DPC
82 | STATCOM | STATCOM | STATCOM OPERATION | REACTIVE POWER CONTROL MODE DISABLE CMD |  | DPC
83 | STATCOM | STATCOM | STATCOM OPERATION | GAIN ADJUSTMENT AUTOMATIC CMD |  | DPC
84 | STATCOM | STATCOM | STATCOM OPERATION | GAIN ADJUSTMENT MANUAL CMD |  | DPC
85 | STATCOM | STATCOM | STATCOM OPERATION | NPS ON CMD |  | DPC
86 | STATCOM | STATCOM | STATCOM OPERATION | NPS OFF CMD |  | DPC
87 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICES HV AUTOMATIC |  | DPC
88 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICES HV OFF |  | DPC
89 | STATCOM | STATCOM | STATCOM OPERATION | AUTO-RESTART ON SELECTED |  | DPC
90 | STATCOM | STATCOM | STATCOM OPERATION | AUTO-RESTART OFF SELECTED |  | DPC
91 | STATCOM | STATCOM | STATCOM OPERATION | SELECT SYSTEM 1 ACTIVE |  | DPC
92 | STATCOM | STATCOM | STATCOM OPERATION | SELECT SYSTEM 2 ACTIVE |  | DPC
93 | STATCOM | STATCOM | STATCOM OPERATION | UNEQUAL LOAD SHARING MODE ON CMD |  | DPC
94 | STATCOM | STATCOM | STATCOM OPERATION | UNEQUAL LOAD SHARING MODE OFF CMD |  | DPC
95 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICE LV1 PSD BYPASS COMMAND |  | DPC
96 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICE LV1 PSD ON COMMAND |  | DPC
97 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICE LV2 PSD BYPASS COMMAND |  | DPC
98 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICE LV2 PSD ON COMMAND |  | DPC
99 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICE LV3 PSD BYPASS COMMAND |  | DPC
100 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICE LV3 PSD ON COMMAND |  | DPC
101 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICE LV4 PSD BYPASS COMMAND |  | DPC
102 | STATCOM | STATCOM | STATCOM OPERATION | EXTERNAL DEVICE LV4 PSD ON COMMAND |  | DPC
STATCOM (RXPE)
1 | XX KV | FUTURE BAY | 89A | ISOLATOR OPEN COMMAND |  | DPC
2 | XX KV | FUTURE BAY | 89A | ISOLATOR CLOSE COMMAND |  | DPC
3 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | CB OPEN COMMAND |  | DPC
4 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | CB CLOSE COMMAND |  | DPC
5 | XX KV | FUTURE& COUPLING T/F-1 TIE | 89A | 89A OPEN COMMAND |  | DPC
6 | XX KV | FUTURE& COUPLING T/F-1 TIE | 89A | 89A CLOSE COMMAND |  | DPC
7 | XX KV | FUTURE& COUPLING T/F-1 TIE | 89B | 89B OPEN COMMAND |  | DPC
8 | XX KV | FUTURE& COUPLING T/F-1 TIE | 89B | 89B CLOSE COMMAND |  | DPC
9 | XX KV | COUPLING TRANSFORMER (HV) | 52 | CB OPEN COMMAND |  | DPC
10 | XX KV | COUPLING TRANSFORMER (HV) | 52 | CB CLOSE COMMAND |  | DPC
11 | XX KV | COUPLING TRANSFORMER (HV) | 89A | ISOLATOR OPEN COMMAND |  | DPC
12 | XX KV | COUPLING TRANSFORMER (HV) | 89A | ISOLATOR CLOSE COMMAND |  | DPC
13 | XX KV | COUPLING TRANSFORMER (HV) | 89 | ISOLATOR OPEN COMMAND |  | DPC
14 | XX KV | COUPLING TRANSFORMER (HV) | 89 | ISOLATOR CLOSE COMMAND |  | DPC
15 | XX KV | COUPLING TRANSFORMER (HV) | 89TR | ISOLATOR OPEN COMMAND |  | DPC
16 | XX KV | COUPLING TRANSFORMER (HV) | 89TR | ISOLATOR CLOSE COMMAND |  | DPC
17 | XX KV | COUPLING TRANSFORMER (HV) | 89TSR | ISOLATOR OPEN COMMAND |  | DPC
18 | XX KV | COUPLING TRANSFORMER (HV) | 89TSR | ISOLATOR CLOSE COMMAND |  | DPC
19 | XX KV | COUPLING TRANSFORMER (HV) | 89TY | ISOLATOR OPEN COMMAND |  | DPC
20 | XX KV | COUPLING TRANSFORMER (HV) | 89TY | ISOLATOR CLOSE COMMAND |  | DPC
21 | XX KV | COUPLING TRANSFORMER (HV) | 89TSY | ISOLATOR OPEN COMMAND |  | DPC
22 | XX KV | COUPLING TRANSFORMER (HV) | 89TSY | ISOLATOR CLOSE COMMAND |  | DPC
23 | XX KV | COUPLING TRANSFORMER (HV) | 89TB | ISOLATOR OPEN COMMAND |  | DPC
24 | XX KV | COUPLING TRANSFORMER (HV) | 89TB | ISOLATOR CLOSE COMMAND |  | DPC
25 | XX KV | COUPLING TRANSFORMER (HV) | 89TSB | ISOLATOR OPEN COMMAND |  | DPC
26 | XX KV | COUPLING TRANSFORMER (HV) | 89TSB | ISOLATOR CLOSE COMMAND |  | DPC
27 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TAP CHANGER LOWER COMMAND |  | DPC
28 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TAP CHANGER RAISE COMMAND |  | DPC
29 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TR1 | ISOLATOR OPEN/CLOSE |  | DPC
30 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TR2 | ISOLATOR OPEN/CLOSE |  | DPC
31 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TY1 | ISOLATOR OPEN/CLOSE |  | DPC
32 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TY2 | ISOLATOR OPEN/CLOSE |  | DPC
33 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TB1 | ISOLATOR OPEN/CLOSE |  | DPC
34 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TB2 | ISOLATOR OPEN/CLOSE |  | DPC
35 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSR1 | ISOLATOR OPEN/CLOSE |  | DPC
36 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSR2 | ISOLATOR OPEN/CLOSE |  | DPC
37 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSY1 | ISOLATOR OPEN/CLOSE |  | DPC
38 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSY2 | ISOLATOR OPEN/CLOSE |  | DPC
39 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSB1 | ISOLATOR OPEN/CLOSE |  | DPC
40 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSB2 | ISOLATOR OPEN/CLOSE |  | DPC
41 | 38.5KV | STATCOM- 1 | STATCOM VSC 60189A | ISOLATOR OPEN/CLOSE |  | DPC
42 | 38.5KV | STATCOM- 1 | 60152 | CB OPEN/CLOSE |  | DPC
43 | 38.5KV | STATCOM- 1 | VSC-1 | STATCOM-1 COOLING SYSTEM COMMAND |  | DPC
44 | 38.5KV | STATCOM- 2 | STATCOM VSC 60289A | ISOLATOR OPEN/CLOSE |  | DPC
45 | 38.5KV | STATCOM- 2 | 60252 | CB OPEN / CLOSE |  | DPC
46 | 38.5KV | STATCOM- 2 | VSC-2 | STATCOM-2 COOLING SYSTEM COMMAND |  | DPC
47 | 38.5KV | MSC | 60352 | CB OPEN/CLOSE |  | DPC
48 | 38.5KV | MSC | 60389A | ISOLATOR OPEN/CLOSE |  | DPC
49 | 38.5KV | MSR- 1 | 60452 | CB OPEN/CLOSE |  | DPC
50 | 38.5KV | MSR- 1 | 60489A | ISOLATOR OPEN/CLOSE |  | DPC
51 | 38.5KV | MSR- 2 | 60552 | CB OPEN/CLOSE |  | DPC
52 | 38.5KV | MSR- 2 | 60589A | ISOLATOR OPEN/CLOSE |  | DPC
53 | 38.5KV | AUX T/F | 60652 | CB OPEN/CLOSE |  | DPC
54 | 38.5KV | AUX T/F | 60689A | ISOLATOR OPEN/CLOSE |  | DPC
55 | 33KV | AUX | TERTIARY 33KV ISOLATOR | ISOLATOR OPEN/CLOSE |  | DPC
56 | 33KV | AUX | TERTIARY 33KV CB | CB OPEN/CLOSE |  | DPC
57 | 415 V | AUX | MSB INCOMER-1 | INCOMER-1 ON/OFF |  | DPC
58 | 415 V | AUX | MSB BUS COUPLER | BUSCOUPLER ON/OFF |  | DPC
59 | 415 V | AUX | MSB INCOMER-2 | INCOMER-2 ON/OFF |  | DPC
60 | 415 V | AUX | ACDB INCOMER-1 | INCOMER-1 ON/OFF |  | DPC
61 | 415 V | AUX | ACDB BUS COUPLER | BUSCOUPLER ON/OFF |  | DPC
62 | 415 V | AUX | ACDB INCOMER-2 | INCOMER-2 ON/OFF |  | DPC
63 | 415 V | AUX | DG SET | DG START/STOP |  | DPC
64 | 415 V | AUX | DG SET | DG INCOMER CB ON/OFF |  | DPC
STATCOM (HYOSUNG)
1 | 400KV | COUPLING TRANSFORMER (HV) | 52 | CB OPEN/CLOSE |  | DPC
2 | 400KV | COUPLING TRANSFORMER (HV) | 89A | ISOLATOR OPEN/CLOSE |  | DPC
3 | 400KV | COUPLING TRANSFORMER (HV) | 89B | ISOLATOR OPEN/CLOSE |  | DPC
4 | 400KV | COUPLING TRANSFORMER (HV) | 89TR | ISOLATOR OPEN/CLOSE |  | DPC
5 | 400KV | COUPLING TRANSFORMER (HV) | 89TSR | ISOLATOR OPEN/CLOSE |  | DPC
6 | 400KV | COUPLING TRANSFORMER (HV) | 89TY | ISOLATOR OPEN/CLOSE |  | DPC
7 | 400KV | COUPLING TRANSFORMER (HV) | 89TSY | ISOLATOR OPEN/CLOSE |  | DPC
8 | 400KV | COUPLING TRANSFORMER (HV) | 89TB | ISOLATOR OPEN/CLOSE |  | DPC
9 | 400KV | COUPLING TRANSFORMER (HV) | 89TSB | ISOLATOR OPEN/CLOSE |  | DPC
10 | 20KV | COUPLING TRANSFORMER (MV) | 89TR | ISOLATOR OPEN/CLOSE |  | DPC
11 | 20KV | COUPLING TRANSFORMER (MV) | 89TY | ISOLATOR OPEN/CLOSE |  | DPC
12 | 20KV | COUPLING TRANSFORMER (MV) | 89TB | ISOLATOR OPEN/CLOSE |  | DPC
13 | 20KV | COUPLING TRANSFORMER (MV) | 89TSR | ISOLATOR OPEN/CLOSE |  | DPC
14 | 20KV | COUPLING TRANSFORMER (MV) | 89TSY | ISOLATOR OPEN/CLOSE |  | DPC
15 | 20KV | COUPLING TRANSFORMER (MV) | 89TSB | ISOLATOR OPEN/CLOSE |  | DPC
16 | 20KV | STATCOM-1 | VSC-1 -52 | CB OPEN/CLOSE |  | DPC
17 | 20KV | STATCOM-1 | VSC-1 -89A | ISOLATOR OPEN/CLOSE |  | DPC
18 | 20KV | STATCOM-1 | VSC-1 -89B | ISOLATOR OPEN/CLOSE |  | DPC
19 | 20KV | STATCOM-2 | VSC-2 -52 | CB OPEN/CLOSE |  | DPC
20 | 20KV | STATCOM-2 | VSC-2 -89A | ISOLATOR OPEN/CLOSE |  | DPC
21 | 20KV | STATCOM-2 | VSC-2 -89B | ISOLATOR OPEN/CLOSE |  | DPC
22 | 20KV | GND T/F | 89 | ISOLATOR OPEN/CLOSE |  | DPC
23 | 20KV | BUS PT | 89 | ISOLATOR OPEN/CLOSE |  | DPC
24 | 20KV | AUX.T/F | 89 | ISOLATOR OPEN/CLOSE |  | DPC
25 | 20KV | AUX.T/F | 52 | CB OPEN/CLOSE |  | DPC
26 | 33KV | AUX.T/F | TERTIARY 52 | CB OPEN / CLOSE |  | DPC
27 | 33KV | AUX.T/F | TERTIARY 89 | 89 OPEN / CLOSE |  | DPC
28 | 20KV | MSR-1 | 89A | ISOLATOR OPEN/CLOSE |  | DPC
29 | 20KV | MSR-1 | 52 | CB OPEN/CLOSE |  | DPC
30 | 20KV | MSR-1 | 89B | ISOLATOR OPEN/CLOSE |  | DPC
31 | 20KV | MSR-2 | 89A | ISOLATOR OPEN/CLOSE |  | DPC
32 | 20KV | MSR-2 | 52 | CB OPEN/CLOSE |  | DPC
33 | 20KV | MSR-2 | 89B | ISOLATOR OPEN/CLOSE |  | DPC
34 | 20KV | MSC | 89A | ISOLATOR OPEN/CLOSE |  | DPC
35 | 20KV | MSC | 52 | CB OPEN/CLOSE |  | DPC
36 | 20KV | MSC | 89B | ISOLATOR OPEN/CLOSE |  | DPC
37 | 400KV | FUTURE | 89A | ISOLATOR OPEN/CLOSE |  | DPC
38 | 400KV | FUTURE & STATCOM TIE | 52 | CB OPEN/CLOSE |  | DPC
39 | 400KV | FUTURE & STATCOM TIE | 89A | ISOLATOR OPEN/CLOSE |  | DPC
40 | 400KV | FUTURE & STATCOM TIE | 89B | ISOLATOR OPEN/CLOSE |  | DPC
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30

## SPC (hidden)
Sl.NO | BAY NUM. | BAY NAME | DEVICE ID | SIGNAL DESCRIPTION | DATA TYPE | SCADA ID | REMARK
765 KV/ 400 KV/ 220 KV LINE FEEDER
1 | ABC | LINE FEEDER | LINE | 86A TRIP RELAY RESET | SPC | 86AO
2 | ABC | LINE FEEDER | LINE | 86B TRIP RELAY RESET | SPC | 86BO
3 | ABC | LINE FEEDER | CB | CB CHECK SYNC BYPASS COMMAND | SPC | DLCC
4 | ABC | LINE FEEDER | CB | A/R LOCK OUT RELAY RESET | SPC | ARLO
765 KV/ 400 KV SWITCHABLE LINE REACTOR/ BUS REACTOR
1 | ABC | LINE FEEDER WITH SW REACTOR | RE | REACTOR TRIP RELAY 86A RESET | SPC | GRAO
2 | ABC | LINE FEEDER WITH SW REACTOR | RE | REACTOR TRIP RELAY 86B RESET | SPC | GRBO
3 | ABC | LINE FEEDER WITH SW REACTOR | ZBR | BYPASS CMD FOR CNTRL SWITCH DEVICE | SPC | BYSW
4 | ABC | LINE FEEDER WITH SW REACTOR | RE | COMMAND FOR DELUGE VALVE - R PH | SPC |  | To be combined in case of 3 phase Line Reactor/Bus Reactor
5 | ABC | LINE FEEDER WITH SW REACTOR | RE | COMMAND FOR DELUGE VALVE - Y PH | SPC
6 | ABC | LINE FEEDER WITH SW REACTOR | RE | COMMAND FOR DELUGE VALVE - B PH | SPC
7 | ABC | LINE FEEDER WITH SW REACTOR | RE | COMMAND FOR DELUGE VALVE - SPARE | SPC
FIXED SERIES CAPACITOR (FSC)
1 | ABC | FSC |  | MASTER TRIP RST | SPC
765 KV/ 400 KV/220 KV TIE/ BUS SECTION BAY
1 | ABC | TIE / BS | CB | 86A TRIP RELAY RESET | SPC | 86AO
2 | ABC | TIE / BS | CB | 86B TRIP RELAY RESET | SPC | 86BO
3 | ABC | TIE / BS | CB | CB CHECK SYNC BYPASS COMMAND | SPC | DLCC
4 | ABC | TIE | CB | BYPASS CMD FOR CNTRL SWITCH DEVICE | SPC | BYSW | In case of ICT, Line Reactor or Bus Reactor in Main Bays
5 | ABC | TIE / BS | CB | A/R LOCK OUT RELAY RESET | SPC | ARLO
ICT
1 | ABC | ICT | XFMR_P | 86A TRIP RELAY RESET | SPC | 89AO
2 | ABC | ICT | XFMR_P | 86B TRIP RELAY RESET | SPC | 86AO
3 | ABC | ICT | XFMR_P | CB CHECK SYNC BYPASS COMMAND | SPC | DLCC
4 | ABC | ICT | XFMR_P | BYPASS CMD FOR CNTRL SWITCH DEVICE | SPC | BYSW
5 | ABC | ICT | XFMR_P | COMMAND FOR DELUGE VALVE - R PH | SPC | DVTR | To be combined in case of 3 phase ICT
6 | ABC | ICT | XFMR_P | COMMAND FOR DELUGE VALVE - Y PH | SPC | DVTY
7 | ABC | ICT | XFMR_P | COMMAND FOR DELUGE VALVE - B PH | SPC | DVTB
8 | ABC | ICT | XFMR_P | TAP CHANGER RAISE COMMAND | SPC
9 | ABC | ICT | XFMR_P | TAP CHANGER LOWER COMMAND | SPC
10 | ABC | SPARE ICT | XFMR_P | COMMAND FOR DELUGE VALVE - SPARE | SPC
BUS COUPLER
1 | ABC | BUS COUPLER | CB | CB CHECK SYNC BYPASS COMMAND | SPC | DLCC
TRANSFER BUS COUPLER
1 | ABC | TRANSFER BUS COUPLER | LINE | 86A TRIP RELAY RESET | SPC | 86AO
2 | ABC | TRANSFER BUS COUPLER | LINE | 86B TRIP RELAY RESET | SPC | 86BO
3 | ABC | TRANSFER BUS COUPLER | CB | CB CHECK SYNC BYPASS COMMAND | SPC | DLCC
4 | ABC | TRANSFER BUS COUPLER | CB | A/R LOCK OUT RELAY RESET | SPC | ARLO
AUXILIARY SYSTEM
1 | 415 V | FP | EPUMP | EMER. START OF ELECTRIC MOTOR DRIVEN PUMP | SPC
2 | 415 V | FP | EPUMP | EMER. STOP OF ELECTRIC MOTOR DRIVEN PUMP | SPC
3 | 415 V | FP | DPUMP | EMER. START OF DIESEL MOTOR DRIVEN PUMP | SPC
4 | 415 V | FP | DPUMP | EMER. STOP OF DIESEL MOTOR DRIVEN PUMP | SPC
5 | 415 V | FP | G_703_ICT-1 | DELGUE VALVE ICT ON COMMAND | SPC
6 | 415 V | FP | G_701_BR-1 | DELUGE VALVE ON COMMAND FOR BUS REACTOR | SPC
7 | 415 V | SYSTEM | AUX_SYSTEM | SUBSTATION COMMAND FOR MAIN CONTROL ON NTAMC | SPC
8 | 415 V | SYSTEM | AUX_SYSTEM | SUBSTATION COMMAND FOR MAIN CONTROL ON RTAMC | SPC
9 | 415 V | SYSTEM | AUX_SYSTEM | SUBSTATION COMMAND FOR MAIN CONTROL ON BACK UP NTAMC | SPC
10 | 415 V | SYSTEM | AUX_SYSTEM | SUBSTATION COMMAND FOR AUX CONTROL ON NTAMC | SPC
11 | 415 V | SYSTEM | AUX_SYSTEM | SUBSTATION COMMAND FOR AUXCONTROL ON RTAMC | SPC
12 | 415 V | SYSTEM | AUX_SYSTEM | SUBSTATION COMMAND FOR AUX CONTROL ON BACK UP NTAMC | SPC
13 | 415 V | DG Set | DGSET-1 | DG SET START COMMAND | SPC
14 | 415 V | DG Set | DGSET-1 | DG SET STOP COMMAND | SPC
STATCOM (SIEMENS)
1 | STATCOM | STATCOM | STATCOM OPERATION | ACKNOWLEDGE CMD VSC 1 | SPC
2 | STATCOM | STATCOM | STATCOM OPERATION | ACKNOWLEDGE CMD VSC 2 | SPC
3 | STATCOM | STATCOM | STATCOM OPERATION | CONTROL VIA HMI REMOTE COMMAND | SPC
4 | STATCOM | STATCOM | STATCOM OPERATION | CONTROL VIA RCI COMMAND | SPC
5 | STATCOM | STATCOM | STATCOM OPERATION | EMERGENCY T+E20RIP CMD | SPC
STATCOM (RXPE)
1 | XX KV | FUTURE& COUPLING T/F-1 TIE |  | 86A TRIP RELAY RESET COMMAND | SPC
2 | XX KV | FUTURE& COUPLING T/F-1 TIE |  | 86B TRIP RELAY RESET COMMAND | SPC
3 | XX KV | FUTURE& COUPLING T/F-1 TIE |  | BYPASS CMD FOR CNTRL SWITCH DEVICE | SPC
4 | XX KV | FUTURE& COUPLING T/F-1 TIE |  | CB CHECK SYNC. BYPASS COMMAND | SPC
5 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 86A TRIP RELAY RESET | SPC
6 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 86B TRIP RELAY RESET | SPC
7 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | CB CHECK SYNC. BYPASS COMMAND | SPC
8 | 38.5KV | STATCOM CONTROL | STATCOM | ONE KEY START | SPC
9 | 38.5KV | STATCOM CONTROL | STATCOM | ONE KEY STOP | SPC
10 | 38.5KV | STATCOM CONTROL | STATCOM | ONE KEY EXIT | SPC
11 | 38.5KV | STATCOM CONTROL | STATCOM | ONE KEY FAULT CLEAR (RESET) | SPC
12 | 38.5KV | STATCOM CONTROL | STATCOM | STATCOM 1 EMG. STOP | SPC
13 | 38.5KV | STATCOM CONTROL | STATCOM | STATCOM 2 EMG. STOP | SPC
14 | 38.5KV | STATCOM CONTROL | STATCOM | SUBSTATION EMG. STOP | SPC
15 | 38.5KV | STATCOM CONTROL | STATCOM | EXTERNAL CONTROL AUTO (MSR & MSC, HV B/R) | SPC
16 | 38.5KV | STATCOM CONTROL | STATCOM | EXTERNAL CONTROL MANUAL (MSR & MSC, HV B/R) | SPC
17 | 38.5KV | STATCOM CONTROL | STATCOM | UP-SET U-REF(PU) | SPC
18 | 38.5KV | STATCOM CONTROL | STATCOM | DN-SET U-REF(PU) | SPC
19 | 38.5KV | STATCOM CONTROL | STATCOM | Q-SET REF(PU)/FS REF(PU) UP | SPC
20 | 38.5KV | STATCOM CONTROL | STATCOM | Q-SET REF(PU)/FS REF(PU) DN | SPC
21 | 38.5KV | STATCOM CONTROL | STATCOM | VOLTAGE MODE CONTROL | SPC
22 | 38.5KV | STATCOM CONTROL | STATCOM | REACTIVE MODE CONTROL | SPC
23 | 415 V | AUX | FP CUPLING TRAFO | DELUGE VALVE R-PH CONTROL CMD | SPC
24 | 415 V | AUX | FP CUPLING TRAFO | DELUGE VALVE Y-PH CONTROL CMD | SPC
25 | 415 V | AUX | FP CUPLING TRAFO | DELUGE VALVE B-PH CONTROL CMD | SPC
26 | 415 V | AUX | FP CUPLING TRAFO | DELUGE VALVE S-PH CONTROL CMD | SPC
STATCOM (HYOSUNG)
1 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY 86.1 TRIP RELAY RESET | SPC
2 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY 86.2 TRIP RELAY RESET | SPC
3 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY CSD BYPASS-ON | SPC
4 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY CSD BYPASS-OFF (IN SERVICE) | SPC
5 | 20KV | STATCOM-1 | VSC-1 | STATCOM UNIT-1 TRIP RELAY-A(86A) RESET | SPC
6 | 20KV | STATCOM-1 | VSC-1 | STATCOM UNIT-1 TRIP RELAY-B(86B) RESET | SPC
7 | 20KV | STATCOM-2 | VSC-2 | STATCOM UNIT-2 TRIP RELAY-A(86A) RESET | SPC
8 | 20KV | STATCOM-2 | VSC-2 | STATCOM UNIT-2 TRIP RELAY-B(86B) RESET | SPC
9 | 20KV | AUX.T/F | AUX T/F | TRIP RELAY-A(86A) RESET | SPC
10 | 20KV | AUX.T/F | AUX T/F | TRIP RELAY-B(86B) RESET | SPC
11 | 20KV | MSR-1 | MSR | MSR-1 TRIP RELAY-A(86A) RESET | SPC
12 | 20KV | MSR-1 | MSR | MSR-1 TRIP RELAY-B(86B) RESET | SPC
13 | 20KV | MSR-2 | MSR | MSR-2 TRIP RELAY-A(86A) RESET | SPC
14 | 20KV | MSR-2 | MSR | MSR-2 TRIP RELAY-B(86B) RESET | SPC
15 | 20KV | MSC | MSC | MSC TRIP RELAY-A(86A) RESET | SPC
16 | 20KV | MSC | MSC | MSC TRIP RELAY-B(86B) RESET | SPC
17 | 400KV | FUTURE & STATCOM TIE |  | 86.1 TRIP RELAY RESET | SPC
18 | 400KV | FUTURE & STATCOM TIE |  | 86.2 TRIP RELAY RESET | SPC
19 | 400KV | FUTURE & STATCOM TIE |  | CSD BYPASS-ON | SPC
20 | 400KV | FUTURE & STATCOM TIE |  | CSD BYPASS-OFF (IN SERVICE) | SPC

## Sheet1 (hidden)
Annexure A :
Annexure B : HYSONG
Annexure C: RXPE

## SUMMARY (hidden)
ABC DATA LIST
IEC 60870-5-104 interoperability Profile for NTAMC Control centers
PROTOCOL SUMMARY
SL.No. | Description |  |  |  | Value |  | Remark
1 | ASDU Common Address |  |  |  | 237 |  | Integer Number to be provided by NTAMC
2 | Common Address Size of ASDU |  |  |  | 2 Byte
3 | Information object Address Structure |  |  |  | 3 Byte
4 | Frame Max Length |  |  |  | 255
5 | MV Periodic Cycle |  |  |  | Periodic cycle 15Sec and Spontaneous transmission on 1% change of Current value. For Frequency 0.02% (i.e.0.01 Hz)
6 | Binary Time Stamp Size |  |  |  | 7 Byte |  | CP56 Time 2a
7 | T0: Connection Time Out |  |  |  | 30 Sec.
8 | T1: APDU Time Out |  |  |  | 15 Sec.
9 | T2: Acknowledge Time Out |  |  |  | 10 Sec.
10 | T3: Test Frame Time Out |  |  |  | 20 Sec.
11 | K: Send Acknowledgement Frames (APDU) |  |  |  | 12
12 | W: Acknowledgement Received Frame (APDU) |  |  |  | 8
13 | Time Synchronisation |  |  |  | NA |  | Locally through IRIG-B or SNTP
14 | Cause of Transmission |  |  |  | 2 Byte
DIGTAL STATUS SETTINGS PROFILE
SL.No. | Discription | Duration |  |  |  |  | Remark
1 | Debouncing Time | 4ms
2 | Filtering Delay | 5ms
IEC 60870-5-104 Digital Signal type
SL.No. | Discription |  | Status Signal type | CONTROL TYPE |  |  | PULSE WIDTH DURATION | TIME OUT DURATION
1(a) | Circuit Breaker (ON/OFF) |  | DPS | DPC |  | SBO | 500 ms | 3 Sec
1(b) | Circuit breaker (Check synch bypass) |  | SPS | SPC |  | DIRECT OPERATE | 500 ms | 3 Sec
2 | Isolator |  | DPS | DPC |  | SBO | 500 ms | 20 Sec
3 | Tap Changer status & RAISE/LOWER control command |  | DPS | DPC |  | SBO | 500 ms | 10 Sec
4 | Trip Relay & L/O Relays reset |  | SPS | SPC |  | DIRECT OPERATE | 500 ms | 10 Sec
5 | Mode Selection (e.g. AR Auto/Non-auto, Protection Transfer etc.), Auxiliaries Motor, DG set & Diesel Engine, etc |  | DPS | DPC |  | SBO | 500 ms | 10 Sec
6 | Control Switching Device (CSD) BYPASS COMMAND & Status |  | SPS | SPC |  | DIRECT OPERATE | 500 ms | 10 Sec
7 | Fire fighting tank Water level, Manual Open/Close status (One SPS for each level) |  | SPS | NA
8 | Control Authority Transfer signals (NTAMC/BNTAMC/RTAMC) |  | SPS | SPC |  | DIRECT OPERATE | 500 ms | 3 Sec
9 | Auto/Manual, Local/Remote |  | DPS | NA
10 | Other signals |  | SPS | SPC (If applicable) |  | DIRECT OPERATE | 500 ms | 3 Sec
The abnormal state for SPS signals shall be the HIGH state for alarms like ALARM/NORMAL, UNHEALTHY/HEALTHY, LOW/NORMAL, ON/OFF, FAIL/NORMAL, SET/RESET.
IEC 60870-5-104 ASDU ANALOG Data TYPE
SL.No. | Description |  |  | Remark
1 | Tap Position (1- 25) | Analog
2 | MW, MVAR, Current, Freq, Volatge | Analog
3 | Temperature, Humidity | Analog
4 | Fire fighting System Water pressure | Analog
5 | DC Supply Volatge /Current | Analog
6 | DG set & FF engine Battery volatge | Analog
IEC 60870-5-104 ASDU TYPE
SL.No. | Description |  |  |  | ASDU TYPE ID |  | Remark
1 | Analog | Measured Valuse, Short Floating Point Value |  |  | 13
2 | SPS | Single Point Information with Time Tag |  |  | 30
3 | DPS | Double Point Information with Time Tag |  |  | 31
4 | Analog spontaneous transmission | Measured Value, Short Floating Point Value with Time Tag |  |  | 36
5 | SPC | Single Command |  |  | 45 |  | OPEN/CLOSE, SET/RESET
6 | DPC | Double Command |  |  | 46 |  | OPEN/CLOSE, RAISE/LOWER, AUTO/MANUAL
IEC 60870-5-104 IOA ADDRESS STRUCTURE
SL.No. | Description |  |  |  | Starting Address |  | Remark
1 | Single Point Status (SPS) |  |  |  | 1
2 | Double Point Status (DPS) |  |  |  | 5000
3 | Measurement Value (MV) or Analog Value (AI) |  |  |  | 10000
4 | Double Point Control (DPC) |  |  |  | 15000
5 | Single Point Control (SPC) |  |  |  | 17000
NOTE:
A. Control Authority Transfer Scheme for NTAMC/RTAMC/Backup NTAMC
Both the SAS Gateways shall be configured to report independently to three control centers of NTAMC system (Main NTAMC, Backup NTAMC & RTAMC) simultaneously. There shall be a Control Center Authority Transfer scheme implemented such that at a time, only one Control Center shall be able to Control the Substation. Any Control center shall be able to takeover supervisory control authority from the substation gateway for either / both main system / auxiliary system after substation is manually put in remote mode from local station. The information regarding which control center is having the control authority shall be known to all the other control centers. The total points in the substation will be categorised in two Groups either as "POWER" or "AUXILLIARY". The Control Authority transfer to a Control Center shall be possible for any of the groups i.e. POWER or AUXILIARY or both. This takeover control logic shall be implemented in the SAS Gateway.
B. Substation Level Local/Remote Switch
A Substation Level Local/Remote switch shall be provided prefarably in SUX BCU Panel in control room. The function is to transfer the supervisory control from SUBSTATION level to the CONTROL CENTER level. The controls shall be from SUBSTATION if the switch is in LOCAL position. It will be from the CONTROL CENTERs (Main NTAMC /Backup NTAMC / RTAMC) if the switch is in REMOTE MODE. The Control Authority Transfer shall be applicable when in REMOTE MODE.
C. | Station ID shall be a unique number for each substation to be provided by NTAMC Control Center
D. | A Dummy Circuit Breaker to be provided in the Aux BCU Panel in Substation Control Room to test healthiness of the communication link including Substation Gateway / RTU from NTAMC control center. The associated control & monitoring indication to be hard wired to Aux BCU for the same.

## SPS (hidden)
Sl.NO | BAY NUM. | BAY NAME | DEVICE ID | SIGNAL DESCRIPTION | DATA TYPE | SCADA ID | Remarks
765 KV/ 400 KV/ 220 KV LINE FEEDER
1 | ABC | LINE FEEDER | BCU | BAY IN MAINTENANCE MODE | SPS | BAYM
2 | ABC | LINE FEEDER | BCU | BCU DC SUPPLY FAIL-1/2 | SPS | BCUD
3 | ABC | LINE FEEDER | BCU | BCU UNHEALTHY | SPS | BCUH
4 | ABC | LINE FEEDER | BCU | BCU TIME SYNC ERROR | SPS | BCUC
5 | ABC | LINE FEEDER | CB | CB MANUAL OPEN | SPS | MNOP
6 | ABC | LINE FEEDER | CB | CB MANUAL CLOSE | SPS | MNCL
7 | ABC | LINE FEEDER | CB | LBB PROTECTION OPERATED | SPS | LBBO
8 | ABC | LINE FEEDER | CB | OPERATION LOCKOUT | SPS | OPLO
9 | ABC | LINE FEEDER | CB | CB POLE DISCREPANCY OPERATED | SPS | PDIS
10 | ABC | LINE FEEDER | CB | CB POLE DISCREPANCY WITH IN POLE OPERATED | SPS | PDIB
11 | ABC | LINE FEEDER | CB | CB DC SUPPLY 1/2 FAIL | SPS | DC
12 | ABC | LINE FEEDER | CB | CB AC SUPPLY FAIL | SPS | ACSP
13 | ABC | LINE FEEDER | CB | CB SPRING DISCHARGE | SPS | SPRG
14 | ABC | LINE FEEDER | CB | CB SF6 LOW ALARM | SPS | SF6L
15 | ABC | LINE FEEDER | CB | CB TC1 Faulty | SPS | TC1F
16 | ABC | LINE FEEDER | CB | CB TC2 Faulty | SPS | TC2F
17 | ABC | LINE FEEDER | CB | AUTORECLOSE LOCKOUT | SPS | ARLO
18 | ABC | LINE FEEDER | CB | AUTORECLOSE OPERATED | SPS | AROP
17 | ABC | LINE FEEDER | CB | CB IN LOCAL/REMOTE | SPS | CBLM
19 | ABC | LINE FEEDER | LINE | AUTORECLOSE UNSUCCESFUL | SPS | ARFM
20 | ABC | LINE FEEDER | LINE | MAIN-1 PROTECTION OPERATED | SPS | M1OP
21 | ABC | LINE FEEDER | LINE | MAIN-1 DISTANCE PROTECTION ZONE1 TRIP | SPS | M1Z1
22 | ABC | LINE FEEDER | LINE | MAIN-1 DISTANCE PROTECTION ZONE2 TRIP | SPS | M1Z2
23 | ABC | LINE FEEDER | LINE | MAIN-1 DISTANCE PROTECTION ZONE3 TRIP | SPS | M1Z3
24 | ABC | LINE FEEDER | LINE | MAIN-1 DISTANCE PROTECTION REVERSE ZONE TRIP | SPS | M1RP
25 | ABC | LINE FEEDER | LINE | MAIN-1 A/R BLOCK | SPS | M1AR
26 | ABC | LINE FEEDER | LINE | MAIN-1 CVT FUSE FAILURE | SPS | M1FU
27 | ABC | LINE FEEDER | LINE | MAIN-1 RELAY FAULTY | SPS | M1UH
28 | ABC | LINE FEEDER | LINE | MAIN-1 DEF OPERATED | SPS | M1DE
29 | ABC | LINE FEEDER | LINE | MAIN-1 SOTF OPERATED | SPS | M1SO
30 | ABC | LINE FEEDER | LINE | MAIN-1 CARRIER SEND CH-1 | SPS | CAR7
31 | ABC | LINE FEEDER | LINE | MAIN-1 CARRIER SEND CH-2 | SPS | CAR8
32 | ABC | LINE FEEDER | LINE | MAIN-1 CARRIED RECD CH-1 | SPS | CAR3
33 | ABC | LINE FEEDER | LINE | MAIN-1 CARRIED RECD CH-2 | SPS | CAR5
34 | ABC | LINE FEEDER | LINE | MAIN-1 CARRIER AIDED TRIP | SPS | CAT1
35 | ABC | LINE FEEDER | LINE | MAIN-1 CARRIER SWITCH IN OUT OF SERVICE | SPS | CAS1
36 | ABC | LINE FEEDER | LINE | MAIN-2 PROTECTION OPERATED | SPS | M2OP
37 | ABC | LINE FEEDER | LINE | MAIN-2 DISTANCE PROTECTION ZONE1 TRIP | SPS | M2Z1
38 | ABC | LINE FEEDER | LINE | MAIN-2 DISTANCE PROTECTION ZONE2 TRIP | SPS | M2Z2
39 | ABC | LINE FEEDER | LINE | MAIN-2 DISTANCE PROTECTION ZONE3 TRIP | SPS | M2Z3
40 | ABC | LINE FEEDER | LINE | MAIN-2 DISTANCE PROTECTION REVERSE ZONE TRIP | SPS | M2RP
41 | ABC | LINE FEEDER | LINE | MAIN-2 A/R BLOCK | SPS | M2AR
42 | ABC | LINE FEEDER | LINE | MAIN-2 CVT FUSE FAILURE | SPS | M2FU
43 | ABC | LINE FEEDER | LINE | MAIN-2 RELAY FAULTY | SPS | M2UH
44 | ABC | LINE FEEDER | LINE | MAIN-2 DEF OPERATED | SPS | M2DE
45 | ABC | LINE FEEDER | LINE | MAIN-2 SOTF OPERATED | SPS | M2SO
46 | ABC | LINE FEEDER | LINE | MAIN-2 CARRIER SEND CH-1 | SPS | CAR9
47 | ABC | LINE FEEDER | LINE | MAIN-2 CARRIER SEND CH-2 | SPS | CARS
48 | ABC | LINE FEEDER | LINE | MAIN-2 CARRIED RECD CH-1 | SPS | CAR4
49 | ABC | LINE FEEDER | LINE | MAIN-2 CARRIED RECD CH-2 | SPS | CAR6
50 | ABC | LINE FEEDER | LINE | MAIN-2 CARRIER AIDED TRIP | SPS | CAT2
51 | ABC | LINE FEEDER | LINE | MAIN-2 CARRIER SWITCH IN OUT OF SERVICE | SPS | CAS2
52 | ABC | LINE FEEDER | LINE | MAIN-1 BB PROTECTION OPTD | SPS | BB1P
53 | ABC | LINE FEEDER | LINE | MAIN-2 BB PROTECTION OPTD | SPS | BB2P
54 | ABC | LINE FEEDER | LINE | MAIN-1 BB PU UNIT FAULTY | SPS | B1UH
55 | ABC | LINE FEEDER | LINE | MAIN-2 BB PU UNIT FAULTY | SPS | B2UH
56 | ABC | LINE FEEDER | LINE | DIRECT TRIP SEND CHANNEL 1 | SPS | TRS1
57 | ABC | LINE FEEDER | LINE | DIRECT RECEIVED CHANNEL 1 | SPS | TRP1
58 | ABC | LINE FEEDER | LINE | DIRECT TRIP SEND CHANNEL 2 | SPS | TRS2
59 | ABC | LINE FEEDER | LINE | DIRECT RECEIVED CHANNEL 2 | SPS | TRP2
60 | ABC | LINE FEEDER | LINE | 86A TRIP RELAY OPERATED | SPS | 86AO
61 | ABC | LINE FEEDER | LINE | 86B TRIP RELAY OPERATED | SPS | 86BO
62 | ABC | LINE FEEDER | LINE | 86A TRIP RELAY FAULTY | SPS | 86AU
63 | ABC | LINE FEEDER | LINE | 86B TRIP RELAY FAULTY | SPS | 86BU
64 | ABC | LINE FEEDER | LINE | CARRIER FAIL CH-1 | SPS | CAF1
65 | ABC | LINE FEEDER | LINE | CARRIER FAIL CH-2 | SPS | CAF2
66 | ABC | LINE FEEDER | LINE | DC SOURCE-1 FAIL | SPS | DC-1
67 | ABC | LINE FEEDER | LINE | DC SOURCE-2 FAIL | SPS | DC-2
68 | ABC | LINE FEEDER | LINE | MAIN-1 PSB DETECTED | SPS | PSB1
69 | ABC | LINE FEEDER | LINE | MAIN-1 STUB PROTN OPERATED | SPS | STUB
70 | ABC | LINE FEEDER | LINE | MAIN-1 O/V STAGE-1 TRIP | SPS | OV-1
71 | ABC | LINE FEEDER | LINE | MAIN-1 O/V STAGE-2 TRIP | SPS | OV-12
72 | ABC | LINE FEEDER | LINE | MAIN-2 PSB DETECTED | SPS | PSB2
73 | ABC | LINE FEEDER | LINE | MAIN-2 STUB PROTECTION OPERATED | SPS | STUP
74 | ABC | LINE FEEDER | LINE | MAIN-2 O/V STAGE-1 TRIP | SPS | OV-3
75 | ABC | LINE FEEDER | LINE | MAIN-2 O/V STAGE-2 TRIP | SPS | OV-4
76 | ABC | LINE FEEDER | LINE | MAIN-1 LINE DIFFERENTIAL PROTECTION OPERATED | SPS
77 | ABC | LINE FEEDER | LINE | MAIN-2 LINE DIFFERENTIAL PROTECTION OPERATED | SPS
78 | ABC | LINE FEEDER | LINE | 89L OPERATED FOR STUB M1 | SPS
79 | ABC | LINE FEEDER | LINE | 89L OPERATED FOR STUB M2 | SPS
80 | ABC | LINE FEEDER | LINE | SPEECH CHANNEL FAIL | SPS
81 | ABC | LINE FEEDER | LINE | CB MCB TRIPPED ( Motor/Heating/Lighting) | SPS
82 | ABC | LINE FEEDER | LINE | MAIN-1 DIFFERENTIAL PROTN TRIP R PH | SPS
83 | ABC | LINE FEEDER | LINE | MAIN-1 DIFFERENTIAL PROTN TRIP Y PH | SPS
84 | ABC | LINE FEEDER | LINE | MAIN-1 DIFFERENTIAL PROTN TRIP B PH | SPS
85 | ABC | LINE FEEDER | LINE | MAIN-2 DIFFERENTIAL PROTN TRIP R PH | SPS
86 | ABC | LINE FEEDER | LINE | MAIN-2 DIFFERENTIAL PROTN TRIP Y PH | SPS
87 | ABC | LINE FEEDER | LINE | MAIN-2 DIFFERENTIAL PROTN TRIP B PH | SPS
88 | ABC | LINE FEEDER | LINE | MAIN-1 DIFFERENTIATED WAVE BLOCK | SPS
89 | ABC | LINE FEEDER | LINE | MAIN-1 DIFFERENTIATED HORMONICS BLOCK | SPS
90 | ABC | LINE FEEDER | LINE | MAIN-2 DIFFERENTIATED WAVE BLOCK | SPS
91 | ABC | LINE FEEDER | LINE | MAIN-2 DIFFERENTIATED HORMONICS BLOCK | SPS
92 | ABC | LINE FEEDER | LINE | MAIN-1 DIFFERENTIATED RESTRAIN TRIP | SPS
93 | ABC | LINE FEEDER | LINE | MAIN-2 DIFFERENTIATED RESTRAIN TRIP | SPS
94 | ABC | LINE FEEDER | LINE | MAIN-1 DIFFERENTIATED UNRESTRAIN TRIP | SPS
95 | ABC | LINE FEEDER | LINE | MAIN-2 DIFFERENTIATED UNRESTRAIN TRIP | SPS
96 | ABC | LINE FEEDER | LINE | MAIN-1 BROKEN CONDUCTOR ALARM | SPS
97 | ABC | LINE FEEDER | LINE | MAIN-2 BROKEN CONDUCTOR ALARM | SPS
98 | ABC | LINE FEEDER | LINE | Autoreclosure Block | SPS
99 | ABC | LINE FEEDER | CB | INTERLOCK ENABLED | SPS | INTL
100 | ABC | LINE FEEDER | 89A | INTERLOCK ENABLED | SPS | INTL
101 | ABC | LINE FEEDER | 89B | INTERLOCK ENABLED | SPS | INTL
102 | ABC | LINE FEEDER | 89L | INTERLOCK ENABLED | SPS | INTL
103 | ABC | LINE FEEDER | 89AE1 | INTERLOCK ENABLED | SPS | INTL | Bus Earth Switch
104 | ABC | LINE FEEDER | 89AE2 | INTERLOCK ENABLED | SPS | INTL
105 | ABC | LINE FEEDER | 89BE | INTERLOCK ENABLED | SPS | INTL
106 | ABC | LINE FEEDER | 89LE | INTERLOCK ENABLED | SPS | INTL
107 | ABC | LINE FEEDER | CB | CB PUMP RUNTIME EXCEEDED | SPS |  | For GIS Line Feeder Bays
108 | ABC | LINE FEEDER | CB | DE DRIVE STATUS ALARM | SPS
109 | ABC | LINE FEEDER | CB | CRANK HANDLE INSERTED | SPS
110 | ABC | LINE FEEDER |  | PARTIAL DISCHARGE HIGH ALARM | SPS
111 | ABC | LINE FEEDER |  | LCC IN LOCAL MODE | SPS
112 | ABC | LINE FEEDER |  | LCC IN REMOTE MODE | SPS
113 | ABC | LINE FEEDER |  | BAY INTERLOCK BYPASS SELECTED | SPS
114 | ABC | LINE FEEDER |  | GAS LKG R/Y/B STG1 REFILL | SPS | SF61
115 | ABC | LINE FEEDER |  | GAS LKG R/Y/B STG2 LOW | SPS | SF62
116 | ABC | LINE FEEDER |  | GAS LKG R/Y/B ZONE TRIP | SPS | SF6T
117 | ABC | LINE FEEDER |  | GAS LKG R/Y/B CB LOCKOUT/CB OPERATION LOCKOUT | SPS | SF6T
765 KV/ 400 KV LINE REACTOR/ BUS REACTOR
1 | ABC | LINE REACTOR/ BUS REACTOR | BCU | BAY IN MAINTENANCE MODE | SPS | BAYM
2 | ABC | LINE REACTOR/ BUS REACTOR | BCU | BCU DC SUPPLY FAIL-1/2 | SPS | BCUD
3 | ABC | LINE REACTOR/ BUS REACTOR | BCU | BCU UNHEALTHY | SPS | BCUH
4 | ABC | LINE REACTOR/ BUS REACTOR | BCU | BCU TIME SYNC ERROR | SPS | BCUC
5 | ABC | LINE REACTOR/ BUS REACTOR | 52R | CB MANUAL OPEN | SPS | MNOP | Required if reactor is switchable
6 | ABC | LINE REACTOR/ BUS REACTOR | 52R | CB MANUAL CLOSE | SPS | MNCL
7 | ABC | LINE REACTOR/ BUS REACTOR | 52R | LBB PROTECTION OPERATED | SPS | LBBO
8 | ABC | LINE REACTOR/ BUS REACTOR | 52R | OPERATION LOCKOUT | SPS | OPLO
9 | ABC | LINE REACTOR/ BUS REACTOR | 52R | CB POLE DISCREPANCY OPERATED | SPS | PDIS
10 | ABC | LINE REACTOR/ BUS REACTOR | 52R | CB POLE DISCREPANCY WITH IN POLE OPERATED | SPS | PDIB
11 | ABC | LINE REACTOR/ BUS REACTOR | 52R | CB DC SUPPLY 1/2 FAIL | SPS | DC
12 | ABC | LINE REACTOR/ BUS REACTOR | 52R | CB AC SUPPLY FAIL | SPS | ACSP
13 | ABC | LINE REACTOR/ BUS REACTOR | 52R | CB SPRING DISCHARGE | SPS | SPRG
14 | ABC | LINE REACTOR/ BUS REACTOR | 52R | CB SF6 LOW ALARM | SPS | SF6L
15 | ABC | LINE REACTOR/ BUS REACTOR | 52R | CB TC1 Faulty | SPS | TC1F
16 | ABC | LINE REACTOR/ BUS REACTOR | 52R | CB TC2 Faulty | SPS | TC2F
17 | ABC | LINE REACTOR/ BUS REACTOR | RE | DIFFERENTIAL RELAY OPTD. | SPS | REDI
18 | ABC | LINE REACTOR/ BUS REACTOR | RE | B/U IMPEDANCE OPTD | SPS | BUIO
19 | ABC | LINE REACTOR/ BUS REACTOR | RE | REF OPTD | SPS | RERE
20 | ABC | LINE REACTOR/ BUS REACTOR | RE | B/U RELAY FAULTY | SPS | BURF
21 | ABC | LINE REACTOR/ BUS REACTOR | RE | DIFFERENTIAL RELAY FAULTY | SPS | DIRU
22 | ABC | LINE REACTOR/ BUS REACTOR | RE | SELECTED VT FUSE FAIL ALARM | SPS | VTFU
23 | ABC | LINE REACTOR/ BUS REACTOR | RE | REACTOR 86A TRIP RELAY OPERATED | SPS | GRAO
24 | ABC | LINE REACTOR/ BUS REACTOR | RE | REACTOR 86B TRIP RELAY OPERATED | SPS | GRBO
25 | ABC | LINE REACTOR/ BUS REACTOR | RE | REACTOR 86A TRIP RELAY FAULTY | SPS | GRAU
26 | ABC | LINE REACTOR/ BUS REACTOR | RE | REACTOR 86B TRIP RELAY FAULTY | SPS | GRBU
27 | ABC | LINE REACTOR/ BUS REACTOR | RE | MAIN-1 BB PROTECTION OPTD | SPS | BB1P
28 | ABC | LINE REACTOR/ BUS REACTOR | RE | MAIN-2 BB PROTECTION OPTD | SPS | BB2P
29 | ABC | LINE REACTOR/ BUS REACTOR | RE | MAIN-1 BB PU UNIT FAULTY | SPS | B1UH
30 | ABC | LINE REACTOR/ BUS REACTOR | RE | MAIN-2 BB PU UNIT FAULTY | SPS | B2UH
31 | ABC | LINE REACTOR/ BUS REACTOR | RE | DC SOURCE-1 FAIL | SPS | DC-1
32 | ABC | LINE REACTOR/ BUS REACTOR | RE | DC SOURCE-2 FAIL | SPS | DC-2
33 | ABC | LINE REACTOR/ BUS REACTOR | RE | Oil level low alarm R phase | SPS | REOL | 3 PHASE STATUS IS REQUIRED IF LINE REACTOR/ BUS REACTOR IS 3 PHASE
34 | ABC | LINE REACTOR/ BUS REACTOR | RE | MOISTURE ALARM in R phase | SPS | MOSA
35 | ABC | LINE REACTOR/ BUS REACTOR | RE | BUCHOLTZ ALARM_R PHASE | SPS | BUCA
36 | ABC | LINE REACTOR/ BUS REACTOR | RE | BUCHOLTZ TRIP_R PHASE | SPS | BUCT
37 | ABC | LINE REACTOR/ BUS REACTOR | RE | SHUT_OFF_VALVE TRIP R PHASE | SPS | VLVT
38 | ABC | LINE REACTOR/ BUS REACTOR | RE | WTI ALARM_R PHASE | SPS | WTIA
39 | ABC | LINE REACTOR/ BUS REACTOR | RE | WTI_TRIP_R PHASE | SPS | WTIT
40 | ABC | LINE REACTOR/ BUS REACTOR | RE | OTI_ALARM_R_PHASE | SPS | OTIA
41 | ABC | LINE REACTOR/ BUS REACTOR | RE | OTI_TRIP_R_PHASE | SPS | OTIT
42 | ABC | LINE REACTOR/ BUS REACTOR | RE | PRV_TRIP_1_R_PHASE | SPS | REPR
43 | ABC | LINE REACTOR/ BUS REACTOR | RE | PRV_TRIP_2_R_PHASE | SPS | PRV2
44 | ABC | LINE REACTOR/ BUS REACTOR | RE | FIRE PROTN OPTD R PHASE | SPS | FRRR
45 | ABC | LINE REACTOR/ BUS REACTOR | RE | DELUGE VALVE ON - R PHASE | SPS | DVRR
46 | ABC | LINE REACTOR/ BUS REACTOR | RE | DGA MONITORING DEVICE UNHEALTHY | SPS | DGAM
47 | ABC | LINE REACTOR/ BUS REACTOR | RE | SPARE REACTOR SELECT FOR R PHASE | SPS | SPRE
48 | ABC | LINE REACTOR/ BUS REACTOR | RE | Oil level Low Alarm Y PHASE | SPS | REOL
49 | ABC | LINE REACTOR/ BUS REACTOR | RE | MOISTURE ALARM in Y PHASE | SPS | MOSA
50 | ABC | LINE REACTOR/ BUS REACTOR | RE | BUCHOLTZ ALARM_Y PHASE | SPS | BUCA
51 | ABC | LINE REACTOR/ BUS REACTOR | RE | BUCHOLTZ TRIP_Y PHASE | SPS | BUCT
52 | ABC | LINE REACTOR/ BUS REACTOR | RE | SHUT_OFF_VALVE TRIP Y PHASE | SPS | VLVT
53 | ABC | LINE REACTOR/ BUS REACTOR | RE | WTI ALARM_Y PHASE | SPS | WTIA
54 | ABC | LINE REACTOR/ BUS REACTOR | RE | WTI_TRIP_Y PHASE | SPS | WTIT
55 | ABC | LINE REACTOR/ BUS REACTOR | RE | OTI_ALARM_Y PHASE | SPS | OTIA
56 | ABC | LINE REACTOR/ BUS REACTOR | RE | OTI_TRIP_Y PHASE | SPS | OTIT
57 | ABC | LINE REACTOR/ BUS REACTOR | RE | PRV_TRIP_1_Y PHASE | SPS | REPR
58 | ABC | LINE REACTOR/ BUS REACTOR | RE | PRV_TRIP_2_Y PHASE | SPS | PRV2
59 | ABC | LINE REACTOR/ BUS REACTOR | RE | FIRE PROTN OPTD Y PHASE | SPS | FRRY
60 | ABC | LINE REACTOR/ BUS REACTOR | RE | DELUGE VALVE ON - Y PHASE | SPS | DVRY
61 | ABC | LINE REACTOR/ BUS REACTOR | RE | DGA MONITORING DEVICE UNHEALTHY | SPS
62 | ABC | LINE REACTOR/ BUS REACTOR | RE | SPARE REACTOR SELECT FOR Y PHASE | SPS | SPRE
63 | ABC | LINE REACTOR/ BUS REACTOR | RE | Oil level low alarm B PHASE | SPS | REOL
64 | ABC | LINE REACTOR/ BUS REACTOR | RE | MOISTURE ALARM in B PHASE | SPS | MOSA
65 | ABC | LINE REACTOR/ BUS REACTOR | RE | BUCHOLTZ ALARM_B PHASE | SPS | BUCA
66 | ABC | LINE REACTOR/ BUS REACTOR | RE | BUCHOLTZ TRIP_B PHASE | SPS | BUCT
67 | ABC | LINE REACTOR/ BUS REACTOR | RE | SHUT_OFF_VALVE TRIP B PHASE | SPS | VLVT
68 | ABC | LINE REACTOR/ BUS REACTOR | RE | WTI ALARM_B PHASE | SPS | WTIA
69 | ABC | LINE REACTOR/ BUS REACTOR | RE | WTI_TRIP_B PHASE | SPS | WTIT
70 | ABC | LINE REACTOR/ BUS REACTOR | RE | OTI_ALARM_B PHASE | SPS | OTIA
71 | ABC | LINE REACTOR/ BUS REACTOR | RE | OTI_TRIP_B PHASE | SPS | OTIT
72 | ABC | LINE REACTOR/ BUS REACTOR | RE | PRV_TRIP_1_B PHASE | SPS | REPR
73 | ABC | LINE REACTOR/ BUS REACTOR | RE | PRV_TRIP_2_B PHASE | SPS | PRV2
74 | ABC | LINE REACTOR/ BUS REACTOR | RE | FIRE PROTN OPTD B PHASE | SPS | FRRR
75 | ABC | LINE REACTOR/ BUS REACTOR | RE | DELUGE VALVE ON - B PHASE | SPS | DVRB
76 | ABC | LINE REACTOR/ BUS REACTOR | RE | DGA MONITORING DEVICE UNHEALTHY | SPS
77 | ABC | LINE REACTOR/ BUS REACTOR | RE | SPARE REACTOR SELECT FOR B PHASE | SPS | SPRE
78 | ABC | LINE REACTOR/ BUS REACTOR | RE | TEED PROTECTION OPTD | SPS
79 | ABC | LINE REACTOR/ BUS REACTOR | RE | TEED RELAY FAULTY | SPS
80 | ABC | LINE REACTOR/ BUS REACTOR | CB | INTERLOCK ENABLED | SPS | INTL | Applicable in case of Bus Reactor
81 | ABC | LINE REACTOR/ BUS REACTOR | 89A | INTERLOCK ENABLED | SPS | INTL
82 | ABC | LINE REACTOR/ BUS REACTOR | 89B | INTERLOCK ENABLED | SPS | INTL
83 | ABC | LINE REACTOR/ BUS REACTOR | 89AE | INTERLOCK ENABLED | SPS | INTL
84 | ABC | LINE REACTOR/ BUS REACTOR | 89BE | INTERLOCK ENABLED | SPS | INTL
85 | ABC | LINE REACTOR/ BUS REACTOR | 52R | INTERLOCK ENABLED | SPS | INTL
86 | ABC | LINE REACTOR/ BUS REACTOR | 89RR | INTERLOCK ENABLED | SPS | INTL
87 | ABC | LINE REACTOR/ BUS REACTOR | 89RY | INTERLOCK ENABLED | SPS | INTL
88 | ABC | LINE REACTOR/ BUS REACTOR | 89RB | INTERLOCK ENABLED | SPS | INTL
89 | ABC | LINE REACTOR/ BUS REACTOR | 89RS1R | INTERLOCK ENABLED | SPS | INTL
90 | ABC | LINE REACTOR/ BUS REACTOR | 89RS1Y | INTERLOCK ENABLED | SPS | INTL
91 | ABC | LINE REACTOR/ BUS REACTOR | 89RS1B | INTERLOCK ENABLED | SPS | INTL
92 | ABC | LINE REACTOR/ BUS REACTOR | 89RER | INTERLOCK ENABLED | SPS | INTL
93 | ABC | LINE REACTOR/ BUS REACTOR | 89REY | INTERLOCK ENABLED | SPS | INTL
94 | ABC | LINE REACTOR/ BUS REACTOR | 89REB | INTERLOCK ENABLED | SPS | INTL
95 | ABC | LINE REACTOR/ BUS REACTOR | 52R | CONTROL SWITCH DEVICE BYPASSED | SPS | BYSW
96 | ABC | LINE REACTOR/ BUS REACTOR | 52R | CONTROL SWITCH DEVICE TROUBLE | SPS
97 | ABC | LINE REACTOR/ BUS REACTOR | CB | CB PUMP RUNTIME EXCEEDED | SPS |  | FOR GIS BAYS
98 | ABC | LINE REACTOR/ BUS REACTOR | CB | DE DRIVE STATUS ALARM | SPS
99 | ABC | LINE REACTOR/ BUS REACTOR | CB | CRANK HANDLE INSERTED | SPS
100 | ABC | LINE REACTOR/ BUS REACTOR |  | GAS LKG R/Y/B STG1 REFILL | SPS | SF61
101 | ABC | LINE REACTOR/ BUS REACTOR |  | GAS LKG R/Y/B STG2 LOW | SPS | SF62
102 | ABC | LINE REACTOR/ BUS REACTOR |  | GAS LKG R/Y/B ZONE TRIP | SPS | SF6T
103 | ABC | LINE REACTOR/ BUS REACTOR |  | GAS LKG R/Y/B CB LOCKOUT/CB OPERATION LOCKOUT | SPS | SF6T
NGR
1 | ABC | LINE FEEDER WITH REACTOR | NGR | BUCHHOLZ TRIP(NGR) | SPS | BUCT
2 | ABC | LINE FEEDER WITH REACTOR | NGR | REACTOR PRV TRIP(NGR) | SPS | REPR
3 | ABC | LINE FEEDER WITH REACTOR | NGR | OTI TRIP(NGR) | SPS | OTIT
4 | ABC | LINE FEEDER WITH REACTOR | NGR | OTI ALARM(NGR) | SPS | OTIA
5 | ABC | LINE FEEDER WITH REACTOR | NGR | BUCHHOLZ ALARM(NGR) | SPS | BUCA
6 | ABC | LINE FEEDER WITH REACTOR | NGR | LOW OIL LEVEL ALARM(NGR) | SPS | REOL
7 | ABC | LINE FEEDER WITH REACTOR | NGR | OPERATION LOCKOUT | SPS | OPLO
8 | ABC | LINE FEEDER WITH REACTOR | 52NGR | CB AC SUPPLY FAIL | SPS | ACSP
9 | ABC | LINE FEEDER WITH REACTOR | 52NGR | CB SPRING DISCHARGE | SPS | SPRG
10 | ABC | LINE FEEDER WITH REACTOR | 52NGR | CB SF6 LOW ALARM | SPS | SF6L
11 | ABC | LINE FEEDER WITH REACTOR | 52NGR | CB TC1 Faulty | SPS | TC1F
12 | ABC | LINE FEEDER WITH REACTOR | 52NGR | CB TC2 Faulty | SPS | TC2F
SPARE LINE REACTOR
1 | ABC | SPARE LINE REACTOR | RE | Oil level low alarm SPARE | SPS | REOL
2 | ABC | SPARE LINE REACTOR | RE | MOISTURE ALARM in SPARE | SPS | MOSA
3 | ABC | SPARE LINE REACTOR | RE | BUCH1/2_ALARM_SPARE | SPS | BUCA
4 | ABC | SPARE LINE REACTOR | RE | BUCH1/2 TRIP_SPARE | SPS | BUCT
5 | ABC | SPARE LINE REACTOR | RE | SHUT_OFF_VALVE TRIP SPARE | SPS | VLVT
6 | ABC | SPARE LINE REACTOR | RE | WTI ALARM_SPARE | SPS | WTIA
7 | ABC | SPARE LINE REACTOR | RE | WTI_TRIP_SPARE | SPS | WTIT
8 | ABC | SPARE LINE REACTOR | RE | OTI_ALARM_SPARE | SPS | OTIA
9 | ABC | SPARE LINE REACTOR | RE | OTI_TRIP_SPARE | SPS | OTIT
10 | ABC | SPARE LINE REACTOR | RE | PRV_TRIP_1_SPARE | SPS | REPR
11 | ABC | SPARE LINE REACTOR | RE | PRV_TRIP_2_SPARE | SPS | PRV2
12 | ABC | SPARE LINE REACTOR | RE | FIRE PROTN OPTD SPARE PHASE | SPS | FRRS
13 | ABC | SPARE LINE REACTOR | RE | DELUGE VALVE ON SPARE | SPS | DVRS
84 | ABC | SPARE LINE REACTOR |  | GAS LKG R/Y/B STG1 REFILL | SPS | SF61 | For GIS Bays
86 | ABC | SPARE LINE REACTOR |  | GAS LKG R/Y/B ZONE TRIP | SPS | SF6T
765 KV/ 400KV TIE/ BUS SECTION BAY
1 | ABC | TIE/ BS | BCU | BAY IN MAINTENANCE MODE | SPS | BAYM
2 | ABC | TIE/ BS | BCU | BCU DC SUPPLY FAIL-1/2 | SPS | BCUD
3 | ABC | TIE/ BS | BCU | BCU UNHEALTHY | SPS | BCUH
4 | ABC | TIE/ BS | BCU | BCU TIME SYNC ERROR | SPS | BCUC
5 | ABC | TIE/ BS | CB | CB MANUAL OPEN | SPS | MNOP
6 | ABC | TIE/ BS | CB | CB MANUAL CLOSE | SPS | MNCL
7 | ABC | TIE/ BS | CB | LBB PROTECTION OPERATED | SPS | LBBO
8 | ABC | TIE/ BS | CB | OPERATION LOCKOUT | SPS | OPLO
9 | ABC | TIE/ BS | CB | CB POLE DISCREPANCY OPERATED | SPS | PDIS
10 | ABC | TIE/ BS | CB | CB POLE DISCREPANCY WITH IN POLE OPERATED | SPS | PDIB
11 | ABC | TIE/ BS | CB | CB DC SUPPLY 1/2 FAIL | SPS | DC
12 | ABC | TIE/ BS | CB | CB AC SUPPLY FAIL | SPS | ACSP
13 | ABC | TIE/ BS | CB | CB SPRING DISCHARGE | SPS | SPRG
14 | ABC | TIE/ BS | CB | CB SF6 LOW ALARM | SPS | SF6L
15 | ABC | TIE/ BS | CB | CB TC1 Faulty | SPS | TC1F
16 | ABC | TIE/ BS | CB | CB TC2 Faulty | SPS | TC2F
17 | ABC | TIE/ BS | CB | AUTORECLOSE LOCKOUT | SPS | ARLO
18 | ABC | TIE/ BS | CB | AUTORECLOSE OPERATED | SPS | AROP
19 | ABC | TIE/ BS | LINE | AUTORECLOSE UNSUCCESFUL | SPS | ARFT
20 | ABC | TIE/ BS | CB | 86A TRIP RELAY OPERATED | SPS | 86AO
21 | ABC | TIE/ BS | CB | 86B TRIP RELAY OPERATED | SPS | 86BO
22 | ABC | TIE/ BS | CB | 86A TRIP RELAY FAULTY | SPS | 86AU
23 | ABC | TIE/ BS | CB | 86B TRIP RELAY FAULTY | SPS | 86BU
24 | ABC | TIE | CB | CONTROL SWITCH DEVICE BYPASSED | SPS | BYSW | In case of Line Reactor/ Bus Reactor/ ICT in main bays
25 | ABC | TIE | CB | CONTROL SWITCH DEVICE TROUBLE | SPS
26 | ABC | TIE/ BS | CB | INTERLOCK ENABLED | SPS | INTL
27 | ABC | TIE/ BS | 89A | INTERLOCK ENABLED | SPS | INTL
28 | ABC | TIE/ BS | 89B | INTERLOCK ENABLED | SPS | INTL
29 | ABC | TIE/ BS | 89AE1 | INTERLOCK ENABLED | SPS | INTL
30 | ABC | TIE/ BS | 89AE2 | INTERLOCK ENABLED | SPS | INTL
31 | ABC | TIE/ BS | 89BE1 | INTERLOCK ENABLED | SPS | INTL
32 | ABC | TIE/ BS | 89BE2 | INTERLOCK ENABLED | SPS | INTL
33 | ABC | TIE/ BS |  | GAS LKG R/Y/B STG1 REFILL | SPS | SF61 | For GIS Bays
34 | ABC | TIE/ BS |  | GAS LKG R/Y/B STG2 LOW | SPS | SF62
35 | ABC | TIE/ BS |  | GAS LKG R/Y/B ZONE TRIP | SPS | SF6T
36 | ABC | TIE/ BS |  | GAS LKG R/Y/B CB LOCKOUT/CB OPERATION LOCKOUT | SPS | SF6T
765 KV / 400 KV/ 220 KV FUTURE BAY
1 | ABC | FUTURE LINE | BCU | BAY IN MAINTENANCE MODE | SPS | BAYM
2 | ABC | FUTURE LINE | BCU | BCU DC SUPPLY FAIL-1/2 | SPS | BCUD
3 | ABC | FUTURE LINE | BCU | BCU UNHEALTHY | SPS | BCUH
4 | ABC | FUTURE LINE | BCU | BCU TIME SYNC ERROR | SPS | BCUC
5 | ABC | FUTURE LINE | 89A | INTERLOCK ENABLED | SPS | INTL
6 | ABC | FUTURE LINE | 89AE | INTERLOCK ENABLED | SPS | INTL
ICT (PRIMARY SIDE)
1 | ABC | ICT | BCU | BAY IN MAINTENANCE MODE | SPS | BAYM
2 | ABC | ICT | BCU | BCU DC SUPPLY FAIL-1/2 | SPS | BCUD
3 | ABC | ICT | BCU | BCU UNHEALTHY | SPS | BCUH
4 | ABC | ICT | BCU | BCU TIME SYNC ERROR | SPS | BCUC
5 | ABC | ICT | CB | CB MANUAL OPEN | SPS | MNOP
6 | ABC | ICT | CB | CB MANUAL CLOSE | SPS | MNCL
7 | ABC | ICT | CB | LBB PROTECTION OPERATED | SPS | LBBO
8 | ABC | ICT | CB | OPERATION LOCKOUT | SPS | OPLO
9 | ABC | ICT | CB | CB POLE DISCREPANCY OPERATED | SPS | PDIS
10 | ABC | ICT | CB | CB POLE DISCREPANCY WITH IN POLE OPERATED | SPS | PDIB
11 | ABC | ICT | CB | CB DC SUPPLY 1/2 FAIL | SPS | DC
12 | ABC | ICT | CB | CB AC SUPPLY FAIL | SPS | ACSP
13 | ABC | ICT | CB | CB SPRING DISCHARGE | SPS | SPRG
14 | ABC | ICT | CB | CB SF6 LOW ALARM | SPS | SF6L
15 | ABC | ICT | CB | CB TC1 Faulty | SPS | TC1F
16 | ABC | ICT | CB | CB TC2 Faulty | SPS | TC2F
17 | ABC | ICT | CB | CONTROL SWITCH DEVICE BYPASSED | SPS | BYSW
18 | ABC | ICT | CB | CONTROL SWITCH DEVICE TROUBLE | SPS
19 | ABC | ICT | XFMR_P | DIFFERENTIAL RELAY OPTD. | SPS | TFDI
20 | ABC | ICT | XFMR_P | DIFF RELAY UNHEALTHY | SPS | DIRU
21 | ABC | ICT | XFMR_P | OVERFLUX ALARM | SPS | OFLA
22 | ABC | ICT | XFMR_P | OVERFLUX TRIP OPTD | SPS | OFLP
23 | ABC | ICT | XFMR_P | BACKUP O/C, E/F OPTD (HV) | SPS | BUOC
24 | ABC | ICT | XFMR_P | BACKUP O/C E/F RELAY UNHEALTHY | SPS | CFRL
25 | ABC | ICT | XFMR_P | 86A TRIP RELAY OPERATED | SPS | 86AO
26 | ABC | ICT | XFMR_P | 86B TRIP RELAY OPERATED | SPS | 86BO
27 | ABC | ICT | XFMR_P | 86A TRIP REALY UNHEALTHY | SPS | 86AU
28 | ABC | ICT | XFMR_P | 86B TRIP REALY UNHEALTHY | SPS | 86BU
29 | ABC | ICT | XFMR_P | SELECTED VT FUSE FAIL ALARM | SPS | VTFU
30 | ABC | ICT | XFMR_P | INTERTRIP OPTD. | SPS | TRPO
31 | ABC | ICT | XFMR_P | MAIN-1 BB PROTECTION OPTD | SPS | BB1P
32 | ABC | ICT | XFMR_P | MAIN-2 BB PROTECTION OPTD | SPS | BB2P
33 | ABC | ICT | XFMR_P | MAIN-1 BB PU UNIT FAULTY | SPS | B1UH
34 | ABC | ICT | XFMR_P | MAIN-2 BB PU UNIT FAULTY | SPS | B2UH
35 | ABC | ICT | XFMR_P | DC SOURCE-1 FAIL | SPS | DC-1
36 | ABC | ICT | XFMR_P | DC SOURCE-2 FAIL | SPS | DC-2
37 | ABC | ICT | XFMR_P | TAP CHANGER IN PROGRESS | SPS | TCIP
38 | ABC | ICT | XFMR_P | TAP CHANGER IN REMOTE | SPS | TCIR
39 | ABC | ICT | XFMR_P | TAP CHANGER OUT OF STEP | SPS | TCOS
40 | ABC | ICT | XFMR_P | TAP CHANGER PHASE DISCREPANCY | SPS | TCPD
41 | ABC | ICT | XFMR_P | TAP CHANGER IN FOLLOWER MODE | SPS | TCIF
42 | ABC | ICT | XFMR_P | TAP CHANGER IN INDEPENDENT MODE | SPS | TCII
43 | ABC | ICT | XFMR_P | TAP CHANGER IN MASTER MODE+E362 | SPS | TCIM
44 | ABC | ICT | XFMR_P | REF OPTD R PHASE | SPS | TFRF | TO BE COMBINED IN CASE OF 3 PHASE ICT
45 | ABC | ICT | XFMR_P | BUCHHOLZ ALARM R PHASE | SPS | BUCA
46 | ABC | ICT | XFMR_P | BUCHHOLZ TRIP R PHASE | SPS | BUCT
47 | ABC | ICT | XFMR_P | OTI ALARM R PHASE | SPS | OTIA
48 | ABC | ICT | XFMR_P | OTI TRIP R PHASE | SPS | OTIT
49 | ABC | ICT | XFMR_P | WTI ALARM (HV/IV/LV) R PHASE | SPS | WTIA
50 | ABC | ICT | XFMR_P | WTI TRIP (HV/IV/LV) R PHASE | SPS | WTIT
51 | ABC | ICT | XFMR_P | PRV-1 TRIP R-PHASE | SPS | TFPR
52 | ABC | ICT | XFMR_P | PRV-2 TRIP R-PHASE | SPS | PRV2
53 | ABC | ICT | XFMR_P | OLTC OIL SURGE RELAY OPTD- R PHASE | SPS | OLTR
54 | ABC | ICT | XFMR_P | OLTC PRV TRIP OPTD- R PHASE | SPS | OLTP
55 | ABC | ICT | XFMR_P | OIL FLOW VALVE TRIP- R PHASE | SPS
56 | ABC | ICT | XFMR_P | FANS FAIL TO START BANK A - R PHASE | SPS | FANF
57 | ABC | ICT | XFMR_P | FANS FAIL TO START BANK B - R PHASE | SPS | FANB
58 | ABC | ICT | XFMR_P | PUMPS FAIL TO START BANK A - R PHASE | SPS | PMPF
59 | ABC | ICT | XFMR_P | PUMPS FAIL TO START BANK B - R PHASE | SPS | PMPB
60 | ABC | ICT | XFMR_P | OIL FLOW LOW ALARM BANK R PHASE | SPS | TFOL
61 | ABC | ICT | XFMR_P | COMMON THERMAL O/L ALARM R PHASE | SPS | OLAL
62 | ABC | ICT | XFMR_P | COMMON THERMAL O/L TRIP R PHASE | SPS | CTTP
63 | ABC | ICT | XFMR_P | STANDBY SUPLY FAIL R PHASE | SPS | SBSF
64 | ABC | ICT | XFMR_P | MOISTURE ALARM R PHASE | SPS | MOSA
65 | ABC | ICT | XFMR_P | DGA ALARM R PHASE | SPS | DGAA
66 | ABC | ICT | XFMR_P | FIRE IN TRANSFORMER R PHASE | SPS | FRTR
67 | ABC | ICT | XFMR_P | DELUGE VALVE OPTD - R PHASE | SPS | DVTR
68 | ABC | ICT | XFMR_P | OLTC OIL LEVEL ALARM R PHASE | SPS
69 | ABC | ICT | XFMR_P | DGA MONITORING DEVICE UNHEALTHY R PHASE | SPS
70 | ABC | ICT | XFMR_P | SPARE ICT SELECTED FOR R PHASE | SPS
71 | ABC | ICT | XFMR_P | REF OPTD Y PHASE | SPS
72 | ABC | ICT | XFMR_P | REF PROTN Y PHASE BLOCKED | SPS
73 | ABC | ICT | XFMR_P | BACKUP O/C OPTD (HV) Y PHASE | SPS | BUOC
74 | ABC | ICT | XFMR_P | BUCHHOLZ ALARM Y PHASE | SPS | BUCA
75 | ABC | ICT | XFMR_P | BUCHHOLZ TRIP Y PHASE | SPS | BUCT
76 | ABC | ICT | XFMR_P | OTI ALARM Y PHASE | SPS | OTIA
77 | ABC | ICT | XFMR_P | OTI TRIP Y PHASE | SPS | OTIT
78 | ABC | ICT | XFMR_P | WTI ALARM (HV/IV/LV) Y PHASE | SPS | WTIA
79 | ABC | ICT | XFMR_P | WTI TRIP (HV/IV/LV) Y PHASE | SPS | WTIT
80 | ABC | ICT | XFMR_P | PRV-1 TRIP Y PHASE | SPS | TFPR
81 | ABC | ICT | XFMR_P | PRV-2 TRIP Y PHASE | SPS | PRV2
82 | ABC | ICT | XFMR_P | OLTC OIL SURGE RELAY OPTD- Y PHASE | SPS | OLTR
83 | ABC | ICT | XFMR_P | OLTC PRV TRIP OPTD- Y PHASE | SPS | OLTP
84 | ABC | ICT | XFMR_P | OIL FLOW VALVE TRIP- Y PHASE | SPS
85 | ABC | ICT | XFMR_P | FANS FAIL TO START BANK A - Y PHASE | SPS | FANF
86 | ABC | ICT | XFMR_P | FANS FAIL TO START BANK B - Y PHASE | SPS | FANB
87 | ABC | ICT | XFMR_P | PUMPS FAIL TO START BANK A - Y PHASE | SPS | PMPF
88 | ABC | ICT | XFMR_P | PUMPS FAIL TO START BANK B - Y PHASE | SPS | PMPB
89 | ABC | ICT | XFMR_P | OIL FLOW LOW ALARM BANK Y PHASE | SPS | TFOL
90 | ABC | ICT | XFMR_P | COMMON THERMAL O/L ALARM Y PHASE | SPS | OLAL
91 | ABC | ICT | XFMR_P | COMMON THERMAL O/L TRIP Y PHASE | SPS | CTTP
92 | ABC | ICT | XFMR_P | STANDBY SUPLY FAIL Y PHASE | SPS | SBSF
93 | ABC | ICT | XFMR_P | MOISTURE ALARM Y PHASE | SPS | MOSA
94 | ABC | ICT | XFMR_P | DGA ALARM Y PHASE | SPS | DGAA
95 | ABC | ICT | XFMR_P | FIRE IN TRANSFORMER Y PHASE | SPS | FRTY
96 | ABC | ICT | XFMR_P | DELUGE VALVE OPTD - Y PHASE | SPS | DVTY
97 | ABC | ICT | XFMR_P | OLTC OIL LEVEL ALARM Y PHASE | SPS
98 | ABC | ICT | XFMR_P | DGA MONITORING DEVICE UNHEALTHY Y PHASE | SPS
99 | ABC | ICT | XFMR_P | SPARE ICT SELECTED FOR Y PHASE | SPS
100 | ABC | ICT | XFMR_P | REF OPTD B PHASE | SPS
101 | ABC | ICT | XFMR_P | REF PROTN B PHASE BLOCKED | SPS
102 | ABC | ICT | XFMR_P | BACKUP O/C OPTD (HV) B PHASE | SPS | BUOC
103 | ABC | ICT | XFMR_P | BUCHHOLZ ALARM B PHASE | SPS | BUCA
104 | ABC | ICT | XFMR_P | BUCHHOLZ TRIP B PHASE | SPS | BUCT
105 | ABC | ICT | XFMR_P | OTI ALARM B PHASE | SPS | OTIA
106 | ABC | ICT | XFMR_P | OTI TRIP B PHASE | SPS | OTIT
107 | ABC | ICT | XFMR_P | WTI ALARM (HV/IV/LV) B PHASE | SPS | WTIA
108 | ABC | ICT | XFMR_P | WTI TRIP (HV/IV/LV) B PHASE | SPS | WTIT
109 | ABC | ICT | XFMR_P | PRV-1 TRIP B PHASE | SPS | TFPR
110 | ABC | ICT | XFMR_P | PRV-2 TRIP B PHASE | SPS | PRV2
111 | ABC | ICT | XFMR_P | OLTC OIL SURGE RELAY OPTD- B PHASE | SPS | OLTR
112 | ABC | ICT | XFMR_P | OLTC PRV TRIP OPTD- B PHASE | SPS | OLTP
113 | ABC | ICT | XFMR_P | OIL FLOW VALVE TRIP- B PHASE | SPS
114 | ABC | ICT | XFMR_P | FANS FAIL TO START BANK A - B PHASE | SPS | FANF
115 | ABC | ICT | XFMR_P | FANS FAIL TO START BANK B - B PHASE | SPS | FANB
116 | ABC | ICT | XFMR_P | PUMPS FAIL TO START BANK A - B PHASE | SPS | PMPF
117 | ABC | ICT | XFMR_P | PUMPS FAIL TO START BANK B - B PHASE | SPS | PMPB
118 | ABC | ICT | XFMR_P | OIL FLOW LOW ALARM BANK B PHASE | SPS | TFOL
119 | ABC | ICT | XFMR_P | COMMON THERMAL O/L ALARM B PHASE | SPS | OLAL
120 | ABC | ICT | XFMR_P | COMMON THERMAL O/L TRIP B PHASE | SPS | CTTP
121 | ABC | ICT | XFMR_P | STANDBY SUPLY FAIL B PHASE | SPS | SBSF
122 | ABC | ICT | XFMR_P | MOISTURE ALARM B PHASE | SPS | MOSA
123 | ABC | ICT | XFMR_P | DGA ALARM B PHASE | SPS | DGAA
124 | ABC | ICT | XFMR_P | FIRE IN TRANSFOMER B PHASE | SPS | FRTB
125 | ABC | ICT | XFMR_P | DELUGE VALVE ON - B PHASE | SPS | DVTB
126 | ABC | ICT | XFMR_P | OLTC OIL LEVEL ALARM B PHASE | SPS
127 | ABC | ICT | XFMR_P | DGA MONITORING DEVICE UNHEALTHY B PHASE | SPS
128 | ABC | ICT | XFMR_P | SPARE ICT SELECTED FOR B PHASE | SPS
129 | ABC | ICT | XFMR_P | FANS FAIL TO START BANK A - B PHASE | SPS | FANF
130 | ABC | ICT | XFMR_P | FANS FAIL TO START BANK B - B PHASE | SPS | FANB
131 | ABC | ICT | XFMR_P | PUMPS FAIL TO START BANK A - B PHASE | SPS | PMPF
132 | ABC | ICT | XFMR_P | PUMPS FAIL TO START BANK B - B PHASE | SPS | PMPB
133 | ABC | ICT | XFMR_P | AVR OPERATION FAIL | SPS
134 | ABC | ICT | XFMR_P | OLTC DRIVE MOTOR FAULTY | SPS
135 | ABC | ICT | XFMR_P | OLTC ON LOWER LIMIT | SPS
136 | ABC | ICT | XFMR_P | OLTC ON UPPER LIMIT | SPS
137 | ABC | ICT | XFMR_P | NEUTRAL O/C PROTECTION OPTD | SPS
138 | ABC | ICT | XFMR_P | NEUTRAL O/C RELAY UNHEALTHY | SPS
139 | ABC | ICT | XFMR_P | DIRECT WDG TEMP MONITORING TRIP R PHASE | SPS
140 | ABC | ICT | XFMR_P | BACKUP IMPEDANCE TRIP Z1 | SPS | BUZ1
141 | ABC | ICT | XFMR_P | BACKUP IMPEDANCE TRIP Z2 | SPS | BUZ2
142 | ABC | ICT | XFMR_P | BACKUP IMPEDANCE TRIP Z3 | SPS | BUZ3
143 | ABC | ICT | XFMR_P | BACKUP IMPEDANCE TRIP Z4 | SPS | BUZ4
144 | ABC | ICT | XFMR_P | BU IMPEDANCE RELAY FAULTY | SPS
145 | ABC | ICT | XFMR_P | VT FUSE FAIL ALARM | SPS | VTFU
146 | ABC | ICT | XFMR_P | POWER SWING BLOCKING | SPS
140 | ABC | ICT | XFMR_P | CABLE BOX BCUZ ALARM OK | SPS
141 | ABC | ICT | XFMR_P | CABLEBOX BCUZTRIP RESET | SPS
142 | ABC | ICT | XFMR_P | H2 GAS ALARM-1 | SPS
143 | ABC | ICT | XFMR_P | H2 GAS ALARM-2 | SPS
144 | ABC | ICT | XFMR_P | ICT CABLBOX RPH PRD OPT | SPS
145 | ABC | ICT | XFMR_P | ICT CABLBOX YPH PRD OPT | SPS
146 | ABC | ICT | XFMR_P | ICT CABLBOX BPH PRD OPT | SPS
147 | ABC | ICT | CB | INTERLOCK ENABLED | SPS | INTL
148 | ABC | ICT | 89A | INTERLOCK ENABLED | SPS | INTL
149 | ABC | ICT | 89B | INTERLOCK ENABLED | SPS | INTL
150 | ABC | ICT | 89AE | INTERLOCK ENABLED | SPS | INTL
151 | ABC | ICT | 89BE | INTERLOCK ENABLED | SPS | INTL
152 | ABC | ICT | 89TR | INTERLOCK ENABLED | SPS | INTL
153 | ABC | ICT | 89TY | INTERLOCK ENABLED | SPS | INTL
154 | ABC | ICT | 89TB | INTERLOCK ENABLED | SPS | INTL
155 | ABC | ICT | 89TS1R | INTERLOCK ENABLED | SPS | INTL
156 | ABC | ICT | 89TS1Y | INTERLOCK ENABLED | SPS | INTL
157 | ABC | ICT | 89TS1B | INTERLOCK ENABLED | SPS | INTL
158 | ABC | ICT | 89TER | INTERLOCK ENABLED | SPS | INTL
159 | ABC | ICT | 89TEY | INTERLOCK ENABLED | SPS | INTL
160 | ABC | ICT | 89TEB | INTERLOCK ENABLED | SPS | INTL
161 | ABC | ICT | 89TS2EB | INTERLOCK ENABLED | SPS | INTL
162 | ABC | ICT |  | GAS LKG R/Y/B STG1 REFILL | SPS | SF61 | For GIS Bays
163 | ABC | ICT |  | GAS LKG R/Y/B STG2 LOW | SPS | SF62
164 | ABC | ICT |  | GAS LKG R/Y/B ZONE TRIP | SPS | SF6T
165 | ABC | ICT |  | GAS LKG R/Y/B CB LOCKOUT/CB OPERATION LOCKOUT | SPS | SF6T
SPARE ICT
1 | ABC | SPARE ICT | XFMR_P | REF OPTD SPARE | SPS
2 | ABC | SPARE ICT | XFMR_P | REF PROTN SPARE BLOCKED | SPS
3 | ABC | SPARE ICT | XFMR_P | BACKUP O/C OPTD (HV) SPARE | SPS | BUOC
4 | ABC | SPARE ICT | XFMR_P | BUCHHOLZ ALARM SPARE | SPS | BUCA
5 | ABC | SPARE ICT | XFMR_P | BUCHHOLZ TRIP SPARE | SPS | BUCT
6 | ABC | SPARE ICT | XFMR_P | OTI ALARM SPARE | SPS | OTIA
7 | ABC | SPARE ICT | XFMR_P | OTI TRIP SPARE | SPS | OTIT
8 | ABC | SPARE ICT | XFMR_P | WTI ALARM (HV/IV/LV) SPARE | SPS | WTIA
9 | ABC | SPARE ICT | XFMR_P | WTI TRIP (HV/IV/LV) SPARE | SPS | WTIT
10 | ABC | SPARE ICT | XFMR_P | PRV-1 TRIP SPARE | SPS | TFPR
11 | ABC | SPARE ICT | XFMR_P | PRV-2 TRIP SPARE | SPS | PRV2
12 | ABC | SPARE ICT | XFMR_P | OLTC OIL SURGE RELAY OPTD- SPARE | SPS | OLTR
13 | ABC | SPARE ICT | XFMR_P | OIL FLOW LOW ALARM BANK SPARE | SPS | TFOL
14 | ABC | SPARE ICT | XFMR_P | OLTC PRV TRIP OPTD- SPARE | SPS | OLTP
15 | ABC | SPARE ICT | XFMR_P | OIL FLOW VALVE TRIP- B PHASE | SPS
16 | ABC | SPARE ICT | XFMR_P | COMMON THERMAL O/L ALARM SPARE | SPS | OLAL
17 | ABC | SPARE ICT | XFMR_P | COMMON THERMAL O/L TRIP SPARE | SPS | CTTP
18 | ABC | SPARE ICT | XFMR_P | STANDBY SUPLY FAIL SPARE | SPS | SBSF
19 | ABC | SPARE ICT | XFMR_P | FANS FAIL TO START BANK A - SPARE | SPS | FANF
20 | ABC | SPARE ICT | XFMR_P | FANS FAIL TO START BANK B - SPARE | SPS | FANB
21 | ABC | SPARE ICT | XFMR_P | PUMPS FAIL TO START BANK A - SPARE | SPS | PMPF
22 | ABC | SPARE ICT | XFMR_P | PUMPS FAIL TO START BANK B - SPARE | SPS | PMPB
23 | ABC | SPARE ICT | XFMR_P | MOISTURE ALARM SPARE | SPS | MOSA
24 | ABC | SPARE ICT | XFMR_P | DGA ALARM SPARE | SPS | DGAA
25 | ABC | SPARE ICT | XFMR_P | FIRE IN TREASFORMER - SPARE | SPS | FRTS
26 | ABC | SPARE ICT | XFMR_P | DELUGE VALVE ON - SPARE | SPS | DVTS
27 | ABC | SPARE ICT | XFMR_P | OLTC OIL LEVEL ALARM SPARE | SPS
28 | ABC | SPARE ICT | XFMR_P | DGA MONITORING DEVICE UNHEALTHY SPARE | SPS
29 | ABC | SPARE ICT |  | GAS LKG R/Y/B STG1 REFILL | SPS | SF61 | For GIS Bays
30 | ABC | SPARE ICT |  | GAS LKG R/Y/B ZONE TRIP | SPS | SF6T
ICT (SECONDARY SIDE)
1 | ABC | ICT | BCU | BAY IN MAINTENANCE MODE | SPS | BAYM
2 | ABC | ICT | BCU | BCU DC SUPPLY FAIL-1/2 | SPS | BCUD
3 | ABC | ICT | BCU | BCU UNHEALTHY | SPS | BCUH
4 | ABC | ICT | BCU | BCU TIME SYNC ERROR | SPS | BCUC
5 | ABC | ICT | CB | CB MANUAL OPEN | SPS | MNOP
6 | ABC | ICT | CB | CB MANUAL CLOSE | SPS | MNCL
7 | ABC | ICT | CB | LBB PROTECTION OPERATED | SPS | LBBO
8 | ABC | ICT | CB | OPERATION LOCKOUT | SPS | OPLO
9 | ABC | ICT | CB | CB POLE DISCREPANCY OPERATED | SPS | PDIS
10 | ABC | ICT | CB | CB DC SUPPLY 1/2 FAIL | SPS | DC
11 | ABC | ICT | CB | CB AC SUPPLY FAIL | SPS | ACSP
12 | ABC | ICT | CB | CB SPRING/AIR/OIL LOW | SPS | SPRG
13 | ABC | ICT | CB | CB SF6 LOW ALARM | SPS | SF6L
14 | ABC | ICT | CB | CB TC1 Faulty | SPS | TC1F
15 | ABC | ICT | CB | CB TC2 Faulty | SPS | TC2F
16 | ABC | ICT | XFMR_S | LV - OVERFLUX ALARM | SPS | OFLA
17 | ABC | ICT | XFMR_S | LV - OVERFLUX OPTD | SPS | OFLP
18 | ABC | ICT | XFMR_S | LV - BACKUP O/C OPTD | SPS | BUOC
19 | ABC | ICT | XFMR_S | LV - BACKUP E/F OPTD | SPS | BUEF
20 | ABC | ICT | XFMR_S | SELECTED VT FUSE FAIL ALARM | SPS | VTFU
21 | ABC | ICT | XFMR_S | 86A TRIP RELAY OPERATED | SPS | 86AO
22 | ABC | ICT | XFMR_S | 86B TRIP RELAY OPERATED | SPS | 86BO
23 | ABC | ICT | XFMR_S | 86A TRIP REALY UNHEALTHY | SPS | 86AU
24 | ABC | ICT | XFMR_S | 86B TRIP REALY UNHEALTHY | SPS | 86BU
25 | ABC | ICT | XFMR_S | MAIN-1 BB PROTECTION OPTD | SPS | BB1P
26 | ABC | ICT | XFMR_S | MAIN-2 BB PROTECTION OPTD | SPS | BB2P
27 | ABC | ICT | XFMR_S | MAIN-1 BB PU UNIT FAULTY | SPS | B1UH
28 | ABC | ICT | XFMR_S | MAIN-2 BB PU UNIT FAULTY | SPS | B2UH
29 | ABC | ICT | XFMR_S | DC SOURCE-1 FAIL | SPS | DC-1
30 | ABC | ICT | XFMR_S | DC SOURCE-2 FAIL | SPS | DC-2
31 | ABC | ICT | CB | INTERLOCK ENABLED | SPS | INTL
32 | ABC | ICT | 89A | INTERLOCK ENABLED | SPS | INTL
33 | ABC | ICT | 89B | INTERLOCK ENABLED | SPS | INTL
34 | ABC | ICT | 89L | INTERLOCK ENABLED | SPS | INTL
35 | ABC | ICT | 89T | INTERLOCK ENABLED | SPS | INTL
36 | ABC | ICT | 89AE | INTERLOCK ENABLED | SPS | INTL
37 | ABC | ICT | 89LE1 | INTERLOCK ENABLED | SPS | INTL
38 | ABC | ICT | 89LE2 | INTERLOCK ENABLED | SPS | INTL
LINE SERIES REACTOR/ BUS SERIES REACTOR
1 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | CB | INTERLOCK ENABLED | SPS | INTL
2 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | 89A | INTERLOCK ENABLED | SPS | INTL
3 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | 89AE | INTERLOCK ENABLED | SPS | INTL
4 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | 89B | INTERLOCK ENABLED | SPS | INTL
5 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | 89BE | INTERLOCK ENABLED | SPS | INTL
6 | ABC | LSR / BSR | 89L/ 89BSR | INTERLOCK ENABLED | SPS | INTL
7 | ABC | LSR / BSR | 89LE/ 89BSRE | INTERLOCK ENABLED | SPS | INTL
8 | ABC | LSR | 89LSR | INTERLOCK ENABLED | SPS | INTL | In case of Line Series Reactor
9 | ABC | LSR | 89LSR1 | INTERLOCK ENABLED | SPS | INTL
10 | ABC | LSR | 89LSR2 | INTERLOCK ENABLED | SPS | INTL
11 | ABC | LSR | 89LSR2- ES | INTERLOCK ENABLED | SPS | INTL
12 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | BCU | BAY IN MAINTENANCE MODE | SPS | BAYM
13 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | BCU | BCU DC SUPPLY FAIL-1/2 | SPS | BCUD
14 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | BCU | BCU UNHEALTHY | SPS | BCUH
15 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | BCU | BCU TIME SYNC ERROR | SPS | BCUC
16 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | CB | CB MANUAL OPEN | SPS | MNOP | CB corresponding to main bay
17 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | CB | CB MANUAL CLOSE | SPS | MNCL
18 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | CB | LBB PROTECTION OPERATED | SPS | LBBO
19 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | CB | OPERATION LOCKOUT | SPS | OPLO
20 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | CB | CB POLE DISCREPANCY OPERATED | SPS | PDIS
21 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | CB | CB POLE DISCREPANCY WITH IN POLE OPERATED | SPS | PDIB
22 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | CB | CB DC SUPPLY 1/2 FAIL | SPS | DC
23 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | CB | CB AC SUPPLY FAIL | SPS | ACSP
24 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | CB | CB SPRING DISCHARGE | SPS | SPRG
25 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | CB | CB SF6 LOW ALARM | SPS | SF6L
26 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | CB | CB TC1 Faulty | SPS | TC1F
27 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | CB | CB TC2 Faulty | SPS | TC2F
28 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | 86A TRIP RELAY OPTD. | SPS
29 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | 86B TRIP RELAY OPTD. | SPS
30 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | 86A TRIP RELAY UNHEALTHY | SPS
31 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | 86B TRIP RELAY UNHEALTHY | SPS
32 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | DIFFERENTIAL PROTN OPTD. 87 R2 | SPS
33 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | BACK-UP IMPEDANCE PROTN OPTD | SPS
34 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | BACK-UP IMPEDANCE PROTN OPTD - R PHASE | SPS
35 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | BACK-UP IMPEDANCE PROTN OPTD - Y PHASE | SPS
36 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | BACK-UP IMPEDANCE PROTN OPTD - B PHASE | SPS
37 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | BACKUP E/F OPTD. (HV) | SPS
38 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | BACKUP O/C OPTD. (HV) | SPS
39 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | CVT FUSE FAIL (B/U IMP) | SPS
40 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | DIFF. PROTECTION OPTD 87R1 | SPS
41 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | DIFF. PROTECTION OPTD 87R1 - R PHASE | SPS
42 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | DIFF. PROTECTION OPTD 87R1 - Y PHASE | SPS
43 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | DIFF. PROTECTION OPTD 87R1 - B PHASE | SPS
44 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | DC SOURCE-1 FAIL | SPS
45 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | DC SOURCE-2 FAIL | SPS
46 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | DIFFERENTIAL RELAY UNHEALTHY 87R2 | SPS
47 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | BACKUP IMPEDANCE RELAY UNHEALTHY | SPS
48 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | DIFFERENTIAL RELAY UNHEALTHY 87R1 | SPS
49 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | BAY IN MAINTENANCE MODE | SPS
50 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | 87 R2 TIME SYNCHRONISATION ERROR | SPS
51 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | 21 R TIME SYNCHRONISATION ERROR | SPS
52 | ABC | LINE SERIES REACTOR/ BUS SERIES REACTOR | RE | 87 R1 TIME SYNCHRONISATION ERROR | SPS
FIXED SERIES CAPACITOR (FSC)
1 | ABC | FSC | 89ES2 | EARTH SWITCH 2 OPERATION INTERLOCK |  | SPS
2 | ABC | FSC |  | LINE DE-ENRGIZED |  | SPS
3 | ABC | FSC |  | FAULT TO PLATFORM TRIP-1/2 |  | SPS
4 | ABC | FSC |  | PERMANENT BYPASS |  | SPS
5 | ABC | FSC | 52BBR | BPCB STATUS DISCREPANCY |  | SPS
6 | ABC | FSC | 52BBR | BPCB AUX CONTACT DISCORDANCE |  | SPS
7 | ABC | FSC | 52BBR | GENRAL LOCKOUT/MIN OIL PRESSURE LOCKOUT |  | SPS
8 | ABC | FSC | 52BBR | BPCB POLE DISCREPANCY |  | SPS
9 | ABC | FSC | 52BBR | BPCB DC 1/2 FAIL |  | SPS
10 | ABC | FSC | 52BBR | BPCB LOSS OF SF6 |  | SPS
11 | ABC | FSC | 52BBR | 1POLE REINSERTION DURING AR |  | SPS
12 | ABC | FSC | 52BBR | BYPASS BREAKER FAIL TO OPEN |  | SPS
13 | ABC | FSC | 52BBR | BYPASS BREAKER SWITCHWED WITHOUT COMMAND |  | SPS
14 | ABC | FSC | 52BBR | BYPASS BREAKER FAIL TO CLOSE |  | SPS
15 | ABC | FSC | 52BBR | BYPASS CB SPRING DISCHARGE/FAILURE |  | SPS
16 | ABC | FSC | 52BBR | BPCB OPERATION INTERLOCK |  | SPS
17 | ABC | FSC | 89MBS | BYPASS MBS OPERATION INTERLOCK |  | SPS
18 | ABC | FSC | 89DS1 | BYPASS CAP ISO 1 OPERATION INTERLOCK |  | SPS
19 | ABC | FSC | 89DS1 | DISCONNECTOR 1 PHASE DISAGREEMENT |  | SPS
20 | ABC | FSC | 89DS1 | GENERAL ALARM |  | SPS
21 | ABC | FSC | 89MBS | BYPASS DISCONNECTOR ALARM |  | SPS
22 | ABC | FSC | 89DS2 | DISCONNECTOR 2 PHASE DISAGREEMENT |  | SPS
23 | ABC | FSC | 89DS2 | GENERAL ALARM |  | SPS
24 | ABC | FSC | CAP | CAPACITOR UNBALANCE ALARM |  | SPS
25 | ABC | FSC | CAP | CAPACITOR UNBALANCED TRIP |  | SPS
26 | ABC | FSC | CAP | CAPACITOR OVERLOAD ALARM |  | SPS
27 | ABC | FSC | CAP | CAPACITOR OVERLOAD TRIP |  | SPS
28 | ABC | FSC | MOV | MOV TRIP |  | SPS
29 | ABC | FSC | PROT | PROTECTION SYSTEM FAIL-1 |  | SPS
30 | ABC | FSC | PROT | PROTECTION SYSTEM FAIL-2 |  | SPS
31 | ABC | FSC | PROT | SIGNAL TRANSMISSION POWER FAIL |  | SPS
32 | ABC | FSC | PROT | MASTER TRIP |  | SPS
33 | ABC | FSC | PROT | GPS TIME SYNC FAIL |  | SPS
34 | ABC | FSC | PROT | DIRECT TRIP RECEIVE |  | SPS
35 | ABC | FSC | PROT | COMMUNICATION CHANNEL FAIL |  | SPS
36 | ABC | FSC | PROT | BYPASS CAP ISO 2 OPERATION INTERLOCK |  | SPS
37 | ABC | FSC | PROT | MOV FAIL |  | SPS
38 | ABC | FSC | PROT | CONTROL SYSTEM 1 HARDWARE ALARM |  | SPS
39 | ABC | FSC | PROT | PROTECTION SYSTEM 1 HARDWARE ALARM |  | SPS
40 | ABC | FSC | PROT | CONTROL & PROTECTION SYSTEM 1 COMMUNICATION FAULT |  | SPS
41 | ABC | FSC | PROT | PROTECTION SYSTEM 1 MEASURING SYSTEM WARNING |  | SPS
42 | ABC | FSC | PROT | CONTROL SYSTEM 2 HARDWARE ALARM |  | SPS
43 | ABC | FSC | PROT | PROTECTION SYSTEM 2 HARDWARE ALARM |  | SPS
44 | ABC | FSC | PROT | CONTROL & PROTECTION SYSTEM 2 COMMUNICATION FAULT |  | SPS
45 | ABC | FSC | PROT | PROTECTION SYSTEM 2 MEASURING SYSTEM WARNING |  | SPS
46 | ABC | FSC | PROT | CONTROL & PROTECTION SYSTEM POWER SUPPLY ALARM |  | SPS
47 | ABC | FSC | PROT | CONTROL & PROTECTION SYSTEM REDUNDANCY DISTURBED |  | SPS
48 | ABC | FSC | PROT | EARTH SWITCH 1 ALARM |  | SPS
49 | ABC | FSC | PROT | EARTH SWITCH 2 ALARM |  | SPS
50 | ABC | FSC | PROT | DISCONNECTOR SWITCH 1 ALARM |  | SPS
51 | ABC | FSC | PROT | DISCONNECTOR SWITCH 2 ALARM |  | SPS
52 | ABC | FSC | PROT | LINE EARTH SWITCH ALARM |  | SPS
53 | ABC | FSC | PROT | BYPASS BREAKER ALARM |  | SPS
54 | ABC | FSC | PROT | MAIN BYPASS SWITCH ALARM |  | SPS
55 | ABC | FSC | PROT | LINE SIDE 1: DE-ENERGIZED |  | SPS
56 | ABC | FSC | PROT | LINE SIDE 2: DE-ENERGIZED |  | SPS
57 | ABC | FSC | 52BBR | BYPASS BREAKER LOCAL/REMOTE CONTROL |  | SPS
58 | ABC | FSC | 52BBR | BYPASS BREAKER MAIN CLOSING COIL UNHEALTHY |  | SPS
59 | ABC | FSC | 52BBR | BYPASS BREAKER BACKUP CLOSING COIL UNHEALTHY |  | SPS
60 | ABC | FSC | PROT | FIRE FIGHTING SYSTEM: ALARM |  | SPS
61 | ABC | FSC | PROT-1 | SYSTEM 1: MOV OVERLOAD |  | SPS
62 | ABC | FSC | PROT-1 | SYSTEM 1: MOV TEMPERATURE TRIP |  | SPS
63 | ABC | FSC | PROT-1 | SYSTEM 1: MOV TEMPERATURE GRADIENT LOW SET |  | SPS
64 | ABC | FSC | PROT-1 | SYSTEM 1: MOV TEMPERATURE GRADIENT HIGH SET |  | SPS
65 | ABC | FSC | PROT-1 | SYSTEM 1: MOV UNBALANCE |  | SPS
66 | ABC | FSC | PROT-1 | SYSTEM 1: MOV HIGH CURRENT |  | SPS
67 | ABC | FSC | PROT-1 | SYSTEM 1: SPARK GAP FAILED TO TRIGGER |  | SPS
68 | ABC | FSC | PROT-1 | SYSTEM 1: SPARK GAP DELAYED TRIGGER |  | SPS
69 | ABC | FSC | PROT-1 | SYSTEM 1: SPARK GAP PROLONGED CONDUCTION |  | SPS
70 | ABC | FSC | PROT-1 | SYSTEM 1: SPARK GAP SELF TRIGGER |  | SPS
71 | ABC | FSC | PROT-1 | SYSTEM 1: SPARK GAP TRIGGER (R,Y,B) |  | SPS
72 | ABC | FSC | PROT-1 | SYSTEM 1: BYPASS BREAKER FAIL |  | SPS
73 | ABC | FSC | PROT-1 | SYSTEM 1: PREVENT REINSERTION ACTIVE |  | SPS
74 | ABC | FSC | PROT-1 | SYSTEM 1: PERMANENT BYPASS |  | SPS
75 | ABC | FSC | PROT-1 | SYSTEM 1: TEMPORARY BYPASS PHASE(R,Y,B) |  | SPS
76 | ABC | FSC | PROT-1 | SYSTEM 1: REINSERTION |  | SPS
77 | ABC | FSC | PROT-1 | SYSTEM 1: LINE TRIP |  | SPS
78 | ABC | FSC | PROT-2 | SYSTEM 2: MOV OVERLOAD |  | SPS
79 | ABC | FSC | PROT-2 | SYSTEM 2: MOV TEMPERATURE TRIP |  | SPS
80 | ABC | FSC | PROT-2 | SYSTEM 2: MOV TEMPERATURE GRADIENT LOW SET |  | SPS
81 | ABC | FSC | PROT-2 | SYSTEM 2: MOV TEMPERATURE GRADIENT HIGH SET |  | SPS
82 | ABC | FSC | PROT-2 | SYSTEM 2: MOV UNBALANCE |  | SPS
83 | ABC | FSC | PROT-2 | SYSTEM 2: MOV HIGH CURRENT |  | SPS
84 | ABC | FSC | PROT-2 | SYSTEM 2: SPARK GAP FAILED TO TRIGGER |  | SPS
85 | ABC | FSC | PROT-2 | SYSTEM 2: SPARK GAP DELAYED TRIGGER |  | SPS
86 | ABC | FSC | PROT-2 | SYSTEM 2: SPARK GAP PROLONGED CONDUCTION |  | SPS
87 | ABC | FSC | PROT-2 | SYSTEM 2: SPARK GAP SELF TRIGGER |  | SPS
88 | ABC | FSC | PROT-2 | SYSTEM 2: SPARK GAP TRIGGER (R,Y,B) |  | SPS
89 | ABC | FSC | PROT-2 | SYSTEM 2: BYPASS BREAKER FAIL |  | SPS
90 | ABC | FSC | PROT-2 | SYSTEM 2: PREVENT REINSERTION ACTIVE |  | SPS
91 | ABC | FSC | PROT-2 | SYSTEM 2: PERMANENT BYPASS |  | SPS
92 | ABC | FSC | PROT-2 | SYSTEM 2: TEMPORARY BYPASS PHASE(R,Y,B) |  | SPS
93 | ABC | FSC | PROT-2 | SYSTEM 2: REINSERTION |  | SPS
94 | ABC | FSC | PROT-2 | SYSTEM 2: LINE TRIP |  | SPS
765 KV / 400 KV/ 220 KV BUS BAR
1 |  | 765kV BUS-X | BUS | M1 BB Z1 operated | SPS | BB17
2 |  | 765kV BUS-X | BUS | M2 BB Z1 operated | SPS | BB18
3 |  | 765kV BUS-X | BUS | M1 BB Z1 out of service | SPS | BB9
4 |  | 765kV BUS-X | BUS | M2 BB Z1 out of service | SPS | BB30
5 |  | 765kV BUS-X | BUS | M1 BB Z1 CT Trouble | SPS | M1TB
6 |  | 765kV BUS-X | BUS | M2 BB Z1 CT Trouble | SPS | M2TB
7 |  | 765kV BUS-X | BUS | Main-1 BB relay Healthy | SPS | BBH
8 |  | 765kV BUS-X | BUS | Main- 2 BB relay Healthy | SPS | BBH
9 |  | 765kV BUS-X | BUS | MAIN-1 BB ZONE-1 CT SUPVN. ALARM | SPS
10 |  | 765kV BUS-X | BUS | MAIN-2 BB ZONE-1 CT SUPVN. ALARM | SPS
11 |  | 765kV BUS-X | BUS | BUSBAR-1 IN/OUT SWITCH IN OUT POSITION | SPS
12 |  | 765kV BUS-X | BUS | BUSBAR-2 IN/OUT SWITCH IN OUT POSITION | SPS
13 |  | 765kV BUS-X | BUS | MAIN-1 CZ CT SUPV ALARM | SPS
14 |  | 765kV BUS-X | BUS | MAIN-2 CZ CT SUPV ALARM | SPS
BUS COUPLER
1 | ABC | BUS COUPLER | BCU | BAY IN MAINTENANCE MODE | SPS | BAYM
2 | ABC | BUS COUPLER | BCU | BCU DC SUPPLY FAIL-1/2 | SPS | BCUD
3 | ABC | BUS COUPLER | BCU | BCU UNHEALTHY | SPS | BCUH
4 | ABC | BUS COUPLER | BCU | BCU TIME SYNC ERROR | SPS | BCUC
5 | ABC | BUS COUPLER | CB | CB MANUAL OPEN | SPS | MNOP
6 | ABC | BUS COUPLER | CB | CB MANUAL CLOSE | SPS | MNCL
7 | ABC | BUS COUPLER | CB | LBB PROTECTION OPERATED | SPS | LBBO
8 | ABC | BUS COUPLER | CB | OPERATION LOCKOUT | SPS | OPLO
9 | ABC | BUS COUPLER | CB | CB POLE DISCREPANCY OPERATED | SPS | PDIS
10 | ABC | BUS COUPLER | CB | CB DC SUPPLY 1/2 FAIL | SPS | DC
11 | ABC | BUS COUPLER | CB | CB AC SUPPLY FAIL | SPS | ACSP
12 | ABC | BUS COUPLER | CB | CB SPRING/AIR/OIL LOW | SPS | SPRG
13 | ABC | BUS COUPLER | CB | CB SF6 LOW ALARM | SPS | SF6L
14 | ABC | BUS COUPLER | CB | CB TC1 Faulty | SPS | TC1F
15 | ABC | BUS COUPLER | CB | CB TC2 Faulty | SPS | TC2F
16 | ABC | BUS COUPLER | CB | INTERLOCK ENABLED | SPS | INTL
17 | ABC | BUS COUPLER | 89A | INTERLOCK ENABLED | SPS | INTL
18 | ABC | BUS COUPLER | 89B | INTERLOCK ENABLED | SPS | INTL
19 | ABC | BUS COUPLER | 89AE1 | INTERLOCK ENABLED | SPS | INTL
20 | ABC | BUS COUPLER | 89AE2 | INTERLOCK ENABLED | SPS | INTL
21 | ABC | BUS COUPLER | 89BE1 | INTERLOCK ENABLED | SPS | INTL
22 | ABC | BUS COUPLER | 89BE2 | INTERLOCK ENABLED | SPS | INTL
TRANSFER BUS COUPLER
1 | ABC | TRANSFER BUS COUPLER | BCU | BAY IN MAINTENANCE MODE | SPS | BAYM
2 | ABC | TRANSFER BUS COUPLER | BCU | BCU DC SUPPLY FAIL-1/2 | SPS | BCUD
3 | ABC | TRANSFER BUS COUPLER | BCU | BCU UNHEALTHY | SPS | BCUH
4 | ABC | TRANSFER BUS COUPLER | BCU | BCU TIME SYNC ERROR | SPS | BCUC
5 | ABC | TRANSFER BUS COUPLER | CB | CB MANUAL OPEN | SPS | MNOP
6 | ABC | TRANSFER BUS COUPLER | CB | CB MANUAL CLOSE | SPS | MNCL
7 | ABC | TRANSFER BUS COUPLER | CB | LBB PROTECTION OPERATED | SPS | LBBO
8 | ABC | TRANSFER BUS COUPLER | CB | OPERATION LOCKOUT | SPS | OPLO
9 | ABC | TRANSFER BUS COUPLER | CB | CB POLE DISCREPANCY OPERATED | SPS | PDIS
10 | ABC | TRANSFER BUS COUPLER | CB | CB DC SUPPLY 1/2 FAIL | SPS | DC
11 | ABC | TRANSFER BUS COUPLER | CB | CB AC SUPPLY FAIL | SPS | ACSP
12 | ABC | TRANSFER BUS COUPLER | CB | CB SPRING/AIR/OIL LOW | SPS | SPRG
13 | ABC | TRANSFER BUS COUPLER | CB | CB SF6 LOW ALARM | SPS | SF6L
14 | ABC | TRANSFER BUS COUPLER | CB | CB TC1 Faulty | SPS | TC1F
15 | ABC | TRANSFER BUS COUPLER | CB | CB TC2 Faulty | SPS | TC2F
16 | ABC | TRANSFER BUS COUPLER | CB | AUTORECLOSE LOCKOUT | SPS | ARLO
17 | ABC | TRANSFER BUS COUPLER | CB | AUTORECLOSE OPERATED | SPS | AROP
18 | ABC | TRANSFER BUS COUPLER | LINE | AUTORECLOSE UNSUCCESFUL | SPS | ARFM
19 | ABC | TRANSFER BUS COUPLER | LINE | 86A TRIP RELAY OPERATED | SPS | 86AO
20 | ABC | TRANSFER BUS COUPLER | LINE | 86B TRIP RELAY OPERATED | SPS | 86BO
21 | ABC | TRANSFER BUS COUPLER | LINE | 86A TRIP RELAY FAULTY | SPS | 86AU
22 | ABC | TRANSFER BUS COUPLER | LINE | 86B TRIP RELAY FAULTY | SPS | 86BU
23 | ABC | TRANSFER BUS COUPLER | CB | INTERLOCK ENABLED | SPS | INTL
24 | ABC | TRANSFER BUS COUPLER | 89A | INTERLOCK ENABLED | SPS | INTL
25 | ABC | TRANSFER BUS COUPLER | 89B | INTERLOCK ENABLED | SPS | INTL
26 | ABC | TRANSFER BUS COUPLER | 89T | INTERLOCK ENABLED | SPS | INTL
27 | ABC | TRANSFER BUS COUPLER | 89AE | INTERLOCK ENABLED | SPS | INTL
28 | ABC | TRANSFER BUS COUPLER | 89TE1 | INTERLOCK ENABLED | SPS | INTL
29 | ABC | TRANSFER BUS COUPLER | 89TE2 | INTERLOCK ENABLED | SPS | INTL
AUXILLIARY SYSTEM
1 | 220VDC | DCDB | 220V_DCDB-1 | 220V DCDB -1 EARTH FAULT | SPS
2 | 220VDC | DCDB | 220V_DCDB-2 | 220V DCDB -2 EARTH FAULT | SPS
3 | 220VDC | BCHRG | BATCHRG220V-1 | 220V BATTERY CHARGER-1 TROUBLE | SPS
4 | 220VDC | BCHRG | BATCHRG220V-2 | 220V BATTERY CHARGER-2 TROUBLE | SPS
5 | 48 VDC | BCHRG | BATCHRG48V-1 | 48V BATTERY CHARGER-1 TROUBLE | SPS
6 | 48 VDC | BCHRG | BATCHRG48V-2 | 48V BATTERY CHARGER-2 TROUBLE | SPS
7 | 415 V | FP | EPUMP | ELECTRIC MOTOR FIRE WATER PUMP RUNNING | SPS
8 | 415 V | FP | EPUMP | ELECTRIC MOTOR FIRE WATER PUMP FAILS TO START | SPS
9 | 415 V | FP | EPUMP | ELECTRIC PUMP IN AUTO MODE | SPS
10 | 415 V | FP | EPUMP | CONTROL SUPPLY FAIL | SPS
11 | 415 V | FP | DPUMP | DIESEL ENGINE FIRE WATER PUMP FAILS TO START | SPS
12 | 415 V | FP | DPUMP | DIESEL ENGINE FIRE WATER PUMP RUNNING | SPS
13 | 415 V | FP | DPUMP | DIESEL ENGINE PUMP IN AUTO MODE | SPS
14 | 415 V | FP | DPUMP | DIESEL ENGINE BATTERY CHARGER-1 ON | SPS
15 | 415 V | FP | DPUMP | DIESEL ENGINE BATTERY CHARGER-2 ON | SPS
16 | 415 V | FP | DPUMP | DIESEL ENGINE FUEL LEVEL LOW | SPS
17 | 415 V | FP | DPUMP | CONTROL SUPPLY FAIL | SPS
18 | 415 V | FP | DPUMP | DIESEL PUMP OVER SPEED TRIP | SPS
19 | 415 V | FP | DPUMP | DIESEL PUMP LOW OIL PRESSURE TRIP | SPS
20 | 415 V | FP | DPUMP | DIESEL ENGINE HIGH TEMPERATURE ALARM | SPS
21 | 415 V | FP | SMOKE ALARM | CONTROL ROOM ZONE-1 FIRE DETECTED | SPS
22 | 415 V | FP | SMOKE ALARM | CONTROL ROOM ZONE-2 FIRE DETECTED | SPS
23 | 415 V | FP | SMOKE ALARM | CONTROL ROOM ZONE-3 FIRE DETECTED | SPS
24 | 415 V | FP | SMOKE ALARM | CONTROL ROOM ZONE-4 FIRE DETECTED | SPS
25 | 415 V | FP | SMOKE ALARM | 765KV KIOSK-1 FIRE DETECTED | SPS
26 | 415 V | FP | SMOKE ALARM | 400kV KIOSK-1 FIRE DETECTED | SPS
27 | 415 V | FP | FIREPROTN | WATER STORAGE TANK-1 WATER LEVEL LOW | SPS
28 | 415 V | FP | FIREPROTN | WATER STORAGE TANK-2 WATER LEVEL LOW | SPS
29 | 415 V | FP | FIREPROTN | FIRE FIGHTING TANK HEADER PRESSURE LEVEL LOW | SPS
30 | 415 V | FP | FIREPROTN | FIRE ANNAUNCIATION PANEL FAULTY | SPS
31 | 415 V | FP | FIREPROTN | COMMON FIRE ALARM | SPS
32 | 415 V | FP | FIREPROTN | CONTROL SUPPLY FAIL | SPS
33 | 415 V | FP | JPUMP-1 | JOCKEY PUMP-1 RUNNING | SPS
34 | 415 V | FP | JPUMP-1 | JOCKEY PUMP-1 FAILS TO START | SPS
35 | 415 V | FP | JPUMP-1 | JOCKEY PUMP-1 IN AUTO MODE | SPS
36 | 415 V | FP | JPUMP-1 | SUPERVISION OF CONTROL SUPPLY | SPS
37 | 415 V | FP | JPUMP-1 | JOCKEY PUMP-1 TRIP | SPS
38 | 415 V | FP | JPUMP-2 | JOCKEY PUMP-2 RUNNING | SPS
39 | 415 V | FP | JPUMP-2 | JOCKEY PUMP-2 FAILS TO START | SPS
40 | 415 V | FP | JPUMP-2 | JOCKEY PUMP-2 IN AUTO MODE | SPS
41 | 415 V | FP | JPUMP-2 | SUPERVISION OF CONTROL SUPPLY | SPS
42 | 415 V | FP | JPUMP-2 | JOCKEY PUMP-2 TRIP | SPS
43 | 415 V | FP | G_703_ICT-1 | FIRE IN ICT-1 | SPS
44 | 415 V | FP | G_703_ICT-1 | DELUGE SYSTEM OPERATING FOR ICT-1 | SPS
45 | 415 V | FP | G_701_BR-1 | FIRE IN BUS REACTOR | SPS
46 | 415 V | FP | G_701_BR-1 | DELUGE SYSTEM OPERATING FOR BUS REACTOR | SPS
47 | 415 V | FP | G_703_ICT-1 | FF NIS Out of service | SPS
48 | 415 V | FP | G_703_ICT-1 | FF NIS System ON | SPS
49 | 415 V | FP | G_703_ICT-1 | FF NISPNRV Closed | SPS
50 | 415 V | FP | G_703_ICT-1 | FF NIS Fire Detector Trip | SPS
51 | 415 V | FP | G_703_ICT-1 | FF NIS Buchholz Relay Trip | SPS
52 | 415 V | FP | G_703_ICT-1 | FF NIS Oil Drain Valve open | SPS
53 | 415 V | FP | G_703_ICT-1 | FF NIS Extinction in Progress | SPS
54 | 415 V | FP | G_703_ICT-1 | FF NIS Oil Drain Valve closed | SPS
55 | 415 V | FP | G_703_ICT-1 | FF NIS Gas inlet valve closed | SPS
56 | 415 V | FP | G_703_ICT-1 | FF NIS Cylinder pressure low | SPS
57 | 415 V | FP | G_703_ICT-1 | FF NIS Diff. Relay trip | SPS
58 | 415 V | FP | G_703_ICT-1 | FF NIS PRV Trip | SPS
59 | 415 V | FP | G_703_ICT-1 | FF NIS Transformer Trip | SPS
60 | 415 V | FP | G_703_ICT-1 | FF NIS Line Fault Fire Detector | SPS
61 | 415 V | FP | G_703_ICT-1 | FF NIS Line Fault Diff. Relay | SPS
62 | 415 V | FP | G_703_ICT-1 | FF NIS Line Fault Buchholz Relay | SPS
63 | 415 V | FP | G_703_ICT-1 | FF NIS Line fault PRV | SPS
64 | 415 V | FP | G_703_ICT-1 | FF NIS Line fault Transformer Trip | SPS
65 | 415 V | FP | G_703_ICT-1 | FF NIS Line Fault PNRV | SPS
66 | 415 V | FP | G_703_ICT-1 | FF NIS Hooter for DC supply fail | SPS
67 | 415 V | FP | G_703_ICT-1 | FF NIS Contactor for DC Supply Fail | SPS
69 | 415 V | FP | G_703_ICT-1 | Hydrant System in Service | SPS
70 | 415 V | FP | G_703_ICT-1 | Hydrant System Faulty | SPS
71 | 415 V | FP | G_703_ICT-1 | Hydrant Syestem On | SPS
72 | 415 V | COMMON | PLCC | PLCC EXCHANGE FAIL | SPS
73 | 415 V | COMMON | GPS | TIME SYNCH. SIGNAL ABSENT | SPS
74 | 415 V | AIRCON | G_KIOSK_1 | 765KV KIOSK-1 HIGH TEMP ALARM | SPS
75 | 415 V | AIRCON | F_KIOSK_1 | 400KV KIOSK-1 HIGH TEMP ALARM | SPS
76 | 415 V | SYSTEM | AUX_SYSTEM | SUBSTATION MAIN CONTROL ON NTAMC | SPS
77 | 415 V | SYSTEM | AUX_SYSTEM | SUBSTATION MAIN CONTROL ON RTAMC | SPS
78 | 415 V | SYSTEM | AUX_SYSTEM | SUBSTATION MAIN CONTROL ON BACK UP NTAMC | SPS
79 | 415 V | SYSTEM | AUX_SYSTEM | SUBSTATION AUX CONTROL ON NTAMC | SPS
80 | 415 V | SYSTEM | AUX_SYSTEM | SUBSTATION AUXCONTROL ON RTAMC | SPS
81 | 415 V | SYSTEM | AUX_SYSTEM | SUBSTATION AUX CONTROL ON BACK UP NTAMC | SPS
82 | 415 V | DG Set | DGSET-1 | ALTERNATOR ON | SPS
83 | 415 V | DG Set | DGSET-1 | CHARGER 1 ON | SPS
84 | 415 V | DG Set | DGSET-1 | CHARGER 2 ON | SPS
85 | 415 V | DG Set | DGSET-1 | ENGINE OVERHEATING | SPS
86 | 415 V | DG Set | DGSET-1 | HIGH COOLING WATER TEMP. | SPS
87 | 415 V | DG Set | DGSET-1 | LOW OIL PRESSURE TRIP | SPS
88 | 415 V | DG Set | DGSET-1 | DG SET FAILED TO START IN 30 SEC | SPS
89 | 415 V | DG Set | DGSET-1 | LACK OF FUEL | SPS
90 | 415 V | DG Set | DGSET-1 | LOW LEVEL IN DAILY SERVICE FUEL TANK | SPS
91 | 415 V | DG Set | DGSET-1 | HIGH SPEED DIESEL TANK LEVEL LOW | SPS
92 | 415 V | DG Set | DGSET-1 | OVERSPEED TRIP | SPS
93 | 415 V | DG Set | DGSET-1 | DG I/C PROTN OPTD(ALT FAULT,DIFF ETC) | SPS
94 | 415 V | DG Set | DGSET-1 | CONTROL SUPPLY FAIL | SPS
95 | 415 V | DG Set | DGSET-1 | DG PROTECTION OPERATED (O/C, E/F, DIFF.) | SPS
96 | 415 V | DG Set | DGSET-1 | DG PROTECTION U/V OPERATED | SPS
97 | 415 V | DG Set | DGSET-1 | AMF PANEL REMOTE SWITCH INDICATION | SPS
98 | 415 V | DG Set | DGSET-1 | DG OVERLOAD | SPS
99 | 415 V | DG Set | DGSET-1 | PHASE SEQUENCE NEGATIVE ALARM | SPS
100 | 415 V | LTSUP | ACDB-1 | ACDB INCOMER-1 O/C PROTN. RLY OPTD | SPS
101 | 415 V | LTSUP | ACDB-1 | ACDB INCOMER-1 E/F PROTN. RLY OPTD | SPS
102 | 415 V | LTSUP | ACDB-1 | ACDB INCOMER-1 U/V PROTN. RLY OPTD | SPS
103 | 415 V | LTSUP | ACDB-BC | SUPERVISION OF CONTROL SUPPLY | SPS
104 | 415 V | LTSUP | ACDB-2 | ACDB INCOMER-2 O/C PROTN. RLY OPTD | SPS
105 | 415 V | LTSUP | ACDB-2 | ACDB INCOMER-2 E/F PROTN. RLY OPTD | SPS
106 | 415 V | LTSUP | ACDB-2 | ACDB INCOMER-2 U/V PROTN. RLY OPTD | SPS
107 | 415 V | LTSUP | MSB-1 | AUX. TRAFO-1 BUCHHOLZ ALARM | SPS
108 | 415 V | LTSUP | MSB-1 | AUX. TRAFO-1 WTI ALARM | SPS
109 | 415 V | LTSUP | MSB-1 | AUX. TRAFO-1 OTI ALARM | SPS
110 | 415 V | LTSUP | MSB-1 | AUX. TRAFO-1 BUCHHOLZ TRIP | SPS
111 | 415 V | LTSUP | MSB-1 | AUX. TRAFO-1 WTI TRIP | SPS
112 | 415 V | LTSUP | MSB-1 | AUX. TRAFO-1 OTI TRIP | SPS
113 | 415 V | LTSUP | MSB-1 | I/C-1 O/C PROTECTION RELAY TRIP | SPS
114 | 415 V | LTSUP | MSB-1 | I/C-1 E/F PROTECTION RELAY TRIP | SPS
115 | 415 V | LTSUP | MSB-1 | MSB BUS-1 U/V OPTD | SPS
116 | 415 V | LTSUP | MSB-1 | PHASE SEQUENCE NEGATIVE ALARM | SPS
117 | 415 V | LTSUP | MSB_BC | SUPERVISION OF CONTROL SUPPLY | SPS
118 | 415 V | LTSUP | MSB-2 | AUX. TRAFO-2 BUCHHOLZ ALARM | SPS
119 | 415 V | LTSUP | MSB-2 | AUX. TRAFO- 2 WTI ALARM | SPS
120 | 415 V | LTSUP | MSB-2 | AUX. TRAFO-2 OTI ALARM | SPS
121 | 415 V | LTSUP | MSB-2 | AUX. TRAFO-2 BUCHHOLZ TRIP | SPS
122 | 415 V | LTSUP | MSB-2 | AUX. TRAFO-2 WTI TRIP | SPS
123 | 415 V | LTSUP | MSB-2 | AUX. TRAFO-2 OTI TRIP | SPS
124 | 415 V | LTSUP | MSB-2 | I/C-2 O/C PROTECTION RELAY TRIP | SPS
125 | 415 V | LTSUP | MSB-2 | I/C-2 E/F PROTECTION RELAY TRIP | SPS
126 | 415 V | LTSUP | MSB-2 | MSB BUS-2 U/V OPTD | SPS
127 | 415 V | LTSUP | MSB-2 | PHASE SEQUENCE NEGATIVE ALARM | SPS
128 | 33 KV | LTSUP | TERTIARY | CB INTERLOCK ENABLED | SPS
129 | 33 KV | LTSUP | TERTIARY | ISO INTERLOCK ENABLED | SPS
130 | 33 KV | LTSUP | TERTIARY | CB TRIPPED ON PROTN | SPS
131 |  | SAS | GATEWAY | GATEWAY-1 FAIL | SPS
132 |  | SAS | GATEWAY | GATEWAY-2 FAIL | SPS
133 |  | SAS | LOCAL_HMI | LOCAL HMI-1 FAIL | SPS
134 |  | SAS | LOCAL_HMI | LOCAL HMI-2 FAIL | SPS
135 |  |  | AUXBCU | AUX BCU UNHEALTHY | SPS
136 |  |  | AUXBCU | AUX BCU TIME SYNC ERROR | SPS
STATCOM (SIEMENS)
1 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-52 | INTERLOCK ENABLED | SPS
2 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-89A | INTERLOCK ENABLED | SPS
3 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-89B | INTERLOCK ENABLED | SPS
4 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-89AE | INTERLOCK ENABLED | SPS
5 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-89BE | INTERLOCK ENABLED | SPS
6 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX | HV Main Bay Transformer Connected | SPS
7 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX | HV Main Bay PSD Error | SPS
8 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX | HV Main Bay CT SF6 Loss Alarm | SPS
9 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX | HV Main Bay CT SF6 Lockout Alarm | SPS
10 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-52 | HV Main Bay CB SF6 Loss Alarm | SPS
11 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-52 | HV Main Bay CB SF6 Lockout Alarm | SPS
12 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-52 | HV Main Bay CB DC-1/2 Fail | SPS
13 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-52 | HV Main Bay CB Pole Descripency Operated | SPS
14 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-52 | HV Main Bay CB TC-1 Faulty | SPS
15 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX-52 | HV Main Bay CB TC-2 Faulty | SPS
16 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX | HV Main Bay 86.1 Relay Operated | SPS
17 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX | HV Main Bay 86.2 Relay Operated | SPS
18 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX | HV Main Bay CB Spring Discharge | SPS
19 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX | HV Main Bay LBB Operated | SPS
20 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX | HV Main Bay LBB Unhealthy | SPS
21 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX | HV Main Bay PSD Unhealthy | SPS
22 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY 4XX | HV Main Bay BCU Unhealthy | SPS
23 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY PROTN | LOCKOUT RELAYS ACTIVATED HV MAIN BAY | SPS
24 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q2 R PH | INTERLOCK ENABLED | SPS
25 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q2 Y PH | INTERLOCK ENABLED | SPS
26 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q2 B PH | INTERLOCK ENABLED | SPS
27 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q3-R-PH | INTERLOCK ENABLED | SPS
28 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q3 Y PH | INTERLOCK ENABLED | SPS
29 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q3 B PH | INTERLOCK ENABLED | SPS
30 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q51 R PH | INTERLOCK ENABLED | SPS
31 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q51 Y PH | INTERLOCK ENABLED | SPS
32 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q51 B PH | INTERLOCK ENABLED | SPS
33 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) 4XX-Q52 | INTERLOCK ENABLED | SPS
34 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | BUCHHOLZ RELAY 1 ALARM | SPS
35 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | BUCHHOLZ RELAY 2 ALARM | SPS
36 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | BUCHHOLZ RELAY 1 ALARM | SPS
37 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | BUCHHOLZ RELAY 2 ALARM | SPS
38 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | BUCHHOLZ RELAY 1 ALARM | SPS
39 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | BUCHHOLZ RELAY 2 ALARM | SPS
40 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | BUCHHOLZ RELAY 1 ALARM | SPS
41 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | BUCHHOLZ RELAY 2 ALARM | SPS
42 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | FAN FAILURE | SPS
43 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | FAN FAILURE | SPS
44 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | FAN FAILURE | SPS
45 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | FAN FAILURE | SPS
46 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01 | PROTECTION RELAY - 1 TRIP | SPS
47 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01 | PROTECTION RELAY - 2 TRIP | SPS
48 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01 | PROTECTION RELAY - 1 FAILURE | SPS
49 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01 | PROTECTION RELAY - 2 FAILURE | SPS
50 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY | HV Tie Bay Transformer Connected | SPS
51 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY | HV Tie Bay PSD Error | SPS
52 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-CT | HV Tie Bay CT SF6 Loss Alarm | SPS
53 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-CT | HV Tie Bay CT SF6 Lockout Alarm | SPS
54 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-52 | HV Tie Bay CB SF6 Loss Alarm | SPS
55 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-52 | HV Tie Bay CB SF6 Lockout Alarm | SPS
56 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-52 | HV Tie Bay CB DC-1/2 Fail | SPS
57 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-52 | HV Tie Bay CB Pole Descripency Operated | SPS
58 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-52 | HV Tie Bay CB TC-1 Faulty | SPS
59 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-52 | HV Tie Bay CB TC-2 Faulty | SPS
60 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-52 | HV Tie Bay CB Spring Discharge | SPS
61 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY | HV Tie Bay 86.1 Relay Operated | SPS
62 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY | HV Tie Bay 86.2 Relay Operated | SPS
63 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY | HV Tie Bay LBB Operated | SPS
64 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY | HV Tie Bay LBB Unhealthy | SPS
65 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY | HV Tie Bay PSD Unhealthy | SPS
66 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY | HV Tie Bay BCU Unhealthy | SPS
67 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY PROTN | LOCKOUT RELAYS ACTIVATED HV TIE BAY | SPS
68 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-52 | INTERLOCK ENABLED | SPS
69 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-89A | INTERLOCK ENABLED | SPS
70 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-89B | INTERLOCK ENABLED | SPS
71 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-89AE | INTERLOCK ENABLED | SPS
72 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY-89BE | INTERLOCK ENABLED | SPS
73 | 4ZZ | FUTURE | 89A | INTERLOCK ENABLED | SPS
74 | 4ZZ | FUTURE | 89AE | INTERLOCK ENABLED | SPS
75 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q1 R PH | INTERLOCK ENABLED | SPS
76 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q1 Y PH | INTERLOCK ENABLED | SPS
77 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q1 B PH | INTERLOCK ENABLED | SPS
78 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q2 R PH | INTERLOCK ENABLED | SPS
79 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q2 Y PH | INTERLOCK ENABLED | SPS
80 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q2 B PH | INTERLOCK ENABLED | SPS
81 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q12 R PH | INTERLOCK ENABLED | SPS
82 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q12 Y PH | INTERLOCK ENABLED | SPS
83 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q12 B PH | INTERLOCK ENABLED | SPS
84 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q13 R PH | INTERLOCK ENABLED | SPS
85 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q13 Y PH | INTERLOCK ENABLED | SPS
86 | J0 | STATCOM MV SIDE BAY | COUPLING TRANSFORMER (MV) J0-Q13 B PH | INTERLOCK ENABLED | SPS
87 | STATCOM | STATCOM | MV BUS BAR | PROTECTION RELAY - 1 TRIP | SPS
88 | STATCOM | STATCOM | MV BUS BAR | PROTECTION RELAY - 2 TRIP | SPS
89 | STATCOM | STATCOM | MV BUS BAR | PROTECTION RELAY - 1 FAILURE | SPS
90 | STATCOM | STATCOM | MV BUS BAR | PROTECTION RELAY - 2 FAILURE | SPS
91 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER MV-H01 | PROTECTION RELAY - 1 TRIP | SPS
92 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER MV-H01 | PROTECTION RELAY - 2 TRIP | SPS
93 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER MV-H01 | PROTECTION RELAY - 1 FAILURE | SPS
94 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER MV-H01 | PROTECTION RELAY - 2 FAILURE | SPS
95 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER J01-Q0 | INTERLOCK ENABLED | SPS
96 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER J01-Q1 | INTERLOCK ENABLED | SPS
97 | J01 | STATCOM AUX. TRANF. BAY | AUX TRANSFORMER J01-Q52 | INTERLOCK ENABLED | SPS
98 | J02 | STATCOM NGT BAY | GND TRANSFORMER MV-H02 | PROTECTION RELAY - 1 TRIP | SPS
99 | J02 | STATCOM NGT BAY | GND TRANSFORMER MV-H02 | PROTECTION RELAY - 2 TRIP | SPS
100 | J02 | STATCOM NGT BAY | GND TRANSFORMER MV-H02 | PROTECTION RELAY - 1 FAILURE | SPS
101 | J02 | STATCOM NGT BAY | GND TRANSFORMER MV-H02 | PROTECTION RELAY - 2 FAILURE | SPS
102 | J11 | STATCOM VSC-1 BAY | VSC-1 MV-J11 | PROTECTION RELAY - 1 TRIP | SPS
103 | J11 | STATCOM VSC-1 BAY | VSC-1 MV-J11 | PROTECTION RELAY - 2 TRIP | SPS
104 | J11 | STATCOM VSC-1 BAY | VSC-1 MV-J11 | PROTECTION RELAY - 3 TRIP | SPS
105 | J11 | STATCOM VSC-1 BAY | VSC-1 MV-J11 | PROTECTION RELAY - 1 FAILURE | SPS
106 | J11 | STATCOM VSC-1 BAY | VSC-1 MV-J11 | PROTECTION RELAY - 2 FAILURE | SPS
107 | J11 | STATCOM VSC-1 BAY | VSC-1 MV-J11 | PROTECTION RELAY - 3 FAILURE | SPS
108 | J11 | STATCOM VSC-1 BAY | VSC-1 MV-J11 | LOCKOUT RELAYS ACTIVATED | SPS
109 | J11 | STATCOM VSC-1 BAY | VSC-1 MV-J11 | STATCOM READY FOR OPERATION | SPS
110 | J11 | STATCOM VSC-1 BAY | VSC-1 MV-J11 | SEQUENCE FAILURE | SPS
111 | J11 | STATCOM VSC-1 BAY | VSC-1 MV-J11 | SEQUENCE RUNNING | SPS
112 | J11 | STATCOM VSC-1 BAY | VSC-1 J11 Q0 | INTERLOCK ENABLED | SPS
113 | J11 | STATCOM VSC-1 BAY | VSC-1 J11 Q1 | INTERLOCK ENABLED | SPS
114 | J11 | STATCOM VSC-1 BAY | VSC-1 J11 Q5 | INTERLOCK ENABLED | SPS
115 | J12 | STATCOM VSC-2 BAY | VSC-2 MV-J12 | PROTECTION RELAY - 1 TRIP | SPS
116 | J12 | STATCOM VSC-2 BAY | VSC-2 MV-J12 | PROTECTION RELAY - 2 TRIP | SPS
117 | J12 | STATCOM VSC-2 BAY | VSC-2 MV-J12 | PROTECTION RELAY - 3 TRIP | SPS
118 | J12 | STATCOM VSC-2 BAY | VSC-2 MV-J12 | PROTECTION RELAY - 1 FAILURE | SPS
119 | J12 | STATCOM VSC-2 BAY | VSC-2 MV-J12 | PROTECTION RELAY - 2 FAILURE | SPS
120 | J12 | STATCOM VSC-2 BAY | VSC-2 MV-J12 | PROTECTION RELAY - 3 FAILURE | SPS
121 | J12 | STATCOM VSC-2 BAY | VSC-2 MV-J12 | STATCOM READY FOR OPERATION | SPS
122 | J12 | STATCOM VSC-2 BAY | VSC-2 MV-J12 | SEQUENCE FAILURE | SPS
123 | J12 | STATCOM VSC-2 BAY | VSC-2 MV-J12 | SEQUENCE RUNNING | SPS
124 | J12 | STATCOM VSC-2 BAY | VSC-2 MV-J12 | LOCKOUT RELAYS ACTIVATED | SPS
125 | J12 | STATCOM VSC-2 BAY | VSC-2 J12 Q0 | INTERLOCK ENABLED | SPS
126 | J12 | STATCOM VSC-2 BAY | VSC-2 J12 Q1 | INTERLOCK ENABLED | SPS
127 | J12 | STATCOM VSC-2 BAY | VSC-2 J12 Q5 | INTERLOCK ENABLED | SPS
128 | J21 | STATCOM MSR-1 BAY | MSR-1 MV-J21 | PROTECTION RELAY - 1 TRIP | SPS
129 | J21 | STATCOM MSR-1 BAY | MSR-1 MV-J21 | PROTECTION RELAY - 2 TRIP | SPS
130 | J21 | STATCOM MSR-1 BAY | MSR-1 MV-J21 | LOCKOUT RELAYS ACTIVATED | SPS
131 | J21 | STATCOM MSR-1 BAY | MSR-1 MV-J21 | PROTECTION RELAY - 1 FAILURE | SPS
132 | J21 | STATCOM MSR-1 BAY | MSR-1 MV-J21 | PROTECTION RELAY - 2 FAILURE | SPS
133 | J21 | STATCOM MSR-1 BAY | MSR-1 J21 Q0 | INTERLOCK ENABLED | SPS
134 | J21 | STATCOM MSR-1 BAY | MSR-1 J21 Q1 | INTERLOCK ENABLED | SPS
135 | J21 | STATCOM MSR-1 BAY | MSR-1 J21 Q5 | INTERLOCK ENABLED | SPS
136 | J22 | STATCOM MSR-2 BAY | MSR-2 MV-J22 | PROTECTION RELAY - 1 TRIP | SPS
137 | J22 | STATCOM MSR-2 BAY | MSR-2 MV-J22 | PROTECTION RELAY - 2 TRIP | SPS
138 | J22 | STATCOM MSR-2 BAY | MSR-2 MV-J22 | PROTECTION RELAY - 1 FAILURE | SPS
139 | J22 | STATCOM MSR-2 BAY | MSR-2 MV-J22 | PROTECTION RELAY - 2 FAILURE | SPS
140 | J22 | STATCOM MSR-2 BAY | MSR-2 MV-J22 | LOCKOUT RELAYS ACTIVATED | SPS
141 | J22 | STATCOM MSR-2 BAY | MSR-2 J22 Q0 | INTERLOCK ENABLED | SPS
142 | J22 | STATCOM MSR-2 BAY | MSR-2 J22 Q1 | INTERLOCK ENABLED | SPS
143 | J22 | STATCOM MSR-2 BAY | MSR-2 J22 Q5 | INTERLOCK ENABLED | SPS
144 | J31 | STATCOM MSC-1 BAY | MSC-1 MV-J31 | PROTECTION RELAY - 1 TRIP | SPS
145 | J31 | STATCOM MSC-1 BAY | MSC-1 MV-J31 | PROTECTION RELAY - 2 TRIP | SPS
146 | J31 | STATCOM MSC-1 BAY | MSC-1 MV-J31 | PROTECTION RELAY - 1 FAILURE | SPS
147 | J31 | STATCOM MSC-1 BAY | MSC-1 MV-J31 | PROTECTION RELAY - 2 FAILURE | SPS
148 | J31 | STATCOM MSC-1 BAY | MSC-1 MV-J31 | LOCKOUT RELAYS ACTIVATED | SPS
149 | J31 | STATCOM MSC-1 BAY | MSC-1 J31 Q0 | INTERLOCK ENABLED | SPS
150 | J31 | STATCOM MSC-1 BAY | MSC-1 J31 Q1 | INTERLOCK ENABLED | SPS
151 | J31 | STATCOM MSC-1 BAY | MSC-1 J31 Q5 | INTERLOCK ENABLED | SPS
152 | J32 | STATCOM MSC-2 BAY | MSC-2 MV-J32 | PROTECTION RELAY - 1 TRIP | SPS
153 | J32 | STATCOM MSC-2 BAY | MSC-2 MV-J32 | PROTECTION RELAY - 2 TRIP | SPS
154 | J32 | STATCOM MSC-2 BAY | MSC-2 MV-J32 | PROTECTION RELAY - 1 FAILURE | SPS
155 | J32 | STATCOM MSC-2 BAY | MSC-2 MV-J32 | PROTECTION RELAY - 2 FAILURE | SPS
156 | J32 | STATCOM MSC-2 BAY | MSC-2 MV-J32 | LOCKOUT RELAYS ACTIVATED | SPS
157 | J32 | STATCOM MSC-2 BAY | MSC-2 J32 Q0 | INTERLOCK ENABLED | SPS
158 | J32 | STATCOM MSC-2 BAY | MSC-2 J32 Q1 | INTERLOCK ENABLED | SPS
159 | J32 | STATCOM MSC-2 BAY | MSC-2 J32 Q5 | INTERLOCK ENABLED | SPS
160 | STATCOM | STATCOM | STATCOM OPERATION | ACKNOWLEDGE VSC 1 | SPS
161 | STATCOM | STATCOM | STATCOM OPERATION | ACKNOWLEDGE VSC 2 | SPS
162 | STATCOM | STATCOM | STATCOM OPERATION | EMERGENCY TRIP | SPS
163 | STATCOM | STATCOM | STATCOM OPERATION | LOCAL HMI SELECTED | SPS
164 | STATCOM | STATCOM | STATCOM OPERATION | REMOTE HMI SELECTED | SPS
165 | STATCOM | STATCOM | STATCOM OPERATION | RCI SELECTED | SPS
166 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-1 | System 1: TRIP - OVERVOLTAGE HV DETECTED | SPS
167 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-1 | System 1: TRIP - LOCKOUT RELAY ACTIVATED (VSC 1) | SPS
168 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-1 | System 1: ESOF FROM CCS OR MMS (VSC 1) | SPS
169 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-1 | System 1: ESOF DUE TO CONVERTER FAILURE (VSC 1) | SPS
170 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-1 | System 1: ESOF AFTER EXTENDED CONVERTER BLOCKING T > 5 SEC (VSC 1) | SPS
171 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-1 | System 1: ESOF BY SEQUENCE FAULT - CP1 (VSC 1) | SPS
172 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-1 | System 1: ESOF BY FIREFIGHTING - IR SENSOR (VSC 1) | SPS
173 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-1 | System 1: TRIP - LOCKOUT RELAY ACTIVATED (VSC 2) | SPS
174 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-1 | System 1: ESOF FROM CCS OR MMS (VSC 2) | SPS
175 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-1 | System 1: ESOF DUE TO CONVERTER FAILURE (VSC 2) | SPS
176 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-1 | System 1: ESOF AFTER EXTENDED CONVERTER BLOCKING T > 5 SEC (VSC 2) | SPS
177 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-1 | System 1: ESOF BY SEQUENCE FAULT - CP1 (VSC 2) | SPS
178 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-1 | System 1: ESOF BY FIREFIGHTING - IR SENSOR (VSC 2) | SPS
179 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM 1 | TDC 1 FAULT | SPS
180 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-1 | SYSTEM 1: NO EXTERNAL TIME SYNCHRONISATION | SPS
181 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-2 | System 2: TRIP - OVERVOLTAGE HV DETECTED | SPS
182 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-2 | System 2: TRIP - LOCKOUT RELAY ACTIVATED (VSC 1) | SPS
183 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-2 | System 2: ESOF FROM CCS OR MMS (VSC 1) | SPS
184 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-2 | System 2: ESOF DUE TO CONVERTER FAILURE (VSC 1) | SPS
185 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-2 | System 2: ESOF AFTER EXTENDED CONVERTER BLOCKING T > 5 SEC (VSC 1) | SPS
186 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-2 | System 2: ESOF BY SEQUENCE FAULT - CP1 (VSC 1) | SPS
187 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-2 | System 2: ESOF BY FIREFIGHTING - IR SENSOR (VSC 1) | SPS
188 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-2 | System 2: TRIP - LOCKOUT RELAY ACTIVATED (VSC 2) | SPS
189 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-2 | System 2: ESOF FROM CCS OR MMS (VSC 2) | SPS
190 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-2 | System 2: ESOF DUE TO CONVERTER FAILURE (VSC 2) | SPS
191 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-2 | System 2: ESOF AFTER EXTENDED CONVERTER BLOCKING T > 5 SEC (VSC 2) | SPS
192 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-2 | System 2: ESOF BY SEQUENCE FAULT - CP1 (VSC 2) | SPS
193 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-2 | System 2: ESOF BY FIREFIGHTING - IR SENSOR (VSC 2) | SPS
194 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM 2 | TDC 2 FAULT | SPS
195 | STATCOM | STATCOM | STATCOM PROTECTION SYSTEM-2 | SYSTEM 2: NO EXTERNAL TIME SYNCHRONISATION | SPS
196 | STATCOM | STATCOM | STATCOM PROTECTION EMERGENCY TRIP | TRIP FROM EMERGENCY BUTTON | SPS
197 | STATCOM | STATCOM | STATCOM PROTECTION TFR TRIGGER | TFR TRIGGER CMD | SPS
198 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: STATCOM CONTROL WARNING | SPS
199 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: STATCOM CONTROL FAULT | SPS
200 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: STATCOM CONTROL TRIP | SPS
201 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: COMMUNICATION SUMMARY WARNING | SPS
202 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: COMMUNICATION SUMMARY FAULT | SPS
203 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: STATCOM BUILDING ALARM (AIR CONDITION) | SPS
204 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: AC AUXILIARY SUPPLY WARNING | SPS
205 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: AC AUXILIARY SUPPLY FAULT | SPS
206 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: STATCOM PLUS PROTECTION SYSTEM WARNING | SPS
207 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: STATCOM PLUS PROTECTION SYSTEM FAULT | SPS
208 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: STATCOM PLUS PROTECTION SYSTEM TRIP | SPS
209 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: DFR FAULT | SPS
210 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: DC AUXILIARY SUPPLY WARNING | SPS
211 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: DC AUXILIARY SUPPLY FAULT | SPS
212 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: STATCOM NOT READY | SPS
213 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: HV BUSBAR FAULT | SPS
214 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: HV BUSBAR TRIP | SPS
215 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: TRANSFORMER WARNING | SPS
216 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: TRANSFORMER FAULT | SPS
217 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: TRANSFORMER TRIP | SPS
218 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MV BUSBAR FAULT | SPS
219 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: VSC 1 WARNING | SPS
220 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: VSC 1 FAULT | SPS
221 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: VSC 1 TRIP | SPS
222 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: VSC 2 WARNING | SPS
223 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: VSC 2 FAULT | SPS
224 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: VSC 2 TRIP | SPS
225 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSR 1 WARNING | SPS
226 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSR 1 FAULT | SPS
227 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSR 1 TRIP | SPS
228 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSR 2 WARNING | SPS
229 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSR 2 FAULT | SPS
230 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSR 2 TRIP | SPS
231 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSC 1 WARNING | SPS
232 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSC 1 FAULT | SPS
233 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSC 1 TRIP | SPS
234 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSC 2 WARNING | SPS
235 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSC 2 FAULT | SPS
236 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSC 2 TRIP | SPS
237 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: COOLING SYSTEM VSC 1 WARNING | SPS
238 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: COOLING SYSTEM VSC 1 FAULT | SPS
239 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: COOLING SYSTEM VSC 1 TRIP | SPS
240 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: COOLING SYSTEM VSC 2 WARNING | SPS
241 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: COOLING SYSTEM VSC 2 FAULT | SPS
242 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: COOLING SYSTEM VSC 2 TRIP | SPS
243 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: VSC 1 PROTECTION WARNING | SPS
244 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: VSC 1 PROTECTION FAULT | SPS
245 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: VSC 1 PROTECTION TRIP | SPS
246 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: VSC 2 PROTECTION WARNING | SPS
247 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: VSC 2 PROTECTION FAULT | SPS
248 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: VSC 2 PROTECTION TRIP | SPS
249 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSR 1 PROTECTION WARNING | SPS
250 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSR 1 PROTECTION FAULT | SPS
251 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSR 1 PROTECTION TRIP | SPS
252 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSR 2 PROTECTION WARNING | SPS
253 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSR 2 PROTECTION FAULT | SPS
254 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSC 1 PROTECTION WARNING | SPS
255 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSC 1 PROTECTION FAULT | SPS
256 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSC 1 PROTECTION TRIP | SPS
257 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSC 2 PROTECTION WARNING | SPS
258 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSC 2 PROTECTION FAULT | SPS
259 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSC 2 PROTECTION TRIP | SPS
260 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: HV LINK PROTECTION WARNING | SPS
261 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: HV LINK PROTECTION TRIP | SPS
262 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: TRANSFORMER T0 PROTECTION WARNING | SPS
263 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: TRANSFORMER T0 PROTECTION FAULT | SPS
264 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: TRANSFORMER T0 PROTECTION TRIP | SPS
265 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: STATCOM MV BUSBAR PROTECTION WARNING | SPS
266 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: STATCOM MV BUSBAR PROTECTION FAULT | SPS
267 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: STATCOM MV BUSBAR PROTECTION TRIP | SPS
268 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: LV GROUNDING TRANSFORMER PROTECTION WARNING | SPS
269 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: LV GROUNDING TRANSFORMER PROTECTION FAULT | SPS
270 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: LV GROUNDING TRANSFORMER PROTECTION TRIP | SPS
271 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: AUX TRANSFORMER PROTECTION WARNING | SPS
272 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: AUX TRANSFORMER PROTECTION FAULT | SPS
273 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: AUX TRANSFORMER PROTECTION TRIP | SPS
274 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: UPS WARNING | SPS
275 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: FIRE PROTECTION SYSTEM ALARM | SPS
276 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: AUX VOLTAGE STABILIZER ALARM | SPS
277 | STATCOM | STATCOM | STATCOM GROUP ALARM | GROUP MESSAGE: MSR 2 PROTECTION TRIP | SPS
278 | STATCOM AUX | STATCOM AUX | DG SET | DG SET - ALTERNATOR ON | SPS
279 | STATCOM AUX | STATCOM AUX | DG SET | DG SET - DG INCOMING BREAKER ON | SPS
280 | STATCOM AUX | STATCOM AUX | DG SET | DG SET - ENGINE FAULT | SPS
281 | STATCOM AUX | STATCOM AUX | BUILDING FIRE ALARM | FIRE ALARM SYSTEM - BUILDING FIRE DETECTED | SPS
282 | STATCOM AUX | STATCOM AUX | TRANSFORMER FIRE ALARM | FIRE ALARM SYSTEM TRANSFORMER FIRE DETECTED | SPS
283 | STATCOM AUX | STATCOM AUX | COOLING SYSTEM UPS | UPS FOR VALVE COOLING - SWITCH ON MAINTENANCE BYPASS POSITION | SPS
284 | STATCOM AUX | STATCOM AUX | COOLING SYSTEM UPS | UPS FOR VALVE COOLING - AC SUPPLY FAULT | SPS
285 | STATCOM AUX | STATCOM AUX | COOLING SYSTEM UPS | UPS FOR VALVE COOLING - LOW DC VOLTAGE | SPS
286 | STATCOM AUX | STATCOM AUX | COOLING SYSTEM UPS | UPS FOR VALVE COOLING - LOAD ON STATIC BYPASS POSITION | SPS
287 | STATCOM AUX | STATCOM AUX | COOLING SYSTEM UPS | UPS FOR VALVE COOLING - COMMON ALARM | SPS
288 | STATCOM AUX | STATCOM AUX | COOLING SYSTEM UPS | UPS FOR VALVE COOLING - LOAD ON BATTERY | SPS
289 | STATCOM AUX | STATCOM AUX | COOLING SYSTEM UPS | UPS FOR VALVE COOLING - FAN FAILURE | SPS
290 | STATCOM AUX | STATCOM AUX | AIRCON | CONVERTER ROOM-1 AIR CONDITIONER TROUBLE | SPS
291 | STATCOM AUX | STATCOM AUX | AIRCON | CONVERTER ROOM-2 AIR CONDITIONER TROUBLE | SPS
292 | STATCOM AUX | STATCOM AUX | BCHARG220-1 | 220V DCDB 1 BATTERY CHARGER - AC SUPPLY FAULT | SPS
293 | STATCOM AUX | STATCOM AUX | BCHARG220-1 | 220V DCDB 1 BATTERY CHARGER - CHARGER TROUBLE | SPS
294 | STATCOM AUX | STATCOM AUX | BCHARG220-2 | 220V DCDB 2 BATTERY CHARGER - AC SUPPLY FAULT | SPS
295 | STATCOM AUX | STATCOM AUX | BCHARG220-2 | 220V DCDB 2 BATTERY CHARGER - CHARGER TROUBLE | SPS
STATCOM (RXPE)
1 | XX KV | FUTURE BAY | 89A | INTERLOCK ENABLED | SPS
2 | XX KV | FUTURE BAY | 89AE | INTERLOCK ENABLED | SPS
3 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | CB MANUAL OPEN | SPS
4 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | CB MANUAL CLOSE | SPS
5 | XX KV | FUTURE& COUPLING T/F-1 TIE | 89BE | EARTH SWITCH OPEN | SPS
6 | XX KV | FUTURE& COUPLING T/F-1 TIE | 89BE | EARTH SWITCH CLOSE | SPS
7 | XX KV | FUTURE& COUPLING T/F-1 TIE | BCU | BCU DC SUPPLY -1/2 FAIL | SPS
8 | XX KV | FUTURE& COUPLING T/F-1 TIE | BCU | BCU UNHEALTHY | SPS
9 | XX KV | FUTURE& COUPLING T/F-1 TIE | BCU | BCU TIME SYNC ERROR | SPS
10 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | CB OPERATION LOCKOUT | SPS
11 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | CB POLE DISCREPANCY OPTD. | SPS
12 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | CB TC-1 FAULTY | SPS
13 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | CB TC-2 FAULTY | SPS
14 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | CB LBB OPTD. | SPS
15 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | LBB Unhealthy | SPS
16 | XX KV | FUTURE& COUPLING T/F-1 TIE |  | BAY IN MAINTENANCE MODE | SPS
17 | XX KV | FUTURE& COUPLING T/F-1 TIE |  | 86A TRIP RELAY OPTD. | SPS
18 | XX KV | FUTURE& COUPLING T/F-1 TIE |  | 86B TRIP RELAY OPTD. | SPS
19 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | INTERLOCK ENABLED | SPS
20 | XX KV | FUTURE& COUPLING T/F-1 TIE | 89A | INTERLOCK ENABLED | SPS
21 | XX KV | FUTURE& COUPLING T/F-1 TIE | 89AE | INTERLOCK ENABLED | SPS
22 | XX KV | FUTURE& COUPLING T/F-1 TIE | 89B | INTERLOCK ENABLED | SPS
23 | XX KV | FUTURE& COUPLING T/F-1 TIE | 89BE | INTERLOCK ENABLED | SPS
24 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | CB COMPRESSOR / PUMP ON | SPS
25 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | CB AC SUPPLY FAIL | SPS
26 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | CB LOSS OF SF6 STG1 | SPS
27 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | CB LOSS OF SF6 STG2 | SPS
28 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | CB TROUBLE ALARM | SPS
29 | XX KV | FUTURE& COUPLING T/F-1 TIE |  | 86A TRIP RELAY UNHEALTHY | SPS
30 | XX KV | FUTURE& COUPLING T/F-1 TIE |  | 86B TRIP RELAY UNHEALTHY | SPS
31 | XX KV | FUTURE& COUPLING T/F-1 TIE |  | CB SPRING DISCHARGED / AIR /OIL PR LOW | SPS
32 | XX KV | FUTURE& COUPLING T/F-1 TIE |  | CB DC SUPPLY 1/2 FAIL | SPS
33 | XX KV | FUTURE& COUPLING T/F-1 TIE |  | CTRL SWITCH DEVICE TROUBLE/BYPASSED | SPS
34 | XX KV | FUTURE& COUPLING T/F-1 TIE | 52 | CB COMPRESSOR/PUMP RUN TIME EXCEEDED | SPS
35 | XX KV | COUPLING TRANSFORMER (HV) | 52 | CB OPERATION LOCKOUT | SPS
36 | XX KV | COUPLING TRANSFORMER (HV) | 52 | CB POLE DISCREPANCY OPTD. | SPS
37 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | DC SOURCE-1 FAIL | SPS
38 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | DC SOURCE-2 FAIL | SPS
39 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | CB TC-1 FAULTY | SPS
40 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | CB TC-2 FAULTY | SPS
41 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 86A TRIP RELAY OPTD. | SPS
42 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 86B TRIP RELAY OPTD. | SPS
43 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | Main-1 BB PROTN. OPTD. | SPS
44 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | Main-2 BB PROTN. OPTD. | SPS
45 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | MAIN CB LBB OPTD. | SPS
46 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | LBB Unhealthy | SPS
47 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OVERFLUX PROTECTION OPTD.(HV) | SPS
48 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | BACKUP E/F OPTD. (HV) | SPS
49 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OVERLOAD ALARM | SPS
50 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | REF PROTECTION OPTD. | SPS
51 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TRANSFORMER DIFF. PROTECTION OPTD(R-PH) | SPS
52 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | BACKUP O/C OPTD. (HV)(R-PH) | SPS
53 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | BUCHHOLZ TRIP(R-PH) | SPS
54 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OLTC PRV TRIP(R-PH) | SPS
55 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OTI TRIP(R-PH) | SPS
56 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TRANSFORMER PRV TRIP(R-PH) | SPS
57 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI TRIP (HV/IV/LV)(R-PH) | SPS
58 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OVERFLUX ALARM (HV)(R-PH) | SPS
59 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | BUCHHOLZ ALARM(R-PH) | SPS
60 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | LOW OIL LEVEL ALARM(R-PH) | SPS
61 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OTI ALARM(R-PH) | SPS
62 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI ALARM (HV/IV/LV)(R-PH) | SPS
63 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TAP CHANGER IN PROGRESS | SPS
64 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TAP CHANGER IN REMOTE | SPS
65 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TAP CHANGER OUT OF STEP | SPS
66 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OLTC DRIVE MOTOR FAULY ALARM | SPS
67 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | CB COMPRESSOR / PUMP ON | SPS
68 | XX KV | COUPLING TRANSFORMER (HV) | 52 | CB AC SUPPLY FAIL | SPS
69 | XX KV | COUPLING TRANSFORMER (HV) | 52 | CB LOSS OF SF6 STG1 | SPS
70 | XX KV | COUPLING TRANSFORMER (HV) | 52 | CB LOSS OF SF6 STG2 | SPS
71 | XX KV | COUPLING TRANSFORMER (HV) | 52 | CB TROUBLE ALARM | SPS
72 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TAP CHANGER IN FOLLOWER MODE | SPS
73 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TAP CHANGER IN INDEPENDENT MODE | SPS
74 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TAP CHANGER IN MASTER MODE | SPS
75 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | COOLING SYSTEM TROUBLE ALARM(R-PH) | SPS
76 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | FANS FAIL TO START BANK-A/B(R-PH) | SPS
77 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | FANS RUNNING BANK-A/B(R-PH) | SPS
78 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | PUMPS FAIL TO START BANK-A/B(R-PH) | SPS
79 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | PUMPS RUNNING BANK-A/B(R-PH) | SPS
80 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OIL FLOW LOW ALARM BANK-A/B(R-PH) | SPS
81 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | FAN/PUMP THERMALO/L TRIP ALARM(R-PH) | SPS
82 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 86A TRIP RELAY UNHEALTHY | SPS
83 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 86B TRIP RELAY UNHEALTHY | SPS
84 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | CB SPRING DISCHARGED/AIR/OIL PR LOW | SPS
85 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | CB DC SUPPLY 1/2 FAIL | SPS
86 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | CONDITIONING MONITORING DEVICE FOR DGA-UNHEALTHY | SPS
87 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TRANSFORMER DIFF. PROTECTION OPTD(Y-PH) | SPS
88 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | BACKUP O/C OPTD. (HV)(Y-PH) | SPS
89 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | BUCHHOLZ TRIP(Y-PH) | SPS
90 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OLTC PRV TRIP(Y-PH) | SPS
91 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OTI TRIP(Y-PH) | SPS
92 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TRANSFORMER PRV TRIP(Y-PH) | SPS
93 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI TRIP (HV/IV/LV)(Y-PH) | SPS
94 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OVERFLUX ALARM (HV)(Y-PH) | SPS
95 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | BUCHHOLZ ALARM(Y-PH) | SPS
96 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | LOW OIL LEVEL ALARM(Y-PH) | SPS
97 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OTI ALARM(Y-PH) | SPS
98 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI ALARM (HV/IV/LV)(Y-PH) | SPS
99 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | COOLING SYSTEM TROUBLE ALARM(Y-PH) | SPS
100 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | FANS FAIL TO START BANK-A/B(Y-PH) | SPS
101 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | FANS RUNNING BANK-A/B(Y-PH) | SPS
102 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | PUMPS FAIL TO START BANK-A/B(Y-PH) | SPS
103 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | PUMPS RUNNING BANK-A/B(Y-PH) | SPS
104 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OIL FLOW LOW ALARM BANK-A/B(Y-PH) | SPS
105 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | FAN/PUMP THERMALO/L TRIP ALARM(Y-PH) | SPS
106 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TRANSFORMER DIFF. PROTECTION OPTD(B-PH) | SPS
107 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | BACKUP O/C OPTD. (HV)(B-PH) | SPS
108 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | BUCHHOLZ TRIP(B-PH) | SPS
109 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OLTC PRV TRIP(B-PH) | SPS
110 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OTI TRIP(B-PH) | SPS
111 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TRANSFORMER PRV TRIP(B-PH) | SPS
112 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI TRIP (HV/IV/LV)(B-PH) | SPS
113 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OVERFLUX ALARM (HV)(B-PH) | SPS
114 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | BUCHHOLZ ALARM(B-PH) | SPS
115 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | LOW OIL LEVEL ALARM(B-PH) | SPS
116 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OTI ALARM(B-PH) | SPS
117 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI ALARM (HV/IV/LV)(B-PH) | SPS
118 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | COOLING SYSTEM TROUBLE ALARM(B-PH) | SPS
119 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | FANS FAIL TO START BANK-A/B(B-PH) | SPS
120 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | FANS RUNNING BANK-A/B(B-PH) | SPS
121 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | PUMPS FAIL TO START BANK-A/B(B-PH) | SPS
122 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | PUMPS RUNNING BANK-A/B(B-PH) | SPS
123 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OIL FLOW LOW ALARM BANK-A/B(B-PH) | SPS
124 | XX KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | FAN/PUMP THERMALO/L TRIP ALARM(B-PH) | SPS
125 | XX KV | COUPLING TRANSFORMER | STATCOM HV BAY - 52 | INTERLOCK ENABLED | SPS
126 | XX KV | COUPLING TRANSFORMER | STATCOM HV BAY - 89A | INTERLOCK ENABLED | SPS
127 | XX KV | COUPLING TRANSFORMER | STATCOM HV BAY- 89 | INTERLOCK ENABLED | SPS
128 | XX KV | COUPLING TRANSFORMER | STATCOM HV BAY- 89TR | INTERLOCK ENABLED | SPS
129 | XX KV | COUPLING TRANSFORMER | STATCOM HV BAY- 89TSR | INTERLOCK ENABLED | SPS
130 | XX KV | COUPLING TRANSFORMER | STATCOM HV BAY- 89TY | INTERLOCK ENABLED | SPS
131 | XX KV | COUPLING TRANSFORMER | STATCOM HV BAY- 89TSY | INTERLOCK ENABLED | SPS
132 | XX KV | COUPLING TRANSFORMER | STATCOM HV BAY- 89TB | INTERLOCK ENABLED | SPS
133 | XX KV | COUPLING TRANSFORMER | STATCOM HV BAY- 89TSB | INTERLOCK ENABLED | SPS
134 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | TRANSFORMER DIFF. PROTECTION OPTD(SP) | SPS
135 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | BACKUP O/C OPTD. (HV)(SP) | SPS
136 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | BUCHHOLZ TRIP(SP) | SPS
137 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | OLTC PRV TRIP(SP) | SPS
138 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | OTI TRIP (SP) | SPS
139 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | TRANSFORMER PRV TRIP (SP) | SPS
140 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | WTI TRIP (HV/IV/LV) (SP) | SPS
141 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | OVERFLUX ALARM (HV) (SP) | SPS
142 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | BUCHHOLZ ALARM (SP) | SPS
143 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | LOW OIL LEVEL ALARM (SP) | SPS
144 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | OTI ALARM (SP) | SPS
145 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | WTI ALARM (HV/IV/LV) (SP) | SPS
146 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | COOLING SYSTEM TROUBLE ALARM (SP) | SPS
147 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | FANS FAIL TO START BANK-A (SP) | SPS
148 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | FANS FAIL TO START BANK-B (SP) | SPS
149 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | FANS RUNNING BANK-A/B (SP) | SPS
150 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | PUMPS FAIL TO START BANK-A (SP) | SPS
151 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | PUMPS FAIL TO START BANK-B (SP) | SPS
152 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | PUMPS RUNNING BANK-A/B (SP) | SPS
153 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | OIL FLOW LOW ALARM BANK-A (SP) | SPS
154 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | OIL FLOW LOW ALARM BANK-B (SP) | SPS
155 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | OLTC DRIVE MOTOR FAULY ALARM (SP) | SPS
156 | XX KV | SPARE COUPLING T/F | SPARE TRAFO | FAN/PUMP THERMALO/L TRIP ALARM (SP) | SPS
157 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TR1 | INTERLOCK ENABLED | SPS
158 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TR2 | INTERLOCK ENABLED | SPS
159 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TY1 | INTERLOCK ENABLED | SPS
160 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TY2 | INTERLOCK ENABLED | SPS
161 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TB1 | INTERLOCK ENABLED | SPS
162 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TB2 | INTERLOCK ENABLED | SPS
163 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSR1 | INTERLOCK ENABLED | SPS
164 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSR2 | INTERLOCK ENABLED | SPS
165 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSY1 | INTERLOCK ENABLED | SPS
166 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSY2 | INTERLOCK ENABLED | SPS
167 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSB1 | INTERLOCK ENABLED | SPS
168 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSB2 | INTERLOCK ENABLED | SPS
169 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TR1E | INTERLOCK ENABLED | SPS
170 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TR2E | INTERLOCK ENABLED | SPS
171 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TY1E | INTERLOCK ENABLED | SPS
172 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TY2E | INTERLOCK ENABLED | SPS
173 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TB1E | INTERLOCK ENABLED | SPS
174 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TB2E | INTERLOCK ENABLED | SPS
175 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSR1E | INTERLOCK ENABLED | SPS
176 | 38.5KV | COUPLING T/F (S) | ICT (MV) 60089TSR2E | INTERLOCK ENABLED | SPS
177 | 38.5KV | MV BUS BAR | 60089E | INTERLOCK ENABLED | SPS
178 | 38.5 KV | MV BUS BAR | MV BUS BAR | MV BUS PROTECTION TRIP | SPS
179 | 38.5 KV | MV BUS BAR | MV BUS BAR | MV BUS PROTECTION RELAY FAILURE | SPS
180 | 38.5KV | STATCOM- 1 | STATCOM VSC 60189A | INTERLOCK ENABLED | SPS
181 | 38.5KV | STATCOM- 1 | STATCOM VSC 60189AE | INTERLOCK ENABLED | SPS
182 | 38.5KV | STATCOM- 1 | VSC-1 | STATCOM-1 COMMON ALARM | SPS
183 | 38.5KV | STATCOM- 1 | VSC-1 | STATCOM 1 PROTECTION TRIP | SPS
184 | 38.5KV | STATCOM- 1 | VSC-1 | PROTECTION RELAY FAILURE | SPS
185 | 38.5KV | STATCOM- 1 | VSC-1 | MASTER TRIP A | SPS
186 | 38.5KV | STATCOM- 1 | VSC-1 | MASTER TRIP B | SPS
187 | 38.5KV | STATCOM- 1 | VSC-1 | COOLING SYSTEM ALARM | SPS
188 | 38.5KV | STATCOM- 1 | VSC-1 | COOLING SYSTEM TRIP | SPS
189 | 38.5KV | STATCOM- 1 | VSC-1 | CB TROUBLE ALARM | SPS
190 | 38.5KV | STATCOM- 1 | VSC-1 | STATCOM-1 READY FOR OPERATION | SPS
191 | 38.5KV | STATCOM- 1 | VSC-1 | STATCOM-1 ORDER RUNNING | SPS
192 | 38.5KV | STATCOM- 1 | VSC-1 | STATCOM-1 COOLING SYSTEM STATUS | SPS
193 | 38.5KV | STATCOM- 2 | STATCOM VSC 60289A | INTERLOCK ENABLED | SPS
194 | 38.5KV | STATCOM- 2 | STATCOM VSC 60289AE | INTERLOCK ENABLED | SPS
195 | 38.5KV | STATCOM- 2 | VSC-2 | STATCOM-2 COMMON ALARM | SPS
196 | 38.5KV | STATCOM- 2 | VSC-2 | STATCOM 2 PROTECTION TRIP | SPS
197 | 38.5KV | STATCOM- 2 | VSC-2 | PROTECTION RELAY FAILURE | SPS
198 | 38.5KV | STATCOM- 2 | VSC-2 | MASTER TRIP A | SPS
199 | 38.5KV | STATCOM- 2 | VSC-2 | MASTER TRIP B | SPS
200 | 38.5KV | STATCOM- 2 | VSC-2 | COOLING SYSTEM ALARM | SPS
201 | 38.5KV | STATCOM- 2 | VSC-2 | COOLING SYSTEM TRIP | SPS
202 | 38.5KV | STATCOM- 2 | VSC-2 | CB TROUBLE ALARM | SPS
203 | 38.5KV | STATCOM- 2 | VSC-2 | STATCOM-2 READY FOR OPERATION | SPS
204 | 38.5KV | STATCOM- 2 | VSC-2 | STATCOM-2 CB ORDER RUNNNING | SPS
205 | 38.5KV | STATCOM- 2 | VSC-2 | STATCOM-2 COOLING SYSTEM STATUS | SPS
206 | 38.5KV | MSC | 60352 | INTERLOCK ENABLED | SPS
207 | 38.5KV | MSC | 60389A | INTERLOCK ENABLED | SPS
208 | 38.5KV | MSC | 60389AE | INTERLOCK ENABLED | SPS
209 | 38.5KV | MSC | MSC | PROTECTION TRIP | SPS
210 | 38.5KV | MSC | MSC | PROTECTION RELAY FAILURE | SPS
211 | 38.5KV | MSC | MSC | MASTER TRIP A | SPS
212 | 38.5KV | MSC | MSC | MASTER TRIP B | SPS
213 | 38.5KV | MSC | MSC | CB TROUBLE ALARM | SPS
214 | 38.5KV | MSR- 1 | 60452 | INTERLOCK ENABLED | SPS
215 | 38.5KV | MSR- 1 | 60489A | INTERLOCK ENABLED | SPS
216 | 38.5KV | MSR- 1 | 60489AE | INTERLOCK ENABLED | SPS
217 | 38.5KV | MSR- 1 | MSR-1 | PROTECTION TRIP | SPS
218 | 38.5KV | MSR- 1 | MSR-1 | PROTECTION RELAY FAILURE | SPS
219 | 38.5KV | MSR- 1 | MSR-1 | MASTER TRIP A | SPS
220 | 38.5KV | MSR- 1 | MSR-1 | MASTER TRIP B | SPS
221 | 38.5KV | MSR- 1 | MSR-1 | CB TROUBLE ALARM | SPS
222 | 38.5KV | MSR- 2 | 60552 | INTERLOCK ENABLED | SPS
223 | 38.5KV | MSR- 2 | 60589A | INTERLOCK ENABLED | SPS
224 | 38.5KV | MSR- 2 | 60589AE | INTERLOCK ENABLED | SPS
225 | 38.5KV | MSR- 2 | MSR-2 | PROTECTION TRIP | SPS
226 | 38.5KV | MSR- 2 | MSR-2 | PROTECTION RELAY FAILURE | SPS
227 | 38.5KV | MSR- 2 | MSR-2 | MASTER TRIP A | SPS
228 | 38.5KV | MSR- 2 | MSR-2 | MASTER TRIP B | SPS
229 | 38.5KV | MSR- 2 | MSR-2 | CB TROUBLE ALARM | SPS
230 | 38.5KV | AUX T/F | 60652 | INTERLOCK ENABLED | SPS
231 | 38.5KV | AUX T/F | 60689A | INTERLOCK ENABLED | SPS
232 | 38.5KV | AUX T/F | 60689AE | INTERLOCK ENABLED | SPS
233 | 38.5KV | AUX T/F | 60652 | CB TROUBLE ALARM | SPS
234 | 38.5KV | AUX T/F | PROTN | PROTECTION TRIP | SPS
235 | 38.5KV | AUX T/F | PROTN | PROTECTION RELAY FAILURE | SPS
236 | 38.5KV | AUX T/F | PROTN | MASTER TRIP A | SPS
237 | 38.5KV | AUX T/F | PROTN | MASTER TRIP B | SPS
238 | 38.5KV | AUX T/F | AVR | AVR FAIL ALARM | SPS
239 | 38.5KV | STATCOM NGT BAY | GND TRANSFORMER | PROTECTION TRIP | SPS
240 | 38.5KV | STATCOM CONTROL | STATCOM | ONE KEY START STATUS | SPS
241 | 38.5KV | STATCOM CONTROL | STATCOM | ONE KEY STOP STATUS | SPS
242 | 38.5KV | STATCOM CONTROL | STATCOM | ONE KEY EXIT STATUS | SPS
243 | 38.5KV | STATCOM CONTROL | STATCOM | STATCOM 1 EMG. STOP STATUS | SPS
244 | 38.5KV | STATCOM CONTROL | STATCOM | STATCOM 2 EMG. STOP STATUS | SPS
245 | 38.5KV | STATCOM CONTROL | STATCOM | SUBSTATION EMG. STOP STATUS | SPS
246 | 38.5KV | STATCOM CONTROL | STATCOM | EXTERNAL CONTROL AUTO (MSR & MSC, HV B/R) | SPS
247 | 38.5KV | STATCOM CONTROL | STATCOM | EXTERNAL CONTROL MANUAL (MSR & MSC, HV B/R) | SPS
248 | 38.5KV | STATCOM CONTROL | STATCOM | VOLTAGE MODE CONTROL | SPS
249 | 38.5KV | STATCOM CONTROL | STATCOM | REACTIVE MODE CONTROL | SPS
250 | 38.5KV | STATCOM CONTROL | CONTROLLER | CONTROLLER 1 FAULT | SPS
251 | 38.5KV | STATCOM CONTROL | CONTROLLER | CONTROLLER 2 FAULT | SPS
252 | 38.5KV | SAS | COMMON RXPE LOCAL HMI | LOCAL HMI SELECTED | SPS
253 | 38.5KV | SAS | COMMON RXPE REMOTE HMI | REMOTE HMI SELECTED | SPS
254 | 38.5KV | SAS | COMMON GPS | TIME SYNCHRONIZATION ERROR(GPS ERROR) | SPS
255 | 38.5KV | SAS | COMMON STATCOM GATEWAY | COMMUNICATION ALARM/WARNING | SPS
256 | 38.5KV | SAS | COMMON STATCOM GATEWAY | COMMUNICATION FAULT | SPS
257 | 38.5KV | AUX | COMMON NWP PANEL | 220V DC-1 FAIL | SPS
258 | 38.5KV | AUX | COMMON NWP PANEL | 220V DC-2 FAIL | SPS
259 | 415 V | AUX | FP CUPLING TRAFO | DELUGE SYSTEM OPERATING FOR CT R-PH | SPS
260 | 415 V | AUX | FP CUPLING TRAFO | FIRE IN COUPLING TRAFO R-PH | SPS
261 | 415 V | AUX | FP CUPLING TRAFO | DELUGE SYSTEM OPERATING FOR CT Y-PH | SPS
262 | 415 V | AUX | FP CUPLING TRAFO | FIRE IN COUPLING TRAFO Y-PH | SPS
263 | 415 V | AUX | FP CUPLING TRAFO | DELUGE SYSTEM OPERATING FOR CT B-PH | SPS
264 | 415 V | AUX | FP CUPLING TRAFO | FIRE IN COUPLING TRAFO B-PH | SPS
265 | 415 V | AUX | FP CUPLING TRAFO | DELUGE SYSTEM OPERATING FOR CT S-PH | SPS
266 | 415 V | AUX | FP CUPLING TRAFO | FIRE IN COUPLING TRAFO S-PH | SPS
267 | 415 V | AUX | FP SMOKE ALARM | CONTROL ROOM ZONE-1 FIRE DETECTED | SPS
268 | 415 V | AUX | FP SMOKE ALARM | CONTROL ROOM ZONE-2 FIRE DETECTED | SPS
269 | 415 V | AUX | FP SMOKE ALARM | CONTROL ROOM ZONE-3 FIRE DETECTED | SPS
270 | 415 V | AUX | FP SMOKE ALARM | CONTROL ROOM ZONE-4 FIRE DETECTED | SPS
271 | 415 V | AUX | FP SMOKE ALARM | CONTROL ROOM ZONE-5 FIRE DETECTED | SPS
272 | 415 V | AUX | FP SMOKE ALARM | CONTROL ROOM ZONE-6 FIRE DETECTED | SPS
273 | 415 V | AUX | FP SMOKE ALARM | CONTROL ROOM ZONE-7 FIRE DETECTED | SPS
274 | 415 V | AUX | FP SMOKE ALARM | CONTROL ROOM ZONE-8 FIRE DETECTED | SPS
275 | 415 V | AUX | FP SMOKE ALARM | CONTROL ROOM ZONE-9 FIRE DETECTED | SPS
276 | 415 V | AUX | FP SMOKE ALARM | CONTROL ROOM ZONE-10 FIRE DETECTED | SPS
277 | 415 V | AUX | FP SMOKE ALARM | CONTROL ROOM ZONE-11 FIRE DETECTED | SPS
278 | 415 V | AUX | FP SMOKE ALARM | CONTROL ROOM ZONE-12 FIRE DETECTED | SPS
279 | 415 V | AUX | FP SMOKE ALARM | CONTROL ROOM ZONE-13 FIRE DETECTED | SPS
280 | 415 V | AUX | FP SMOKE ALARM | CONTROL ROOM ZONE-14 FIRE DETECTED | SPS
281 | 415 V | AUX | CHARGER-1 | AC POWER FAIL | SPS
282 | 415 V | AUX | CHARGER-1 | RECTIFIER/CHARGER FUSE FAIL | SPS
283 | 415 V | AUX | CHARGER-1 | OVER VOLTAGE ALARM | SPS
284 | 415 V | AUX | CHARGER-1 | UNDER VOLTAGE ALARM | SPS
285 | 415 V | AUX | DCDB-1 | DC-1 EARTH FAULT ALARM | SPS
286 | 415 V | AUX | CHARGER-2 | AC POWER FAIL | SPS
287 | 415 V | AUX | CHARGER-2 | RECTIFIER/CHARGER FUSE FAIL | SPS
288 | 415 V | AUX | CHARGER-2 | OVER VOLTAGE ALARM | SPS
289 | 415 V | AUX | CHARGER-2 | UNDER VOLTAGE ALARM | SPS
290 | 415 V | AUX | DCDB-2 | DC-2 EARTH FAULT ALARM | SPS
291 | 415 V | AUX | UPS-1 | UPS-1 BATTERY LOW ALARM | SPS
292 | 415 V | AUX | UPS-2 | UPS-2 BATTERY LOW ALARM | SPS
293 | 33KV | AUX | TERTIARY 33KV PROTN | TERTIARY TRANSF PROTN OPTD | SPS
294 | 33KV | AUX | TERTIARY 33KV CB | CB INTERLOCK ENABLED | SPS
295 | 33KV | AUX | TERTIARY 33KV ISOLATOR | ISOLATOR INTERLOCK ENABLED | SPS
296 | 415 V | AUX | DG SET AMF PANEL | MAINS-1 ON | SPS
297 | 415 V | AUX | DG SET AMF PANEL | ALTERNATOR FAIL | SPS
298 | 415 V | AUX | DG SET AMF PANEL | ALTERNATOR ON | SPS
299 | 415 V | AUX | DG SET AMF PANEL | CHARGER-1 OFF | SPS
300 | 415 V | AUX | DG SET AMF PANEL | CHARGER-2 OFF | SPS
301 | 415 V | AUX | DG SET AMF PANEL | OVERSPEED | SPS
302 | 415 V | AUX | DG SET AMF PANEL | MAIN-2 LT SUPPLY ON/OFF | SPS
303 | 415 V | AUX | DG SET AMF PANEL | ENGINE OVER HEATING | SPS
304 | 415 V | AUX | DG SET AMF PANEL | LOW FUEL | SPS
305 | 415 V | AUX | DG SET AMF PANEL | LOW OIL PRESSURE | SPS
306 | 415 V | AUX | DG SET AMF PANEL | SET TO START 30S AFTER RX 1ST TIMER | SPS
307 | 415 V | AUX | DG SET AMF PANEL | HIGH COOLING WATER TEMPERATURE | SPS
308 | 415 V | AUX | DG SET AMF PANEL | LACK OF FUEL | SPS
309 | 415 V | AUX | DG SET AMF PANEL | DG SET RUNNING | SPS
310 | 415 V | AUX | AIRCON STATCOM-1 | STATCOM-1 AIR CONDITIONER TROUBLE ALARM | SPS
311 | 415 V | AUX | AIRCON STATCOM-2 | STATCOM-2 AIR CONDITIONER TROUBLE ALARM | SPS
STATCOM (HYOSUNG)
1 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | MAIN-A PROTECTION TRIP | SPS
2 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | MAIN-B PROTECTION TRIP | SPS
3 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | MAIN-A PROTECTION RELAY FAILURE | SPS
4 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | MAIN-B PROTECTION RELAY FAILURE | SPS
5 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) WTI-HV ALARM | SPS
6 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) WTI-LV ALARM | SPS
7 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) OTI ALARM | SPS
8 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) BUCHHOLZ RELAY-1 ALARM | SPS
9 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) BUCHHOLZ RELAY-2 ALARM | SPS
10 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) BUCHHOLZ RELAY-1 TRIP | SPS
11 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) BUCHHOLZ RELAY-2 TRIP | SPS
12 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) PRD-1 TRIP | SPS
13 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) PRD-2 TRIP | SPS
14 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) WTI-HV TRIP | SPS
15 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) WTI-LV TRIP | SPS
16 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) OTI TRIP | SPS
17 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) SPR TRIP | SPS
18 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) WTI-HV ALARM | SPS
19 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) WTI-LV ALARM | SPS
20 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) OTI ALARM | SPS
21 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) BUCHHOLZ RELAY-1 ALARM | SPS
22 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) BUCHHOLZ RELAY-2 ALARM | SPS
23 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) BUCHHOLZ RELAY-1 TRIP | SPS
24 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) BUCHHOLZ RELAY-2 TRIP | SPS
25 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) PRD-1 TRIP | SPS
26 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) PRD-2 TRIP | SPS
27 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) WTI-HV TRIP | SPS
28 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) WTI-LV TRIP | SPS
29 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) OTI TRIP | SPS
30 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) SPR TRIP | SPS
31 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) WTI-HV ALARM | SPS
32 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) WTI-LV ALARM | SPS
33 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) OTI ALARM | SPS
34 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) BUCHHOLZ RELAY-1 ALARM | SPS
35 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) BUCHHOLZ RELAY-2 ALARM | SPS
36 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) BUCHHOLZ RELAY-1 TRIP | SPS
37 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) BUCHHOLZ RELAY-2 TRIP | SPS
38 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) PRD-1 TRIP | SPS
39 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) PRD-2 TRIP | SPS
40 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) WTI-HV TRIP | SPS
41 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) WTI-LV TRIP | SPS
42 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) OTI TRIP | SPS
43 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) SPR TRIP | SPS
44 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) WTI-HV ALARM | SPS
45 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) WTI-LV ALARM | SPS
46 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) OTI ALARM | SPS
47 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) BUCHHOLZ RELAY-1 ALARM | SPS
48 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) BUCHHOLZ RELAY-2 ALARM | SPS
49 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) BUCHHOLZ RELAY-1 TRIP | SPS
50 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) BUCHHOLZ RELAY-2 TRIP | SPS
51 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) PRD-1 TRIP | SPS
52 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) PRD-2 TRIP | SPS
53 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) WTI-HV TRIP | SPS
54 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) WTI-LV TRIP | SPS
55 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) OTI TRIP | SPS
56 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) SPR TRIP | SPS
57 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | GROUP MESSAGE : (C. TRAFO R-PH) FAN FAIL | SPS
58 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | GROUP MESSAGE : (C. TRAFO Y-PH) FAN FAIL | SPS
59 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | GROUP MESSAGE : (C. TRAFO B-PH) FAN FAIL | SPS
60 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | GROUP MESSAGE : (C. TRAFO SP-PH) FAN FAIL | SPS
61 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | SP TR. R-PH SELECTED | SPS
62 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | SP TR. Y-PH SELECTED | SPS
63 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | SP TR. B-PH SELECTED | SPS
64 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | SP TR. DE-SELECTED | SPS
65 | 400KV | COUPLING TRANSFORMER (HV) | 52 | INTERLOCK ENABLED | SPS
66 | 400KV | COUPLING TRANSFORMER (HV) | 89A | INTERLOCK ENABLED | SPS
67 | 400KV | COUPLING TRANSFORMER (HV) | 89AE | INTERLOCK ENABLED | SPS
68 | 400KV | COUPLING TRANSFORMER (HV) | 89B | INTERLOCK ENABLED | SPS
69 | 400KV | COUPLING TRANSFORMER (HV) | 89BE | INTERLOCK ENABLED | SPS
70 | 400KV | COUPLING TRANSFORMER (HV) | 89TR | INTERLOCK ENABLED | SPS
71 | 400KV | COUPLING TRANSFORMER (HV) | 89TRE | INTERLOCK ENABLED | SPS
72 | 400KV | COUPLING TRANSFORMER (HV) | 89TSR | INTERLOCK ENABLED | SPS
73 | 400KV | COUPLING TRANSFORMER (HV) | 89TY | INTERLOCK ENABLED | SPS
74 | 400KV | COUPLING TRANSFORMER (HV) | 89TYE | INTERLOCK ENABLED | SPS
75 | 400KV | COUPLING TRANSFORMER (HV) | 89TSY | INTERLOCK ENABLED | SPS
76 | 400KV | COUPLING TRANSFORMER (HV) | 89TB | INTERLOCK ENABLED | SPS
77 | 400KV | COUPLING TRANSFORMER (HV) | 89TBE | INTERLOCK ENABLED | SPS
78 | 400KV | COUPLING TRANSFORMER (HV) | 89TSB | INTERLOCK ENABLED | SPS
79 | 400KV | COUPLING TRANSFORMER (HV) | 89TSBE | INTERLOCK ENABLED | SPS
80 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400KV MAIN BAY LBB PROTECTION TRIP | SPS
81 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY LBB RELAY FAILURE | SPS
82 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY BCU FAILURE | SPS
83 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY 86.1 TRIP RELAY OPERATED | SPS
84 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY 86.2 TRIP RELAY OPERATED | SPS
85 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY CT SF6 Loss Alarm | SPS
86 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY CT SF6 Lockout Alarm | SPS
87 | 400KV | COUPLING TRANSFORMER (HV) | 52 | 400kV MAIN BAY CB SF6 Loss Alarm | SPS
88 | 400KV | COUPLING TRANSFORMER (HV) | 52 | 400kV MAIN BAY CB SF6 Lockout Alarm 1/2 | SPS
89 | 400KV | COUPLING TRANSFORMER (HV) | 52 | 400kV MAIN BAY CB DC-1/2 Fail | SPS
90 | 400KV | COUPLING TRANSFORMER (HV) | 52 | 400kV MAIN BAY CB Pole Descripency Alarm | SPS
91 | 400KV | COUPLING TRANSFORMER (HV) | 52 | 400kV MAIN BAY CB TC-1 Faulty | SPS
92 | 400KV | COUPLING TRANSFORMER (HV) | 52 | 400kV MAIN BAY CB TC-2 Faulty | SPS
93 | 400KV | COUPLING TRANSFORMER (HV) | 52 | 400kV MAIN BAY CB Spring Charged | SPS
94 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY CSD Alarm | SPS
95 | 400KV | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY CSD out of service | SPS
96 | 20KV | COUPLING TRANSFORMER (MV) | 89TR | INTERLOCK ENABLED | SPS
97 | 20KV | COUPLING TRANSFORMER (MV) | 89TY | INTERLOCK ENABLED | SPS
98 | 20KV | COUPLING TRANSFORMER (MV) | 89TB | INTERLOCK ENABLED | SPS
99 | 20KV | COUPLING TRANSFORMER (MV) | 89TSR | INTERLOCK ENABLED | SPS
100 | 20KV | COUPLING TRANSFORMER (MV) | 89TSY | INTERLOCK ENABLED | SPS
101 | 20KV | COUPLING TRANSFORMER (MV) | 89TSB | INTERLOCK ENABLED | SPS
102 | 20KV | COUPLING TRANSFORMER (MV) | 89TER | INTERLOCK ENABLED | SPS
103 | 20KV | COUPLING TRANSFORMER (MV) | 89TEY | INTERLOCK ENABLED | SPS
104 | 20KV | COUPLING TRANSFORMER (MV) | 89TEB | INTERLOCK ENABLED | SPS
105 | 20KV | COUPLING TRANSFORMER (MV) | TSER | INTERLOCK ENABLED | SPS
106 | 20KV | STATCOM-1 | VSC-1 | MAIN PROTECTION TRIP | SPS
107 | 20KV | STATCOM-1 | VSC-1 | MAIN LBB PROTECTION TRIP | SPS
108 | 20KV | STATCOM-1 | VSC-1 | CONTROLLER FAILURE TRIP | SPS
109 | 20KV | STATCOM-1 | VSC-1 | BACKUP PROTECTION TRIP | SPS
110 | 20KV | STATCOM-1 | VSC-1 | BACKUP LBB PROTECTION TRIP | SPS
111 | 20KV | STATCOM-1 | VSC-1 | MAIN PROTECTION RELAY FAILURE | SPS
112 | 20KV | STATCOM-1 | VSC-1 | BACKUP PROTECTION RELAY FAILURE | SPS
113 | 20KV | STATCOM-1 | VSC-1 | TRIP RELAY-A(86A) OPERATED | SPS
114 | 20KV | STATCOM-1 | VSC-1 | TRIP RELAY-B(86B) OPERATED | SPS
115 | 20KV | STATCOM-1 | VSC-1 | GROUP MESSAGE : STATCOM UNIT-1 CONTROLLER A FAILURE (COMM. FAIL / HW FAIL) | SPS
116 | 20KV | STATCOM-1 | VSC-1 | GROUP MESSAGE : STATCOM UNIT-1 CONTROLLER B FAILURE (COMM. FAIL / HW FAIL) | SPS
117 | 20KV | STATCOM-1 | VSC-1 | GROUP MESSAGE : (COOLING-1) COOLING SYSTME ALARM | SPS
118 | 20KV | STATCOM-1 | VSC-1 | (COOLING-1) COOLING SYSTME CONTROLLER-A ACTIVE | SPS
119 | 20KV | STATCOM-1 | VSC-1 | (COOLING-1) COOLING SYSTME CONTROLLER-B ACTIVE | SPS
120 | 20KV | STATCOM-1 | VSC-1 | (COOLING-1) COOLING SYSTME CONTROLLER-A FAILURE | SPS
121 | 20KV | STATCOM-1 | VSC-1 | (COOLING-1) COOLING SYSTME CONTROLLER-B FAILURE | SPS
122 | 20KV | STATCOM-1 | VSC-1 52 | TRIP CIRCUIT-1 FAULTY | SPS
123 | 20KV | STATCOM-1 | VSC-1 52 | TRIP CIRCUIT-2 FAULTY | SPS
124 | 20KV | STATCOM-1 | VSC-1 52 | PRESSURE BLOCKING ALARM | SPS
125 | 20KV | STATCOM-1 | VSC-1 52 | SF6 GAS LOW ALARM | SPS
126 | 20KV | STATCOM-1 | VSC-1 52 | POLE DISCREPANCY ALARM | SPS
127 | 20KV | STATCOM-1 | VSC-1 52 | AC FAILURE ALARM | SPS
128 | 20KV | STATCOM-1 | VSC-1 52 | INTERLOCK ENABLED | SPS
129 | 20KV | STATCOM-1 | VSC-1 -89A | INTERLOCK ENABLED | SPS
130 | 20KV | STATCOM-1 | VSC-1 -89AE | INTERLOCK ENABLED | SPS
131 | 20KV | STATCOM-1 | VSC-1 -89B | INTERLOCK ENABLED | SPS
132 | 20KV | STATCOM-1 | VSC-1 -89BE1 | INTERLOCK ENABLED | SPS
133 | 20KV | STATCOM-1 | VSC-1 -89BE2 | INTERLOCK ENABLED | SPS
134 | 20KV | STATCOM-1 | VSC-1 | (UNIT-1) VALVE OVERCURRENT TRIP | SPS
135 | 20KV | STATCOM-1 | VSC-1 | (UNIT-1) COOLING SYSTEM TRIP | SPS
136 | 20KV | STATCOM-1 | VSC-1 | GROUP MESSAGE : (UNIT-1) DC CT POWER FAIL | SPS
137 | 20KV | STATCOM-1 | VSC-1 | (UNIT-1) PHASE CONTROLLER FAILURE TRIP | SPS
138 | 20KV | STATCOM-1 | VSC-1 | GROUP MESSAGE : (UNIT-1) VALVE ERROR TRIP | SPS
139 | 20KV | STATCOM-1 | VSC-1 | (UNIT-1) SUB-MODULE FAILURE OR BYPASSED | SPS
140 | 20KV | STATCOM-1 | VSC-1 | (UNIT-1) VALVE HALL-1 TEMPERATURE HIGH TRIP | SPS
141 | 20KV | STATCOM-2 | VSC-2 | MAIN PROTECTION TRIP | SPS
142 | 20KV | STATCOM-2 | VSC-2 | MAIN LBB PROTECTION TRIP | SPS
143 | 20KV | STATCOM-2 | VSC-2 | CONTROLLER FAILURE TRIP | SPS
144 | 20KV | STATCOM-2 | VSC-2 | BACKUP PROTECTION TRIP | SPS
145 | 20KV | STATCOM-2 | VSC-2 | BACKUP LBB PROTECTION TRIP | SPS
146 | 20KV | STATCOM-2 | VSC-2 | MAIN PROTECTION RELAY FAILURE | SPS
147 | 20KV | STATCOM-2 | VSC-2 | BACKUP PROTECTION RELAY FAILURE | SPS
148 | 20KV | STATCOM-2 | VSC-2 | TRIP RELAY-A(86A) OPERATED | SPS
149 | 20KV | STATCOM-2 | VSC-2 | TRIP RELAY-B(86B) OPERATED | SPS
150 | 20KV | STATCOM-2 | VSC-2 | GROUP MESSAGE : STATCOM UNIT-2 CONTROLLER A FAILURE (COMM. FAIL / HW FAIL) | SPS
151 | 20KV | STATCOM-2 | VSC-2 | GROUP MESSAGE : STATCOM UNIT-2 CONTROLLER B FAILURE (COMM. FAIL / HW FAIL) | SPS
152 | 20KV | STATCOM-2 | VSC-2 | GROUP MESSAGE : (COOLING-2) COOLING SYSTME ALARM | SPS
153 | 20KV | STATCOM-2 | VSC-2 | (COOLING-2) COOLING SYSTME CONTROLLER-A ACTIVE | SPS
154 | 20KV | STATCOM-2 | VSC-2 | (COOLING-2) COOLING SYSTME CONTROLLER-B ACTIVE | SPS
155 | 20KV | STATCOM-2 | VSC-2 | (COOLING-2) COOLING SYSTME CONTROLLER-A FAILURE | SPS
156 | 20KV | STATCOM-2 | VSC-2 | (COOLING-2) COOLING SYSTME CONTROLLER-B FAILURE | SPS
157 | 20KV | STATCOM-2 | VSC-2 52 | TRIP CIRCUIT-1 FAULTY | SPS
158 | 20KV | STATCOM-2 | VSC-2 52 | TRIP CIRCUIT-2 FAULTY | SPS
159 | 20KV | STATCOM-2 | VSC-2 52 | PRESSURE BLOCKING ALARM | SPS
160 | 20KV | STATCOM-2 | VSC-2 52 | SF6 GAS LOW ALARM | SPS
161 | 20KV | STATCOM-2 | VSC-2 52 | POLE DISCREPANCY ALARM | SPS
162 | 20KV | STATCOM-2 | VSC-2 52 | AC FAILURE ALARM | SPS
163 | 20KV | STATCOM-2 | VSC-2 52 | INTERLOCK ENABLED | SPS
164 | 20KV | STATCOM-2 | VSC-2 -89A | INTERLOCK ENABLED | SPS
165 | 20KV | STATCOM-2 | VSC-2 -89AE | INTERLOCK ENABLED | SPS
166 | 20KV | STATCOM-2 | VSC-2 -89B | INTERLOCK ENABLED | SPS
167 | 20KV | STATCOM-2 | VSC-2 -89BE1 | INTERLOCK ENABLED | SPS
168 | 20KV | STATCOM-2 | VSC-2 -89BE2 | INTERLOCK ENABLED | SPS
169 | 20KV | STATCOM-2 | VSC-2 | (UNIT-2) VALVE OVERCURRENT TRIP | SPS
170 | 20KV | STATCOM-2 | VSC-2 | (UNIT-2) COOLING SYSTEM TRIP | SPS
171 | 20KV | STATCOM-2 | VSC-2 | GROUP MESSAGE : (UNIT-2) DC CT POWER FAIL | SPS
172 | 20KV | STATCOM-2 | VSC-2 | (UNIT-2) PHASE CONTROLLER FAILURE TRIP | SPS
173 | 20KV | STATCOM-2 | VSC-2 | GROUP MESSAGE : (UNIT-2) VALVE ERROR TRIP | SPS
174 | 20KV | STATCOM-2 | VSC-2 | (UNIT-2) SUB-MODULE FAILURE OR BYPASSED | SPS
175 | 20KV | STATCOM-2 | VSC-2 | (UNIT-2) VALVE HALL-2 TEMPERATURE HIGH TRIP | SPS
176 | 20KV | STATCOM CONTROL | STATCOM | COOLING-1 SYSTME TRIP | SPS
177 | 20KV | STATCOM CONTROL | STATCOM | COOLING-2 SYSTME TRIP | SPS
178 | 20KV | STATCOM CONTROL | STATCOM | STATCOM STATION CONTROLLER FAILURE TRIP | SPS
179 | 20KV | STATCOM CONTROL | STATCOM | STATION CONTROLLER START | SPS
180 | 20KV | STATCOM CONTROL | STATCOM | STATION CONTROLLER STOP | SPS
181 | 20KV | STATCOM CONTROL | STATCOM | STATCOM STATION RUNNING | SPS
182 | 20KV | STATCOM CONTROL | STATCOM | STATCOM STATION SEQUENCE FAIULRE | SPS
183 | 20KV | STATCOM CONTROL | STATCOM | UNIT-1 CONTROLLER START | SPS
184 | 20KV | STATCOM CONTROL | STATCOM | UNIT-1 CONTROLLER STOP | SPS
185 | 20KV | STATCOM CONTROL | STATCOM | STATCOM UNIT-1 STOPPED | SPS
186 | 20KV | STATCOM CONTROL | STATCOM | STATCOM UNIT-1 RUNNING | SPS
187 | 20KV | STATCOM CONTROL | STATCOM | STATCOM UNIT-1 SEQUENCE FAIULRE | SPS
188 | 20KV | STATCOM CONTROL | STATCOM | UNIT-2 CONTROLLER START | SPS
189 | 20KV | STATCOM CONTROL | STATCOM | UNIT-2 CONTROLLER STOP | SPS
190 | 20KV | STATCOM CONTROL | STATCOM | STATCOM UNIT-2 STOPPED | SPS
191 | 20KV | STATCOM CONTROL | STATCOM | STATCOM UNIT-2 RUNNING | SPS
192 | 20KV | STATCOM CONTROL | STATCOM | STATCOM UNIT-2 SEQUENCE FAIULRE | SPS
193 | 20KV | STATCOM CONTROL | STATCOM | AUTOMATIC START | SPS
194 | 20KV | STATCOM CONTROL | STATCOM | AUTOMATIC STOP | SPS
195 | 20KV | STATCOM CONTROL | STATCOM | AUTOMATIC START/STOP SEQUENCE RUNNING | SPS
196 | 20KV | STATCOM CONTROL | STATCOM | AUTOMATIC START/STOP SEQUENCE FAIL | SPS
197 | 20KV | STATCOM CONTROL | STATCOM | (STATION) HV SIDE OVERVOLTAGE TRIP | SPS
198 | 20KV | STATCOM CONTROL | STATCOM | (STATION) HV SIDE UNDERVOLTAGE TRIP | SPS
199 | 20KV | STATCOM CONTROL | STATCOM | (STATION) HV SIDE OVERCURRENT TRIP | SPS
200 | 20KV | STATCOM CONTROL | STATCOM | (STATION) HV PT FAIL TRIP | SPS
201 | 20KV | STATCOM CONTROL | STATCOM | EMERGENCY STOP | SPS
202 | 20KV | STATCOM CONTROL | STATCOM | GROUP MESSAGE : STATION CONTROLLER A FAILURE (COMM. FAIL / HW FAIL) | SPS
203 | 20KV | STATCOM CONTROL | STATCOM | GROUP MESSAGE : STATION CONTROLLER B FAILURE (COMM. FAIL / HW FAIL) | SPS
204 | 20KV | STATCOM CONTROL | STATCOM | MANUAL Q CONTROL MODE SELECTED | SPS
205 | 20KV | STATCOM CONTROL | STATCOM | AUTOMATIC VOLTAGE CONTROL MODE SELECTED | SPS
206 | 20KV | STATCOM CONTROL | STATCOM | POD CONTROL ENABLED | SPS
207 | 20KV | STATCOM CONTROL | STATCOM | SSOD CONTROL ENABLED | SPS
208 | 20KV | STATCOM CONTROL | STATCOM | ADAPTIVE GAIN REDUCTION ENABLED | SPS
209 | 20KV | STATCOM CONTROL | STATCOM | ADAPTIVE GAIN CLACULATION ENABLED | SPS
210 | 20KV | STATCOM CONTROL | STATCOM | NEGATIVE SEQ. VOLTAGE CONTROL ENABLED | SPS
211 | 20KV | STATCOM CONTROL | STATCOM | MSC CONTROL MODE - AUTO. CONTROL SELLECTED | SPS
212 | 20KV | STATCOM CONTROL | STATCOM | MSR-1 CONTROL MODE - AUTO. CONTROL SELLECTED | SPS
213 | 20KV | STATCOM CONTROL | STATCOM | MSR-2 CONTROL MODE - AUTO. CONTROL SELLECTED | SPS
214 | 20KV | STATCOM CONTROL | STATCOM | HV BR MAIN BAY CONTROL MODE - AUTO. CONTROL SELLECTED (HYD ONLY) | SPS
215 | 20KV | STATCOM CONTROL | STATCOM | HV BR TIE BAY CONTROL MODE - AUTO. CONTROL SELLECTED (HYD ONLY) | SPS
216 | 20KV | STATCOM CONTROL | AHU | AHU 1-1 RUNNING | SPS
217 | 20KV | STATCOM CONTROL | AHU | AHU 1-2 RUNNING | SPS
218 | 20KV | STATCOM CONTROL | AHU | AHU 2-1 RUNNING | SPS
219 | 20KV | STATCOM CONTROL | AHU | AHU 2-2 RUNNING | SPS
220 | 20KV | GND T/F | GND T/F | MV BUSBAR BACKUP PROTECTION TRIP (GND TRAFO TRIP) | SPS
221 | 20KV | GND T/F | GND T/F | BACKUP PROTECTION RELAY FAILURE (GND TRAFO) | SPS
222 | 20KV | GND T/F | GND T/F | BUCHHOLZ RELAY TRIP | SPS
223 | 20KV | GND T/F | GND T/F | PRD TRIP | SPS
224 | 20KV | GND T/F | GND T/F | WTI TRIP | SPS
225 | 20KV | GND T/F | GND T/F | OTI TRIP | SPS
226 | 20KV | GND T/F | GND T/F | BUCHHOLZ RELAY ALARM | SPS
227 | 20KV | GND T/F | GND T/F | WTI ALARM | SPS
228 | 20KV | GND T/F | GND T/F | OTI ALARM | SPS
229 | 20KV | GND T/F | 89 | INTERLOCK ENABLED | SPS
230 | 20KV | GND T/F | 89E | INTERLOCK ENABLED | SPS
231 | 20KV | MV BUS BAR | MV BUS BAR | MAIN PROTECTION TRIP | SPS
232 | 20KV | MV BUS BAR | MV BUS BAR | MAIN PROTECTION RELAY FAILURE | SPS
233 | 20KV | BUS PT | 89E1 | INTERLOCK ENABLED | SPS
234 | 20KV | BUS PT | 89 | INTERLOCK ENABLED | SPS
235 | 20KV | BUS PT | 89E2 | INTERLOCK ENABLED | SPS
236 | 20KV | AUX.T/F | MV AUX T/F | MAIN PROTECTION TRIP | SPS
237 | 20KV | AUX.T/F | MV AUX T/F | BACKUP PROTECTION TRIP | SPS
238 | 20KV | AUX.T/F | MV AUX T/F | MAIN PROTECTION RELAY FAILURE | SPS
239 | 20KV | AUX.T/F | MV AUX T/F | BACKUP PROTECTION RELAY FAILURE | SPS
240 | 20KV | AUX.T/F | MV AUX T/F | TRIP RELAY-A(86A) OPERATED | SPS
241 | 20KV | AUX.T/F | MV AUX T/F | TRIP RELAY-B(86B) OPERATED | SPS
242 | 20KV | AUX.T/F | MV AUX T/F | BUCHHOLZ RELAY TRIP | SPS
243 | 20KV | AUX.T/F | MV AUX T/F | WTI TRIP | SPS
244 | 20KV | AUX.T/F | MV AUX T/F | OTI TRIP | SPS
245 | 20KV | AUX.T/F | MV AUX T/F | BUCHHOLZ RELAY ALARM | SPS
246 | 20KV | AUX.T/F | MV AUX T/F | WTI ALARM | SPS
247 | 20KV | AUX.T/F | MV AUX T/F | OTI ALARM | SPS
248 | 20KV | AUX.T/F | 52 | TRIP CIRCUIT-1 FAULTY | SPS
249 | 20KV | AUX.T/F | 52 | TRIP CIRCUIT-2 FAULTY | SPS
250 | 20KV | AUX.T/F | 52 | PRESSURE BLOCKING ALARM | SPS
251 | 20KV | AUX.T/F | 52 | SF6 GAS LOW ALARM | SPS
252 | 20KV | AUX.T/F | 52 | POLE DISCREPANCY ALARM | SPS
253 | 20KV | AUX.T/F | 52 | AC FAILURE ALARM | SPS
254 | 20KV | AUX.T/F | 89 | INTERLOCK ENABLED | SPS
255 | 20KV | AUX.T/F | 89E | INTERLOCK ENABLED | SPS
256 | 20KV | AUX.T/F | 52 | INTERLOCK ENABLED | SPS
257 | 33KV | AUX.T/F | TERTIARY | 33kV AUX. TR PROTECTION TRIP | SPS
258 | 33KV | AUX.T/F | TERTIARY | 33kV AUX. TR TRIP RELAY OPERATED | SPS
259 | 33KV | AUX.T/F | TERTIARY | 33kV AUX. TR CB SF6 Loss Alarm | SPS
260 | 33KV | AUX.T/F | TERTIARY | 33kV AUX. TR CB SF6 Lockout Alarm | SPS
261 | 33KV | AUX.T/F | TERTIARY | 33kV AUX. TR CB Spring Charged | SPS
262 | 33KV | AUX.T/F | TERTIARY | 33kV AUX. TR CB DC 1/2 Fail Alarm | SPS
263 | 33KV | AUX.T/F | TERTIARY | 33kV AUX. TR Bucholz Alarm | SPS
264 | 33KV | AUX.T/F | TERTIARY | 33kV AUX. TR WTI Alarm | SPS
265 | 33KV | AUX.T/F | TERTIARY | 33kV AUX. TR OTI Alarm | SPS
266 | 33KV | AUX.T/F | TERTIARY 52 | INTERLOCK ENABLED | SPS
267 | 33KV | AUX.T/F | TERTIARY 89 | INTERLOCK ENABLED | SPS
268 | 415 V | FP | CONTROL ROOM | CONTROL ROOM FIRE DETECTED | SPS
269 | 415 V | FP | VALVE HALL | VALVE HALL-1 FIRE DETECTED | SPS
270 | 415 V | FP | VALVE HALL | VALVE HALL-2 FIRE DETECTED | SPS
271 | 415 V | FP | CONTROL ROOM | GROUP MESSAGE : CONTROL BUILDING FIRE DETECTED | SPS
272 | 415 V | FP | COUPLING T/F | GROUP MESSAGE : COUPLING TRANSFORMER FIRE DETECTED | SPS
273 | 415 V | DCDB | DCDB-1 | GROUP MESSAGE : 220V DC SOURCE-1 FAILURE | SPS
274 | 415 V | DCDB | DCDB-2 | GROUP MESSAGE : 220V DC SOURCE-2 FAILURE | SPS
275 | 415 V | DCDB | DCDB-1 | EARTH FAULT | SPS
276 | 415 V | DCDB | DCDB-1 | BATTERY CHARGER TROUBLE | SPS
277 | 415 V | DCDB | DCDB-2 | EARTH FAULT | SPS
278 | 415 V | DCDB | DCDB-2 | BATTERY CHARGER TROUBLE | SPS
279 | 415 V | GPS | GPS | GROUP MESSAGE : TIME SYNC. FAIL | SPS
280 | 415 V | DG SET | AMF PANEL | DG SET ON | SPS
281 | 415 V | DG SET | AMF PANEL | DG SET OFF | SPS
282 | 415 V | DG SET | AMF PANEL | DG SET LOW OIL PRESSURE | SPS
283 | 415 V | DG SET | AMF PANEL | DG SET LOW FUEL | SPS
284 | 415 V | DG SET | AMF PANEL | DG SET FAILED TO START IN 30 SEC | SPS
285 | 415 V | DG SET | AMF PANEL | DG SET HIGH COOLING WATER TEMPERATURE | SPS
286 | 415 V | DG SET | AMF PANEL | DG SET LOW LEVEL IN DAILY SERVICE FUEL TANK | SPS
287 | 415 V | DG SET | AMF PANEL | OVER SPEED TRIP | SPS
288 | 415 V | DG SET | AMF PANEL | ALTERNATOR FAULT | SPS
289 | 415 V | DG SET | AMF PANEL | ALTERNATOR ON | SPS
290 | 415 V | COOLING UPS | UPS-1 | BYPASS FAILURE / AC SUPPLY FAILURE | SPS
291 | 415 V | COOLING UPS | UPS-1 | LOW BATTERY | SPS
292 | 415 V | COOLING UPS | UPS-1 | LOAD ON MAINS | SPS
293 | 415 V | COOLING UPS | UPS-1 | LOAD ON MAINTENANCE/BYPASS-MODE | SPS
294 | 415 V | COOLING UPS | UPS-1 | LOAD ON INVERTER | SPS
295 | 415 V | COOLING UPS | UPS-2 | BYPASS FAILURE / AC SUPPLY FAILURE | SPS
296 | 415 V | COOLING UPS | UPS-2 | LOW BATTERY | SPS
297 | 415 V | COOLING UPS | UPS-2 | LOAD ON MAINS | SPS
298 | 415 V | COOLING UPS | UPS-2 | LOAD ON MAINTENANCE/BYPASS-MODE | SPS
299 | 415 V | COOLING UPS | UPS-2 | LOAD ON INVERTER | SPS
300 | 415 V | AUX | AIRCON | VALVE HALL-1 TEMPERATURE HIGH ALARM | SPS
301 | 415 V | AUX | AIRCON | VALVE HALL-2 TEMPERATURE HIGH ALARM | SPS
302 | 415 V | AUX | AIRCON | CONTROL ROOM TEMPERATURE HIGH ALARM | SPS
303 | 415 V | SAS | STATION LOCAL/REMOTE | LOCAL HMI CONTROL SELECTED (HYDERBAD S/S) | SPS
304 | 415 V | SAS | STATION LOCAL/REMOTE | REMOTE CENTER CONTROL SELECTED (NTAMC/RTAMC/B-NTAMC) | SPS
305 | 20KV | MSR-1 | MSR | MSR-1 MAIN PROTECTION TRIP | SPS
306 | 20KV | MSR-1 | MSR | MSR-1 MAIN LBB PROTECTION TRIP | SPS
307 | 20KV | MSR-1 | MSR | MSR-1 BACKUP PROTECTION TRIP | SPS
308 | 20KV | MSR-1 | MSR | MSR-1 BACKUP LBB PROTECTION TRIP | SPS
309 | 20KV | MSR-1 | MSR | MSR-1 MAIN PROTECTION RELAY FAILURE | SPS
310 | 20KV | MSR-1 | MSR | MSR-1 BACKUP PROTECTION RELAY FAILURE | SPS
311 | 20KV | MSR-1 | MSR | MSR-1 TRIP RELAY-A(86A) OPERATED | SPS
312 | 20KV | MSR-1 | MSR | MSR-1 TRIP RELAY-B(86B) OPERATED | SPS
313 | 20KV | MSR-1 | 89A | INTERLOCK ENABLED | SPS
314 | 20KV | MSR-1 | 89AE | INTERLOCK ENABLED | SPS
315 | 20KV | MSR-1 | 52 | INTERLOCK ENABLED | SPS
316 | 20KV | MSR-1 | 89B | INTERLOCK ENABLED | SPS
317 | 20KV | MSR-1 | 89BE1 | INTERLOCK ENABLED | SPS
318 | 20KV | MSR-1 | 89BE2 | INTERLOCK ENABLED | SPS
319 | 20KV | MSR-1 | 52 | TRIP CIRCUIT-1 FAULTY | SPS
320 | 20KV | MSR-1 | 52 | TRIP CIRCUIT-2 FAULTY | SPS
321 | 20KV | MSR-1 | 52 | PRESSURE BLOCKING ALARM | SPS
322 | 20KV | MSR-1 | 52 | SF6 GAS LOW ALARM | SPS
323 | 20KV | MSR-1 | 52 | POLE DISCREPANCY ALARM | SPS
324 | 20KV | MSR-1 | 52 | AC FAILURE ALARM | SPS
325 | 20KV | MSR-2 | MSR | MSR-2 MAIN PROTECTION TRIP | SPS
326 | 20KV | MSR-2 | MSR | MSR-2 MAIN LBB PROTECTION TRIP | SPS
327 | 20KV | MSR-2 | MSR | MSR-2 BACKUP PROTECTION TRIP | SPS
328 | 20KV | MSR-2 | MSR | MSR-2 BACKUP LBB PROTECTION TRIP | SPS
329 | 20KV | MSR-2 | MSR | MSR-2 MAIN PROTECTION RELAY FAILURE | SPS
330 | 20KV | MSR-2 | MSR | MSR-2 BACKUP PROTECTION RELAY FAILURE | SPS
331 | 20KV | MSR-2 | MSR | MSR-2 TRIP RELAY-A(86A) OPERATED | SPS
332 | 20KV | MSR-2 | MSR | MSR-2 TRIP RELAY-B(86B) OPERATED | SPS
333 | 20KV | MSR-2 | 89A | INTERLOCK ENABLED | SPS
334 | 20KV | MSR-2 | 89AE | INTERLOCK ENABLED | SPS
335 | 20KV | MSR-2 | 52 | INTERLOCK ENABLED | SPS
336 | 20KV | MSR-2 | 89B | INTERLOCK ENABLED | SPS
337 | 20KV | MSR-2 | 89BE1 | INTERLOCK ENABLED | SPS
338 | 20KV | MSR-2 | 89BE2 | INTERLOCK ENABLED | SPS
339 | 20KV | MSR-2 | 52 | TRIP CIRCUIT-1 FAULTY | SPS
340 | 20KV | MSR-2 | 52 | TRIP CIRCUIT-2 FAULTY | SPS
341 | 20KV | MSR-2 | 52 | PRESSURE BLOCKING ALARM | SPS
342 | 20KV | MSR-2 | 52 | SF6 GAS LOW ALARM | SPS
343 | 20KV | MSR-2 | 52 | POLE DISCREPANCY ALARM | SPS
344 | 20KV | MSR-2 | 52 | AC FAILURE ALARM | SPS
345 | 20KV | MSC | MSC | MSC MAIN PROTECTION TRIP | SPS
346 | 20KV | MSC | MSC | MSC MAIN LBB PROTECTION TRIP | SPS
347 | 20KV | MSC | MSC | MSC BACKUP PROTECTION TRIP | SPS
348 | 20KV | MSC | MSC | MSC BACKUP LBB PROTECTION TRIP | SPS
349 | 20KV | MSC | MSC | MSC MAIN PROTECTION RELAY FAILURE | SPS
350 | 20KV | MSC | MSC | MSC BACKUP PROTECTION RELAY FAILURE | SPS
351 | 20KV | MSC | MSC | MSC TRIP RELAY-A(86A) OPERATED | SPS
352 | 20KV | MSC | MSC | MSC TRIP RELAY-B(86B) OPERATED | SPS
353 | 20KV | MSC | 89A | INTERLOCK ENABLED | SPS
354 | 20KV | MSC | 89AE | INTERLOCK ENABLED | SPS
355 | 20KV | MSC | 52 | INTERLOCK ENABLED | SPS
356 | 20KV | MSC | 89B | INTERLOCK ENABLED | SPS
357 | 20KV | MSC | 89BE1 | INTERLOCK ENABLED | SPS
358 | 20KV | MSC | 89BE2 | INTERLOCK ENABLED | SPS
359 | 20KV | MSC | 52 | TRIP CIRCUIT-1 FAULTY | SPS
360 | 20KV | MSC | 52 | TRIP CIRCUIT-2 FAULTY | SPS
361 | 20KV | MSC | 52 | PRESSURE BLOCKING ALARM | SPS
362 | 20KV | MSC | 52 | SF6 GAS LOW ALARM | SPS
363 | 20KV | MSC | 52 | POLE DISCREPANCY ALARM | SPS
364 | 20KV | MSC | 52 | AC FAILURE ALARM | SPS
365 | 400KV | FUTURE | 89A | INTERLOCK ENABLED | SPS
366 | 400KV | FUTURE | 89AE | INTERLOCK ENABLED | SPS
367 | 400KV | FUTURE & STATCOM TIE |  | 400KV TIE BAY LBB PROTECTION TRIP | SPS
368 | 400KV | FUTURE & STATCOM TIE |  | 400kV TIE BAY LBB RELAY FAILURE | SPS
369 | 400KV | FUTURE & STATCOM TIE |  | 400kV TIE BAY BCU FAILURE | SPS
370 | 400KV | FUTURE & STATCOM TIE |  | 400kV TIE BAY 86.1 TRIP RELAY OPERATED | SPS
371 | 400KV | FUTURE & STATCOM TIE |  | 400kV TIE BAY 86.2 TRIP RELAY OPERATED | SPS
372 | 400KV | FUTURE & STATCOM TIE |  | CT SF6 Loss Alarm | SPS
373 | 400KV | FUTURE & STATCOM TIE |  | CT SF6 Lockout Alarm | SPS
374 | 400KV | FUTURE & STATCOM TIE | 52 | CB SF6 Loss Alarm | SPS
375 | 400KV | FUTURE & STATCOM TIE | 52 | CB SF6 Lockout Alarm 1/2 | SPS
376 | 400KV | FUTURE & STATCOM TIE | 52 | CB DC-1/2 Fail | SPS
377 | 400KV | FUTURE & STATCOM TIE | 52 | CB Pole Descripency Alarm | SPS
378 | 400KV | FUTURE & STATCOM TIE | 52 | CB TC-1 Faulty | SPS
379 | 400KV | FUTURE & STATCOM TIE | 52 | CB TC-2 Faulty | SPS
380 | 400KV | FUTURE & STATCOM TIE | 52 | CB Spring Charged | SPS
381 | 400KV | FUTURE & STATCOM TIE | 52 | CSD Alarm | SPS
382 | 400KV | FUTURE & STATCOM TIE | 52 | CSD out of service | SPS

## AI (hidden)
Sl. | BAY NUM. | BAY NAME | DEVICE ID | SIGNAL DESCRIPTION | DATA TYPE | SCADA ID | REMARK
765 KV/ 400 KV/ 220 KV/ 132 KV BUS BAR ( MAIN BUS & TRANSFER BUS)
1 | BUS | BUS-X | BUS | VOLTAGE R-Y PHASE | AI | KVRY
2 | BUS | BUS-X | BUS | VOLTAGE Y-B PHASE | AI | KVYB
3 | BUS | BUS-X | BUS | VOLTAGE B-R PHASE | AI | KVBR
4 | BUS | BUS-X | BUS | FREQUENCY | AI | HZ
765 KV/ 400 KV/ 220 KV /132 KV LINE FEEDER / LINE SERIES REACTOR/ BUS SERIES REACTOR (LSR/BSR)
1 | ABC | LINE FEEDER | LINE / LSR / BSR | I (R-PHASE) | AI | IR
2 | ABC | LINE FEEDER | LINE / LSR / BSR | I (Y-PHASE) | AI | IY
3 | ABC | LINE FEEDER | LINE / LSR / BSR | I (B-PHASE) | AI | IB
4 | ABC | LINE FEEDER | LINE / LSR / BSR | MW | AI | MW
5 | ABC | LINE FEEDER | LINE / LSR / BSR | MVAR | AI | MX
6 | ABC | LINE FEEDER | LINE / LSR / BSR | V (R-Y PHASE) | AI | KVRY
7 | ABC | LINE FEEDER | LINE / LSR / BSR | V (Y-B PHASE) | AI | KVYB
8 | ABC | LINE FEEDER | LINE / LSR / BSR | V (B-R PHASE) | AI | KVBR
9 | ABC | LINE FEEDER | LINE / LSR / BSR | FREQUENCY | AI | HZ
10 | ABC | LINE FEEDER | LINE | MAIN-1 FAULT IMPEDANCE | AI | FLZ1
11 | ABC | LINE FEEDER | LINE | MAIN-1 FAULT DISTANCE | AI | FLD1
12 | ABC | LINE FEEDER | LINE | MAIN-1 FAULT PERCENTAGE | AI | FLP1
13 | ABC | LINE FEEDER | LINE | MAIN-2 FAULT IMPEDANCE | AI | FLZ2
14 | ABC | LINE FEEDER | LINE | MAIN-2 FAULT DISTANCE | AI | FLD2
15 | ABC | LINE FEEDER | LINE | MAIN-2 FAULT PERCENTAGE | AI | FLP2
765 KV/ 400 KV LINE REACTOR/ BUS REACTOR
1 | ABC | BUS REACTOR/ LINE REACTOR | RE | REACTOR I (R-PHASE) | AI | IR
2 | ABC | BUS REACTOR/ LINE REACTOR | RE | REACTOR I (Y-PHASE) | AI | IY
3 | ABC | BUS REACTOR/ LINE REACTOR | RE | REACTOR I (B-PHASE) | AI | IB
4 | ABC | BUS REACTOR/ LINE REACTOR | RE | REACTOR MVAR | AI | MX
5 | ABC | BUS REACTOR/ LINE REACTOR | RE | REACTOR V (R-Y PHASE) | AI | KVRY
6 | ABC | BUS REACTOR/ LINE REACTOR | RE | REACTOR V (Y-B PHASE) | AI | KVYB
7 | ABC | BUS REACTOR/ LINE REACTOR | RE | REACTOR V (B-R PHASE) | AI | KVBR
8 | ABC | BUS REACTOR/ LINE REACTOR | RE | FREQUENCY | AI | HZ
9 | ABC | BUS REACTOR/ LINE REACTOR | RE | WTI TEMP R PHASE | AI | WTI | ONLY ONE SIGNAL IN PLACE OF THREE SIGNALS APPLICABLE INDIVIDUALLY FOR R/Y/B PHASES TO BE CONSIDERED FOR 3 PHASE LINE REACTOR/ BUS REACTOR
10 | ABC | BUS REACTOR/ LINE REACTOR | RE | WTI TEMP Y PHASE | AI | WTI
11 | ABC | BUS REACTOR/ LINE REACTOR | RE | WTI TEMP B PHASE | AI | WTI
12 | ABC | BUS REACTOR/ LINE REACTOR | RE | OTI TEMP R PHASE | AI | OTI
13 | ABC | BUS REACTOR/ LINE REACTOR | RE | OTI TEMP Y PHASE | AI | OTI
14 | ABC | BUS REACTOR/ LINE REACTOR | RE | OTI TEMP B PHASE | AI | OTI
15 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA MOISTURE VALUE - R PHASE | AI | MOIS
16 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA H2 VALUE - R PHASE | AI | DGH2
17 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H2 VALUE - R PHASE | AI | C2H2
18 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CO VALUE - R PHASE | AI | DGCO
19 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CO2 VALUE - R PHASE | AI | DCO2
20 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CH4 VALUE - R PHASE | AI | DCH4
21 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H6 VALUE - R PHASE | AI | C2H6
22 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H4 VALUE - R PHASE | AI | C2H4
23 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA O2 VALUE - R PHASE | AI | DGO2
24 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA MOISTURE VALUE - Y PHASE | AI | MOIS
25 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA H2 VALUE - Y PHASE | AI | DGH2
26 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H2 VALUE - Y PHASE | AI | C2H2
27 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CO VALUE - Y PHASE | AI | DGCO
28 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CO2 VALUE - Y PHASE | AI | DCO2
29 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CH4 VALUE - Y PHASE | AI | DCH4
30 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H6 VALUE - Y PHASE | AI | C2H6
31 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H4 VALUE - Y PHASE | AI | C2H4
32 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA O2 VALUE - Y PHASE | AI | DGO2
33 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA MOISTURE VALUE - B PHASE | AI | MOIS
34 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA H2 VALUE - B PHASE | AI | DGH2
35 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H2 VALUE - B PHASE | AI | C2H2
36 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CO VALUE - B PHASE | AI | DGCO
37 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CO2 VALUE - B PHASE | AI | DCO2
38 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CH4 VALUE - B PHASE | AI | DCH4
39 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H6 VALUE - B PHASE | AI | C2H6
40 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H4 VALUE - B PHASE | AI | C2H4
41 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA O2 VALUE - B PHASE | AI | DGO2
765 KV SPARE LINE REACTOR/ BUS REACTOR
1 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | WTI TEMP SPARE | AI | WTI
2 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | OTI TEMP SPARE | AI | OTI
3 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA MOISTURE VALUE | AI | MOIS
4 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA H2 VALUE | AI | DGH2
5 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA C2H2 VALUE | AI | C2H2
6 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA CO VALUE | AI | DGCO
7 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA CO2 VALUE | AI | DCO2
8 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA CH4 VALUE | AI | DCH4
9 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA C2H6 VALUE | AI | C2H6
10 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA C2H4 VALUE | AI | C2H4
11 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA O2 VALUE | AI | DGO2
765 KV/ 400 KV/ 220KV /132 KV TIE BAY / BUS COUPLER / BUS SECTION / TBC
1 | ABC | TIE/ BUS COUPLER / BUS SECTION | TIE/ BC/ BS | I (R-PHASE) | AI | IR
2 | ABC | TIE/ BUS COUPLER / BUS SECTION | TIE/ BC/ BS | I (Y-PHASE) | AI | IY
3 | ABC | TIE/ BUS COUPLER / BUS SECTION | TIE/ BC/ BS | I (B-PHASE) | AI | IB
ICT
1 | ABC | ICT | XFMR_P | I (R-PHASE) | AI | IR
2 | ABC | ICT | XFMR_P | I (Y-PHASE) | AI | IY
3 | ABC | ICT | XFMR_P | I (B-PHASE) | AI | IB
4 | ABC | ICT | XFMR_P | MW | AI | MW
5 | ABC | ICT | XFMR_P | MVAR | AI | MX
6 | ABC | ICT | XFMR_P | V (R-Y PHASE) | AI | KVRY
7 | ABC | ICT | XFMR_P | V (Y-B PHASE) | AI | KVYB
8 | ABC | ICT | XFMR_P | V (B-R PHASE) | AI | KVBR
9 | ABC | ICT | XFMR_P | FREQUENCY | AI | HZ
10 | ABC | ICT | XFMR_P | HVWTI TEMP - R PHASE | AI | HVWT | ONLY ONE SIGNAL IN PLACE OF THREE SIGNALS APPLICABLE INDIVIDUALLY FOR R/Y/B PHASES TO BE CONSIDERED IN CASE OF 3-PHASE ICT
11 | ABC | ICT | XFMR_S | IVWTI TEMP - R PHASE | AI | IVWT
12 | ABC | ICT | XFMR_T | LVWTI TEMP - R PHASE | AI | LVWT
13 | ABC | ICT | XFMR_P | HVWTI TEMP - Y PHASE | AI | HVWT
14 | ABC | ICT | XFMR_S | IVWTI TEMP - Y PHASE | AI | IVWT
15 | ABC | ICT | XFMR_T | LVWTI TEMP - Y PHASE | AI | LVWT
16 | ABC | ICT | XFMR_P | HVWTI TEMP - B PHASE | AI | HVWT
17 | ABC | ICT | XFMR_S | IVWTI TEMP - B PHASE | AI | IVWT
18 | ABC | ICT | XFMR_T | LVWTI TEMP - B PHASE | AI | LVWT
19 | ABC | ICT | XFMR_P | OTI TEMP R PHASE | AI | OTI
20 | ABC | ICT | XFMR_P | OTI TEMP Y PHASE | AI | OTI
21 | ABC | ICT | XFMR_P | OTI TEMP B PHASE | AI | OTI
22 | ABC | ICT | XFMR_P | TAP POSITION INDICATOR - R PHASE | AI | TPI
23 | ABC | ICT | XFMR_P | TAP POSITION INDICATOR - Y PHASE | AI | TPI
24 | ABC | ICT | XFMR_P | TAP POSITION INDICATOR - B PHASE | AI | TPI
25 | ABC | ICT | XFMR_P | DGA MOISTURE VALUE - R PHASE | AI | MOIS
26 | ABC | ICT | XFMR_P | DGA H2 VALUE - R PHASE | AI | DGH2
27 | ABC | ICT | XFMR_P | DGA C2H2 VALUE - R PHASE | AI | C2H2
28 | ABC | ICT | XFMR_P | DGA CO VALUE - R PHASE | AI | DGCO
29 | ABC | ICT | XFMR_P | DGA CO2 VALUE - R PHASE | AI | DCO2
30 | ABC | ICT | XFMR_P | DGA CH4 VALUE - R PHASE | AI | DCH4
31 | ABC | ICT | XFMR_P | DGA C2H6 VALUE - R PHASE | AI | C2H6
32 | ABC | ICT | XFMR_P | DGA C2H4 VALUE - R PHASE | AI | C2H4
33 | ABC | ICT | XFMR_P | DGA O2 VALUE - R PHASE | AI | DGO2
34 | ABC | ICT | XFMR_P | DGA MOISTURE VALUE - Y PHASE | AI | MOIS
35 | ABC | ICT | XFMR_P | DGA H2 VALUE - Y PHASE | AI | DGH2
36 | ABC | ICT | XFMR_P | DGA C2H2 VALUE - Y PHASE | AI | C2H2
37 | ABC | ICT | XFMR_P | DGA CO VALUE - Y PHASE | AI | DGCO
38 | ABC | ICT | XFMR_P | DGA CO2 VALUE - Y PHASE | AI | DCO2
39 | ABC | ICT | XFMR_P | DGA CH4 VALUE - Y PHASE | AI | DCH4
40 | ABC | ICT | XFMR_P | DGA C2H6 VALUE - Y PHASE | AI | C2H6
41 | ABC | ICT | XFMR_P | DGA C2H4 VALUE - Y PHASE | AI | C2H4
42 | ABC | ICT | XFMR_P | DGA O2 VALUE - Y PHASE | AI | DGO2
43 | ABC | ICT | XFMR_P | DGA MOISTURE VALUE - B PHASE | AI | MOIS
44 | ABC | ICT | XFMR_P | DGA H2 VALUE - B PHASE | AI | DGH2
45 | ABC | ICT | XFMR_P | DGA C2H2 VALUE - B PHASE | AI | C2H2
46 | ABC | ICT | XFMR_P | DGA CO VALUE - B PHASE | AI | DGCO
47 | ABC | ICT | XFMR_P | DGA CO2 VALUE - B PHASE | AI | DCO2
48 | ABC | ICT | XFMR_P | DGA CH4 VALUE - B PHASE | AI | DCH4
49 | ABC | ICT | XFMR_P | DGA C2H6 VALUE - B PHASE | AI | C2H6
50 | ABC | ICT | XFMR_P | DGA C2H4 VALUE - B PHASE | AI | C2H4
51 | ABC | ICT | XFMR_P | DGA O2 VALUE - B PHASE | AI | DGO2
765 KV SPARE ICT
1 | SPARE | SPARE ICT | XFMR_P | HVWTI - TEMP SPARE | AI | HVWT
2 | SPARE | SPARE ICT | XFMR_S | IVWTI - TEMP SPARE | AI | IVWT
3 | SPARE | SPARE ICT | XFMR_T | LVWTI - TEMP SPARE | AI | LVWT
4 | SPARE | SPARE ICT | XFMR_P | OTI TEMP SPARE | AI | OTI
5 | SPARE | SPARE ICT | XFMR_P | TAP POSITION INDICATOR | AI | TPI
6 | SPARE | SPARE ICT | XFMR_P | DGA MOISTURE VALUE | AI | MOIS
7 | SPARE | SPARE ICT | XFMR_P | DGA H2 VALUE | AI | DGH2
8 | SPARE | SPARE ICT | XFMR_P | DGA C2H2 VALUE | AI | C2H2
9 | SPARE | SPARE ICT | XFMR_P | DGA CO VALUE | AI | DGCO
10 | SPARE | SPARE ICT | XFMR_P | DGA CO2 VALUE | AI | DCO2
11 | SPARE | SPARE ICT | XFMR_P | DGA CH4 VALUE | AI | DCH4
12 | SPARE | SPARE ICT | XFMR_P | DGA C2H6 VALUE | AI | C2H6
13 | SPARE | SPARE ICT | XFMR_P | DGA C2H4 VALUE | AI | C2H4
14 | SPARE | SPARE ICT | XFMR_P | DGA O2 VALUE | AI | DGO2
FIXED SERIES CAPACITOR (FSC)
1 | ABC | FSC | FSC-X | MOV TEMPERATURE R PHASE | AI
2 | ABC | FSC | FSC-X | MOV TEMPERATURE Y PHASE | AI
3 | ABC | FSC | FSC-X | MOV TEMPERATURE B PHASE | AI
4 | ABC | FSC | FSC-X | CAPACITOR R PHASE CURRENT | AI
5 | ABC | FSC | FSC-X | CAPACITOR Y PHASE CURRENT | AI
6 | ABC | FSC | FSC-X | CAPACITOR B PHASE CURRENT | AI
7 | ABC | FSC | FSC-X | CAPACITOR R PHASE UNBALANCED CURRENT | AI
8 | ABC | FSC | FSC-X | CAPACITOR Y PHASE UNBALANCED CURRENT | AI
9 | ABC | FSC | FSC-X | CAPACITOR B PHASE UNBALANCED CURRENT | AI
10 | ABC | FSC | FSC-X | LINE CT CURRENT R-PH | AI
11 | ABC | FSC | FSC-X | LINE CT CURRENT Y-PH | AI
12 | ABC | FSC | FSC-X | LINE CT CURRENT B-PH | AI
13 | ABC | FSC | FSC-X | KIOSK TEMP | AI
AUXILLIARY SYSTEM
1 | 220VDC | DCDB | 220V_DCDB-1 | 220V DCDB -1 VOLTAGE | AI
2 | 220VDC | DCDB | 220V_DCDB-1 | 220V BATTERY SET-1 CURRENT | AI
3 | 220VDC | DCDB | 220V_DCDB-2 | 220V DCDB -2 VOLTAGE | AI
4 | 220VDC | DCDB | 220V_DCDB-2 | 220V BATTERY SET-2 CURRENT | AI
5 | 48 VDC | DCDB | 48V_DCDB-1 | 48V DCDB -1 VOLTAGE | AI
6 | 48 VDC | DCDB | 48V_DCDB-1 | 48V BATTERY SET-1 CURRENT | AI
7 | 48 VDC | DCDB | 48V_DCDB-2 | 48V DCDB -2 VOLTAGE | AI
8 | 48 VDC | DCDB | 48V_DCDB-2 | 48V BATTERY SET-2 CURRENT | AI
9 | 220VDC | BCHRG | BATCHRG220V-1 | 220V BATTERY CHARGER-1 CURRENT | AI
10 | 220VDC | BCHRG | BATCHRG220V-2 | 220V BATTERY CHARGER-2 CURRENT | AI
11 | 48 VDC | BCHRG | BATCHRG48V-1 | 48V BATTERY CHARGER-1 CURRENT | AI
12 | 48 VDC | BCHRG | BATCHRG48V-2 | 48V BATTERY CHARGER-2 CURRENT | AI
13 | 415 V | FP | FIREPROTN | FIRE FIGHTING PRESSURE MONITORING | AI
14 | 415 V | FP | DPUMP | DIESEL ENGINE BATTERY-1 VOLTAGE | AI
15 | 415 V | FP | DPUMP | DIESEL ENGINE BATTERY-2 VOLTAGE | AI
16 | 415 V | FP | ICT | FF NIS Nitrogen Cylinder Pressure | AI
17 |  |  |  | WIND SPEED | AI
18 |  |  |  | WIND DIRECTION | AI
19 | 415 V | AIRCON | G_KIOSK_1 | 765KV KIOSK-1 TEMP | AI
20 | 415 V | AIRCON | F_KIOSK_1 | 400KV KIOSK-1 TEMP | AI
21 | 415 V | AIRCON | TEMP_MON | CONTROL ROOM TEMPRATURE | AI
22 | 415 V | AIRCON | TEMP_MON | BATTERY ROOM TEMPRATURE | AI
23 | 415 V | AIRCON | TEMP_MON | AMBIENT TEMPERATURE OUTDOOR | AI
24 | 415 V | AIRCON | TEMP_MON | AMBIENT RELATIVE HUMIDITY OUTDOOR | AI
25 | 415 V | DG Set | DGSET-1 | VOLTAGE (R-Y PHASE) | AI
26 | 415 V | DG Set | DGSET-1 | VOLTAGE (Y-B PHASE) | AI
27 | 415 V | DG Set | DGSET-1 | VOLTAGE (B-R PHASE) | AI
28 | 415 V | DG Set | DGSET-1 | CURRENT (R-PHASE) | AI
29 | 415 V | DG Set | DGSET-1 | CURRENT (Y-PHASE) | AI
30 | 415 V | DG Set | DGSET-1 | CURRENT (B-PHASE) | AI
31 | 415 V | DG Set | DGSET-1 | DG SET BATTERY-1 VOLTAGE | AI
32 | 415 V | DG Set | DGSET-1 | DG SET BATTERY-2 VOLTAGE | AI
33 | 415 V | LTSUP | MSB-1 | VOLTAGE (R-Y PHASE) | AI
34 | 415 V | LTSUP | MSB-1 | VOLTAGE (Y-B PHASE) | AI
35 | 415 V | LTSUP | MSB-1 | VOLTAGE (B-R PHASE) | AI
36 | 415 V | LTSUP | MSB-1 | CURRENT (R-PHASE) | AI
37 | 415 V | LTSUP | MSB-1 | CURRENT (Y-PHASE) | AI
38 | 415 V | LTSUP | MSB-1 | CURRENT (B-PHASE) | AI
39 | 415 V | LTSUP | MSB-2 | VOLTAGE (R-Y PHASE) | AI
40 | 415 V | LTSUP | MSB-2 | VOLTAGE (Y-B PHASE) | AI
41 | 415 V | LTSUP | MSB-2 | VOLTAGE (B-R PHASE) | AI
42 | 415 V | LTSUP | MSB-2 | CURRENT (R-PHASE) | AI
43 | 415 V | LTSUP | MSB-2 | CURRENT (Y-PHASE) | AI
44 | 415 V | LTSUP | MSB-2 | CURRENT (B-PHASE) | AI
STATCOM (SIEMENS)
1 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY | HV Main Bay Voltage R-Y | AI
2 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY | HV Main Bay Voltage Y-B | AI
3 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY | HV Main Bay Voltage B-R | AI
4 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY | HV Main Bay Current_Phase R | AI
5 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY | HV Main Bay Current_Phase Y | AI
6 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY | HV Main Bay Current_Phase B | AI
7 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER | COUPLING TRANSFORMER MVAR HV SIDE | AI
8 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA CARBON DIOXIDE | AI
9 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA ETHYLENE | AI
10 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA ACETYLENE | AI
11 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA ETHANE | AI
12 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA HYDROGEN | AI
13 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA OXYGEN | AI
14 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA METHANE | AI
15 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA CARBON MONOXIDE | AI
16 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA NITROGEN | AI
17 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA WATER | AI
18 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA COMBUSTIBLE GASSES | AI
19 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA CARBON DIOXIDE | AI
20 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA ETHYLENE | AI
21 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA ACETYLENE | AI
22 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA ETHANE | AI
23 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA HYDROGEN | AI
24 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA OXYGEN | AI
25 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA METHANE | AI
26 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA CARBON MONOXIDE | AI
27 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA NITROGEN | AI
28 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA WATER | AI
29 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA COMBUSTIBLE GASSES | AI
30 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA CARBON DIOXIDE | AI
31 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA ETHYLENE | AI
32 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA ACETYLENE | AI
33 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA ETHANE | AI
34 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA HYDROGEN | AI
35 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA OXYGEN | AI
36 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA METHANE | AI
37 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA CARBON MONOXIDE | AI
38 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA NITROGEN | AI
39 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA WATER | AI
40 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA COMBUSTIBLE GASSES | AI
41 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA CARBON DIOXIDE | AI
42 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA ETHYLENE | AI
43 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA ACETYLENE | AI
44 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA ETHANE | AI
45 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA HYDROGEN | AI
46 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA OXYGEN | AI
47 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA METHANE | AI
48 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA CARBON MONOXIDE | AI
49 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA NITROGEN | AI
50 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA WATER | AI
51 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA COMBUSTIBLE GASSES | AI
52 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY | HV Tie Bay Current_Phase R | AI
53 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY | HV Tie Bay Current_Phase Y | AI
54 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY | HV Tie Bay Current_Phase B | AI
55 | STATCOM | STATCOM | MV BUS BAR | MV BUS VOLTAGE | AI
56 | J11 | STATCOM VSC-1 BAY | VSC-1 MV-J11 | STATCOM 1 MVAR | AI
57 | J12 | STATCOM VSC-2 BAY | VSC-2 MV-J12 | STATCOM 2 MVAR | AI
58 | J21 | STATCOM MSR-1 BAY | MSR-1 MV-J21 | MSR 1 MVAR | AI
59 | J22 | STATCOM MSR-2 BAY | MSR-2 MV-J22 | MSR 2 MVAR | AI
60 | J31 | STATCOM MSC-1 BAY | MSC-1 MV-J31 | MSC 1 MVAR | AI
61 | J32 | STATCOM MSC-2 BAY | MSC-2 MV-J32 | MSC 2 MVAR | AI
62 | STATCOM | STATCOM | STATCOM OPERATION | SLOPE | AI
63 | STATCOM | STATCOM | STATCOM OPERATION | UP-SET U-REF(PU) | AI
64 | STATCOM | STATCOM | STATCOM OPERATION | DN-SET U-REF(PU) | AI
65 | STATCOM | STATCOM | STATCOM OPERATION | Q-SET REF(PU) | AI
66 | STATCOM | STATCOM | STATCOM OPERATION | LOAD FACTOR SETPOINT | AI
67 | STATCOM | STATCOM | STATCOM OPERATION | FIXED REACTIVE POWER SETPOINT(FS REF) | AI
68 | STATCOM | STATCOM | STATCOM OPERATION | NPS DEADBAND SETPOINT | AI
69 | STATCOM | STATCOM | STATCOM OPERATION | VQ MIN SETPOINT | AI
70 | STATCOM | STATCOM | STATCOM OPERATION | VQ MAX SETPOINT | AI
71 | STATCOM | STATCOM | STATCOM OPERATION | GAIN FACTOR SETPOINT | AI
72 | STATCOM | STATCOM | STATCOM OPERATION | INDUCTIVE VOLTAGE SETPOINT | AI
73 | STATCOM | STATCOM | STATCOM OPERATION | CAPACITIVE VOLTAGE SETPOINT | AI
74 | STATCOM | STATCOM | STATCOM OPERATION | LOAD FACTOR SETPOINT | AI
75 | STATCOM | STATCOM | STATCOM OPERATION | FIXED REACTIVE POWER SETPOINT(FS REF) | AI
76 | STATCOM | STATCOM | STATCOM OPERATION | REACTIVE POWER SETPOINT (QREF) | AI
77 | STATCOM | STATCOM | STATCOM OPERATION | NPS DEADBAND SETPOINT | AI
78 | STATCOM | STATCOM | STATCOM OPERATION | VQ MIN SETPOINT | AI
79 | STATCOM | STATCOM | STATCOM OPERATION | VQ MAX SETPOINT | AI
80 | STATCOM | STATCOM | STATCOM OPERATION | SLOPE SETPOINT | AI
81 | STATCOM | STATCOM | STATCOM OPERATION | GAIN FACTOR SETPOINT | AI
478 | STATCOM | STATCOM | STATCOM OPERATION | INDUCTIVE VOLTAGE SETPOINT | APC
479 | STATCOM | STATCOM | STATCOM OPERATION | CAPACITIVE VOLTAGE SETPOINT | APC
480 | STATCOM | STATCOM | STATCOM OPERATION | LOAD FACTOR SETPOINT | APC
481 | STATCOM | STATCOM | STATCOM OPERATION | FIXED REACTIVE POWER SETPOINT(FS REF) | APC
482 | STATCOM | STATCOM | STATCOM OPERATION | REACTIVE POWER SETPOINT (QREF) | APC
483 | STATCOM | STATCOM | STATCOM OPERATION | NPS DEADBAND SETPOINT | APC
484 | STATCOM | STATCOM | STATCOM OPERATION | VQ MIN SETPOINT | APC
485 | STATCOM | STATCOM | STATCOM OPERATION | VQ MAX SETPOINT | APC
486 | STATCOM | STATCOM | STATCOM OPERATION | SLOPE SETPOINT | APC
487 | STATCOM | STATCOM | STATCOM OPERATION | GAIN FACTOR SETPOINT | APC
STATCOM (RXPE)
1 | ABC | FUTURE& COUPLING T/F-1 TIE |  | TIE BAY CURRENT PHASE_R | AI
2 | ABC | FUTURE& COUPLING T/F-1 TIE |  | TIE BAY CURRENT PHASE_Y | AI
3 | ABC | FUTURE& COUPLING T/F-1 TIE |  | TIE BAY CURRENT PHASE_B | AI
4 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI-R-PH TEMP (HV SIDE) | AI
5 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI -R-PHTEMP (IV SIDE) | AI
6 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI -R-PH TEMP (LV SIDE) | AI
7 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OTI R-PH TEMP | AI
8 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TAP POSITION INDICATION R-PH | AI
9 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI-Y-PH TEMP (HV SIDE) | AI
10 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI -Y-PH TEMP (IV SIDE) | AI
11 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI -Y-PH TEMP (LV SIDE) | AI
12 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OTI Y-PH TEMP | AI
13 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TAP POSITION INDICATION Y-PH | AI
14 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI-B-PH TEMP (HV SIDE) | AI
15 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI -B-PH TEMP (IV SIDE) | AI
16 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI -B-PH TEMP (LV SIDE) | AI
17 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OTI B-PH TEMP | AI
18 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TAP POSITION INDICATION B-PH | AI
19 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI- SP-PH TEMP (HV SIDE) | AI
20 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI -SP-PH TEMP (IV SIDE) | AI
21 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI -SP-PH TEMP (LV SIDE) | AI
22 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OTI SP-PH TEMP | AI
23 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TAP POSITION SP-PH INDICATION | AI
24 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | I (R-PHASE) | AI
25 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | I (Y-PHASE) | AI
26 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | I B-PHASE) | AI
27 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | MVAR | AI
28 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | MW | AI
29 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | V (B-R PHASE) | AI
30 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | V (R-Y PHASE) | AI
31 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | V (Y-B PHASE) | AI
32 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | FREQUENCY | AI
33 | ABC | COUPLING TRANSFORMER | STATCOM HV BAY - RPH | DGA H2O INDICATION R phase | AI
34 | ABC | COUPLING TRANSFORMER | STATCOM HV BAY - RPH | DGA H2 LEVEL INDICATION R phase | AI
35 | ABC | COUPLING TRANSFORMER | STATCOM HV BAY - YPH | DGA H2O INDICATION Y phase | AI
36 | ABC | COUPLING TRANSFORMER | STATCOM HV BAY - YPH | DGA H2 LEVEL INDICATION Y phase | AI
37 | ABC | COUPLING TRANSFORMER | STATCOM HV BAY - BPH | DGA H2O INDICATION B phase | AI
38 | ABC | COUPLING TRANSFORMER | STATCOM HV BAY - BPH | DGA H2 LEVEL INDICATION B phase | AI
39 | ABC | COUPLING TRANSFORMER | STATCOM HV BAY - SPARE PH | DGA H2O INDICATION Spare phase | AI
40 | ABC | COUPLING TRANSFORMER | STATCOM HV BAY - SPARE PH | DGA H2 LEVEL INDICATION Spare phase | AI
41 | 38.5KV | MV BUS BAR | MV BUS BAR | MV BUS VOLTAGE | AI
42 | 38.5KV | STATCOM- 1 | VSC-1 | STATCOM- 1 MVAR | AI
43 | 38.5KV | STATCOM- 2 | VSC-2 | STATCOM- 2 MVAR | AI
44 | 38.5KV | MSC | MSC | MSC MVAR | AI
45 | 38.5KV | MSR- 1 | MSR-1 | MSR- 1 MVAR | AI
46 | 38.5KV | MSR- 2 | MSR-2 | MSR- 2 MVAR | AI
47 | 38.5KV | STATCOM CONTROL | STATCOM | SLOPE OF INDUCTIVE POWER | AI
48 | 38.5KV | STATCOM CONTROL | STATCOM | SLOPE OF CAPACITIVE POWER | AI
49 | 38.5KV | STATCOM CONTROL | STATCOM | UP-SET U-REF(PU) | AI
50 | 38.5KV | STATCOM CONTROL | STATCOM | DN-SET U-REF(PU) | AI
51 | 38.5KV | STATCOM CONTROL | STATCOM | Q-SET REF(PU)/FS REF(PU) | AI
52 | 415 V | AUX | DCDB-1 | DCDB-1 VOLTAGE | AI
53 | 415 V | AUX | DCDB-1 | BATTERY SET-1 CURRENT | AI
54 | 415 V | AUX | CHARGER-1 | BATTERY CHARGER-1 CURRENT | AI
55 | 415 V | AUX | DCDB-2 | DCDB-2 VOLTAGE | AI
56 | 415 V | AUX | DCDB-2 | BATTERY SET-2 CURRENT | AI
57 | 415 V | AUX | CHARGER-2 | BATTERY CHARGER-2 CURRENT | AI
58 | 415 V | AUX | MSB INCOMER-1 | VOLTAGE R-Y | AI
59 | 415 V | AUX | MSB INCOMER-1 | VOLTAGE Y-B | AI
60 | 415 V | AUX | MSB INCOMER-1 | VOLTAGE B-R | AI
61 | 415 V | AUX | MSB INCOMER-1 | CURRENT R | AI
62 | 415 V | AUX | MSB INCOMER-1 | CURRENT Y | AI
63 | 415 V | AUX | MSB INCOMER-1 | CURRENT B | AI
64 | 415 V | AUX | MSB INCOMER-2 | VOLTAGE R-Y | AI
65 | 415 V | AUX | MSB INCOMER-2 | VOLTAGE Y-B | AI
66 | 415 V | AUX | MSB INCOMER-2 | VOLTAGE B-R | AI
67 | 415 V | AUX | MSB INCOMER-2 | CURRENT R | AI
68 | 415 V | AUX | MSB INCOMER-2 | CURRENT Y | AI
69 | 415 V | AUX | MSB INCOMER-2 | CURRENT B | AI
70 | 415 V | AUX | AIRCON AMBIENT | AMBIENT TEMPERATURE SWITCHYARD | AI
71 | 415 V | AUX | AIRCON CONTROL ROOM | CONTROL ROOM TEMPERATURE | AI
72 | 415 V | AUX | AIRCON BATTERY ROOM | BATTERY ROOM TEMPERATURE | AI
73 | 415 V | AUX | AIRCON UPS ROOM | UPS ROOM TEMPERATURE | AI
STATCOM (HYOSUNG)
1 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY Voltage R-Y | AI
2 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY Voltage Y-B | AI
3 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY Voltage B-R | AI
4 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN + TIE Current_Phase R | AI
5 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN + TIE Current_Phase Y | AI
6 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN + TIE Current_Phase B | AI
7 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | MVAR OF COUPLING TRANSFORMER HV SIDE | AI
8 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA R-PH) C2H2 | AI
9 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA R-PH) C2H4 | AI
10 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA R-PH) C2H6 | AI
11 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA R-PH) CH4 | AI
12 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA R-PH) CO2 | AI
13 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA R-PH) CO | AI
14 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA R-PH) H2O | AI
15 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA R-PH) H2 | AI
16 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA Y-PH) C2H2 | AI
17 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA Y-PH) C2H4 | AI
18 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA Y-PH) C2H6 | AI
19 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA Y-PH) CH4 | AI
20 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA Y-PH) CO2 | AI
21 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA Y-PH) CO | AI
22 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA Y-PH) H2O | AI
23 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA Y-PH) H2 | AI
24 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA B-PH) C2H2 | AI
25 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA B-PH) C2H4 | AI
26 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA B-PH) C2H6 | AI
27 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA B-PH) CH4 | AI
28 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA B-PH) CO2 | AI
29 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA B-PH) CO | AI
30 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA B-PH) H2O | AI
31 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA B-PH) H2 | AI
32 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA SP-PH) C2H2 | AI
33 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA SP-PH) C2H4 | AI
34 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA SP-PH) C2H6 | AI
35 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA SP-PH) CH4 | AI
36 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA SP-PH) CO2 | AI
37 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA SP-PH) CO | AI
38 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA SP-PH) H2O | AI
39 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA SP-PH) H2 | AI
40 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) WTI-HV | AI
41 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) WTI-LV | AI
42 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) OTI | AI
43 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) WTI-HV | AI
44 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) WTI-LV | AI
45 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) OTI | AI
46 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) WTI-HV | AI
47 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) WTI-LV | AI
48 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) OTI | AI
49 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) WTI-HV | AI
50 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) WTI-LV | AI
51 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) OTI | AI
52 | 20KV | STATCOM-1 | VSC-1 | STATCOM UNIT-1 MVAR | AI
53 | 20KV | STATCOM-2 | VSC-2 | STATCOM UNIT-2 MVAR | AI
54 | 20KV | STATCOM CONTROL | STATCOM | V-REF SETTING | AI
55 | 20KV | STATCOM CONTROL | STATCOM | DROOP SETTING | AI
56 | 20KV | STATCOM CONTROL | STATCOM | DEAD-BAND UP SETTING | AI
57 | 20KV | STATCOM CONTROL | STATCOM | DEAD-BAND DN SETTING | AI
58 | 20KV | STATCOM CONTROL | STATCOM | Q-REF SETTING | AI
59 | 20KV | MV BUS BAR | MV BUS BAR | MV BUS VOLTAGE | AI
60 | 20KV | AUX.T/F | MV AUX T/F | KW | AI
61 | 20KV | AUX.T/F | MV AUX T/F | KVAR | AI
62 | 33KV | AUX.T/F | TERTIARY | KW | AI
63 | 33KV | AUX.T/F | TERTIARY | KVAR | AI
64 | 415 V | DCDB | DCDB-1 | 220V DCDB-1 VOLTAGE | AI
65 | 415 V | DCDB | DCDB-1 | 220V BATTERY SET-1 CURRENT | AI
66 | 415 V | DCDB | DCDB-1 | 220V BATTERY CHARGER-1 CURRENT | AI
67 | 415 V | DCDB | DCDB-2 | 220V DCDB-2 VOLTAGE | AI
68 | 415 V | DCDB | DCDB-2 | 220V BATTERY SET-2 CURRENT | AI
69 | 415 V | DCDB | DCDB-2 | 220V BATTERY CHARGER-2 CURRENT | AI
70 | 415 V | LTSUP | MSB-1 | (R-PH) INCOMER-1 VOLTAGE | AI
71 | 415 V | LTSUP | MSB-1 | (Y-PH) INCOMER-1 VOLTAGE | AI
72 | 415 V | LTSUP | MSB-1 | (B-PH) INCOMER-1 VOLTAGE | AI
73 | 415 V | LTSUP | MSB-2 | (R-PH) INCOMER-2 VOLTAGE | AI
74 | 415 V | LTSUP | MSB-2 | (Y-PH) INCOMER-2 VOLTAGE | AI
75 | 415 V | LTSUP | MSB-2 | (B-PH) INCOMER-2 VOLTAGE | AI
76 | 415 V | LTSUP | MSB-1 | (R-PH) INCOMER-1 CURRENT | AI
77 | 415 V | LTSUP | MSB-1 | (Y-PH) INCOMER-1 CURRENT | AI
78 | 415 V | LTSUP | MSB-1 | (B-PH) INCOMER-1 CURRENT | AI
79 | 415 V | LTSUP | MSB-2 | (R-PH) INCOMER-2 CURRENT | AI
80 | 415 V | LTSUP | MSB-2 | (Y-PH) INCOMER-2 CURRENT | AI
81 | 415 V | LTSUP | MSB-2 | (B-PH) INCOMER-2 CURRENT | AI
82 | 415 V | LTSUP | DGSET | (R-PH) DG FEEDER VOLTAGE | AI
83 | 415 V | LTSUP | DGSET | (Y-PH) DG FEEDER VOLTAGE | AI
84 | 415 V | LTSUP | DGSET | (B-PH) DG FEEDER VOLTAGE | AI
85 | 415 V | LTSUP | DGSET | (R-PH) DG FEEDER CURRENT | AI
86 | 415 V | LTSUP | DGSET | (Y-PH) DG FEEDER CURRENT | AI
87 | 415 V | LTSUP | DGSET | (B-PH) DG FEEDER CURRENT | AI
88 | 20KV | MSR-1 | MSR | MSR-1 MVAR | AI
89 | 20KV | MSR-2 | MSR | MSR-2 MVAR | AI
90 | 20KV | MSC | MSC | MSC MVAR | AI
91 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | CONTROL MODE : MANUAL Q CONTROL / AUTOMATIC VOLTAGE | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
92 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | V-REF SETTING | AI_CMD
93 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | DEAD-BAND UP SETTING | AI_CMD
94 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | DEAD-BAND DN SETTING | AI_CMD
95 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | DROOP SETTING | AI_CMD
96 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | Q-REF SETTING | AI_CMD
97 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | POD CONTROL ENABLE | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
98 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | SSOD CONTROL ENABLE | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
99 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | ADACTIVE GAIN REDUCTION ENABLE | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
100 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | ADACTIVE GAIN CLACULATION ENABLE | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
101 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | NEGATIVE SEQ. VOLTAGE CONTROL ENABLE | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
102 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | MSC CONTROL MODE - AUTOMATIC / MANUAL | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
103 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | MSR-1 CONTROL MODE - AUTOMATIC / MANUAL | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
104 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | MSR-2 CONTROL MODE - AUTOMATIC / MANUAL | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
105 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | HV BR MAIN BAY CONTROL MODE - AUTOMATIC (HYD ONLY) | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
106 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | HV BR TIE BAY CONTROL MODE - AUTOMATIC (HYD ONLY) | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
107 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | CONTROL MODE : MANUAL Q CONTROL / AUTOMATIC VOLTAGE | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
108 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | V-REF SETTING | AI_CMD
109 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | DEAD-BAND UP SETTING | AI_CMD
110 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | DEAD-BAND DN SETTING | AI_CMD
111 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | DROOP SETTING | AI_CMD
112 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | Q-REF SETTING | AI_CMD
113 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | POD CONTROL ENABLE | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
114 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | SSOD CONTROL ENABLE | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
115 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | ADACTIVE GAIN REDUCTION ENABLE | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
116 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | ADACTIVE GAIN CLACULATION ENABLE | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
117 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | NEGATIVE SEQ. VOLTAGE CONTROL ENABLE | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
118 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | MSC CONTROL MODE - AUTOMATIC / MANUAL | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
119 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | MSR-1 CONTROL MODE - AUTOMATIC / MANUAL | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
120 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | MSR-2 CONTROL MODE - AUTOMATIC / MANUAL | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
121 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | HV BR MAIN BAY CONTROL MODE - AUTOMATIC / MANUAL (HYD ONLY) | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage
122 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | HV BR TIE BAY CONTROL MODE - AUTOMATIC / MANUAL (HYD ONLY) | AI_CMD |  | 1 : Manual Q / 5 : Automatic Voltage

## AI (2) (hidden)
Sl. | BAY NUM. | BAY NAME | DEVICE ID | SIGNAL DESCRIPTION | DATA TYPE | SCADA ID | REMARK
1 | BUS | BUS | BUS | VOLTAGE R-Y PHASE | AI | KVRY
2 | BUS | BUS | BUS | VOLTAGE Y-B PHASE | AI | KVYB
3 | BUS | BUS | BUS | VOLTAGE B-R PHASE | AI | KVBR
4 | BUS | BUS | BUS | FREQUENCY | AI | HZ
1 | ABC | LINE FEEDER | LINE / LSR / BSR | I (R-PHASE) | AI | IR
2 | ABC | LINE FEEDER | LINE / LSR / BSR | I (Y-PHASE) | AI | IY
3 | ABC | LINE FEEDER | LINE / LSR / BSR | I (B-PHASE) | AI | IB
4 | ABC | LINE FEEDER | LINE / LSR / BSR | MW | AI | MW
5 | ABC | LINE FEEDER | LINE / LSR / BSR | MVAR | AI | MX
6 | ABC | LINE FEEDER | LINE / LSR / BSR | V (R-Y PHASE) | AI | KVRY
7 | ABC | LINE FEEDER | LINE / LSR / BSR | V (Y-B PHASE) | AI | KVYB
8 | ABC | LINE FEEDER | LINE / LSR / BSR | V (B-R PHASE) | AI | KVBR
9 | ABC | LINE FEEDER | LINE / LSR / BSR | FREQUENCY | AI | HZ
10 | ABC | LINE FEEDER | LINE | MAIN-1 FAULT IMPEDANCE | AI | FLZ1
11 | ABC | LINE FEEDER | LINE | MAIN-1 FAULT DISTANCE | AI | FLD1
12 | ABC | LINE FEEDER | LINE | MAIN-1 FAULT PERCENTAGE | AI | FLP1
13 | ABC | LINE FEEDER | LINE | MAIN-2 FAULT IMPEDANCE | AI | FLZ2
14 | ABC | LINE FEEDER | LINE | MAIN-2 FAULT DISTANCE | AI | FLD2
15 | ABC | LINE FEEDER | LINE | MAIN-2 FAULT PERCENTAGE | AI | FLP2
1 | ABC | BUS REACTOR/ LINE REACTOR | RE | REACTOR I (R-PHASE) | AI | IR
2 | ABC | BUS REACTOR/ LINE REACTOR | RE | REACTOR I (Y-PHASE) | AI | IY
3 | ABC | BUS REACTOR/ LINE REACTOR | RE | REACTOR I (B-PHASE) | AI | IB
4 | ABC | BUS REACTOR/ LINE REACTOR | RE | REACTOR MVAR | AI | MX
5 | ABC | BUS REACTOR/ LINE REACTOR | RE | REACTOR V (R-Y PHASE) | AI | KVRY
6 | ABC | BUS REACTOR/ LINE REACTOR | RE | REACTOR V (Y-B PHASE) | AI | KVYB
7 | ABC | BUS REACTOR/ LINE REACTOR | RE | REACTOR V (B-R PHASE) | AI | KVBR
8 | ABC | BUS REACTOR/ LINE REACTOR | RE | FREQUENCY | AI | HZ
9 | ABC | BUS REACTOR/ LINE REACTOR | RE | WTI TEMP R PHASE | AI | WTI | ONLY ONE SIGNAL IN PLACE OF THREE SIGNALS APPLICABLE INDIVIDUALLY FOR R/Y/B PHASES TO BE CONSIDERED FOR 3 PHASE LINE REACTOR/ BUS REACTOR
10 | ABC | BUS REACTOR/ LINE REACTOR | RE | WTI TEMP Y PHASE | AI | WTI
11 | ABC | BUS REACTOR/ LINE REACTOR | RE | WTI TEMP B PHASE | AI | WTI
12 | ABC | BUS REACTOR/ LINE REACTOR | RE | OTI TEMP R PHASE | AI | OTI
13 | ABC | BUS REACTOR/ LINE REACTOR | RE | OTI TEMP Y PHASE | AI | OTI
14 | ABC | BUS REACTOR/ LINE REACTOR | RE | OTI TEMP B PHASE | AI | OTI
15 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA MOISTURE VALUE - R PHASE | AI | MOIS
16 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA H2 VALUE - R PHASE | AI | DGH2
17 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H2 VALUE - R PHASE | AI | C2H2
18 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CO VALUE - R PHASE | AI | DGCO
19 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CO2 VALUE - R PHASE | AI | DCO2
20 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CH4 VALUE - R PHASE | AI | DCH4
21 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H6 VALUE - R PHASE | AI | C2H6
22 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H4 VALUE - R PHASE | AI | C2H4
23 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA O2 VALUE - R PHASE | AI | DGO2
24 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA MOISTURE VALUE - Y PHASE | AI | MOIS
25 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA H2 VALUE - Y PHASE | AI | DGH2
26 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H2 VALUE - Y PHASE | AI | C2H2
27 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CO VALUE - Y PHASE | AI | DGCO
28 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CO2 VALUE - Y PHASE | AI | DCO2
29 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CH4 VALUE - Y PHASE | AI | DCH4
30 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H6 VALUE - Y PHASE | AI | C2H6
31 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H4 VALUE - Y PHASE | AI | C2H4
32 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA O2 VALUE - Y PHASE | AI | DGO2
33 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA MOISTURE VALUE - B PHASE | AI | MOIS
34 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA H2 VALUE - B PHASE | AI | DGH2
35 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H2 VALUE - B PHASE | AI | C2H2
36 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CO VALUE - B PHASE | AI | DGCO
37 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CO2 VALUE - B PHASE | AI | DCO2
38 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA CH4 VALUE - B PHASE | AI | DCH4
39 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H6 VALUE - B PHASE | AI | C2H6
40 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA C2H4 VALUE - B PHASE | AI | C2H4
41 | ABC | BUS REACTOR/ LINE REACTOR | RE | DGA O2 VALUE - B PHASE | AI | DGO2
1 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | WTI TEMP SPARE | AI | WTI
2 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | OTI TEMP SPARE | AI | OTI
3 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA MOISTURE VALUE | AI | MOIS
4 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA H2 VALUE | AI | DGH2
5 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA C2H2 VALUE | AI | C2H2
6 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA CO VALUE | AI | DGCO
7 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA CO2 VALUE | AI | DCO2
8 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA CH4 VALUE | AI | DCH4
9 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA C2H6 VALUE | AI | C2H6
10 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA C2H4 VALUE | AI | C2H4
11 | ABC | SPARE LINE REACTOR / BUS REACTOR | RE | DGA O2 VALUE | AI | DGO2
1 | ABC | TIE/ BUS COUPLER / BUS SECTION | TIE/ BC/ BS | I (R-PHASE) | AI | IR
2 | ABC | TIE/ BUS COUPLER / BUS SECTION | TIE/ BC/ BS | I (Y-PHASE) | AI | IY
3 | ABC | TIE/ BUS COUPLER / BUS SECTION | TIE/ BC/ BS | I (B-PHASE) | AI | IB
1 | ABC | ICT | XFMR_P | I (R-PHASE) | AI | IR
2 | ABC | ICT | XFMR_P | I (Y-PHASE) | AI | IY
3 | ABC | ICT | XFMR_P | I (B-PHASE) | AI | IB
4 | ABC | ICT | XFMR_P | MW | AI | MW
5 | ABC | ICT | XFMR_P | MVAR | AI | MX
6 | ABC | ICT | XFMR_P | V (R-Y PHASE) | AI | KVRY
7 | ABC | ICT | XFMR_P | V (Y-B PHASE) | AI | KVYB
8 | ABC | ICT | XFMR_P | V (B-R PHASE) | AI | KVBR
9 | ABC | ICT | XFMR_P | FREQUENCY | AI | HZ
10 | ABC | ICT | XFMR_P | HVWTI TEMP - R PHASE | AI | HVWT | ONLY ONE SIGNAL IN PLACE OF THREE SIGNALS APPLICABLE INDIVIDUALLY FOR R/Y/B PHASES TO BE CONSIDERED IN CASE OF 3-PHASE ICT
11 | ABC | ICT | XFMR_S | IVWTI TEMP - R PHASE | AI | IVWT
12 | ABC | ICT | XFMR_T | LVWTI TEMP - R PHASE | AI | LVWT
13 | ABC | ICT | XFMR_P | HVWTI TEMP - Y PHASE | AI | HVWT
14 | ABC | ICT | XFMR_S | IVWTI TEMP - Y PHASE | AI | IVWT
15 | ABC | ICT | XFMR_T | LVWTI TEMP - Y PHASE | AI | LVWT
16 | ABC | ICT | XFMR_P | HVWTI TEMP - B PHASE | AI | HVWT
17 | ABC | ICT | XFMR_S | IVWTI TEMP - B PHASE | AI | IVWT
18 | ABC | ICT | XFMR_T | LVWTI TEMP - B PHASE | AI | LVWT
19 | ABC | ICT | XFMR_P | OTI TEMP R PHASE | AI | OTI
20 | ABC | ICT | XFMR_P | OTI TEMP Y PHASE | AI | OTI
21 | ABC | ICT | XFMR_P | OTI TEMP B PHASE | AI | OTI
22 | ABC | ICT | XFMR_P | TAP POSITION INDICATOR - R PHASE | AI | TPI
23 | ABC | ICT | XFMR_P | TAP POSITION INDICATOR - Y PHASE | AI | TPI
24 | ABC | ICT | XFMR_P | TAP POSITION INDICATOR - B PHASE | AI | TPI
25 | ABC | ICT | XFMR_P | DGA MOISTURE VALUE - R PHASE | AI | MOIS
26 | ABC | ICT | XFMR_P | DGA H2 VALUE - R PHASE | AI | DGH2
27 | ABC | ICT | XFMR_P | DGA C2H2 VALUE - R PHASE | AI | C2H2
28 | ABC | ICT | XFMR_P | DGA CO VALUE - R PHASE | AI | DGCO
29 | ABC | ICT | XFMR_P | DGA CO2 VALUE - R PHASE | AI | DCO2
30 | ABC | ICT | XFMR_P | DGA CH4 VALUE - R PHASE | AI | DCH4
31 | ABC | ICT | XFMR_P | DGA C2H6 VALUE - R PHASE | AI | C2H6
32 | ABC | ICT | XFMR_P | DGA C2H4 VALUE - R PHASE | AI | C2H4
33 | ABC | ICT | XFMR_P | DGA O2 VALUE - R PHASE | AI | DGO2
34 | ABC | ICT | XFMR_P | DGA MOISTURE VALUE - Y PHASE | AI | MOIS
35 | ABC | ICT | XFMR_P | DGA H2 VALUE - Y PHASE | AI | DGH2
36 | ABC | ICT | XFMR_P | DGA C2H2 VALUE - Y PHASE | AI | C2H2
37 | ABC | ICT | XFMR_P | DGA CO VALUE - Y PHASE | AI | DGCO
38 | ABC | ICT | XFMR_P | DGA CO2 VALUE - Y PHASE | AI | DCO2
39 | ABC | ICT | XFMR_P | DGA CH4 VALUE - Y PHASE | AI | DCH4
40 | ABC | ICT | XFMR_P | DGA C2H6 VALUE - Y PHASE | AI | C2H6
41 | ABC | ICT | XFMR_P | DGA C2H4 VALUE - Y PHASE | AI | C2H4
42 | ABC | ICT | XFMR_P | DGA O2 VALUE - Y PHASE | AI | DGO2
43 | ABC | ICT | XFMR_P | DGA MOISTURE VALUE - B PHASE | AI | MOIS
44 | ABC | ICT | XFMR_P | DGA H2 VALUE - B PHASE | AI | DGH2
45 | ABC | ICT | XFMR_P | DGA C2H2 VALUE - B PHASE | AI | C2H2
46 | ABC | ICT | XFMR_P | DGA CO VALUE - B PHASE | AI | DGCO
47 | ABC | ICT | XFMR_P | DGA CO2 VALUE - B PHASE | AI | DCO2
48 | ABC | ICT | XFMR_P | DGA CH4 VALUE - B PHASE | AI | DCH4
49 | ABC | ICT | XFMR_P | DGA C2H6 VALUE - B PHASE | AI | C2H6
50 | ABC | ICT | XFMR_P | DGA C2H4 VALUE - B PHASE | AI | C2H4
51 | ABC | ICT | XFMR_P | DGA O2 VALUE - B PHASE | AI | DGO2
1 | SPARE | SPARE ICT | XFMR_P | HVWTI - TEMP SPARE | AI | HVWT
2 | SPARE | SPARE ICT | XFMR_S | IVWTI - TEMP SPARE | AI | IVWT
3 | SPARE | SPARE ICT | XFMR_T | LVWTI - TEMP SPARE | AI | LVWT
4 | SPARE | SPARE ICT | XFMR_P | OTI TEMP SPARE | AI | OTI
5 | SPARE | SPARE ICT | XFMR_P | TAP POSITION INDICATOR | AI | TPI
6 | SPARE | SPARE ICT | XFMR_P | DGA MOISTURE VALUE | AI | MOIS
7 | SPARE | SPARE ICT | XFMR_P | DGA H2 VALUE | AI | DGH2
8 | SPARE | SPARE ICT | XFMR_P | DGA C2H2 VALUE | AI | C2H2
9 | SPARE | SPARE ICT | XFMR_P | DGA CO VALUE | AI | DGCO
10 | SPARE | SPARE ICT | XFMR_P | DGA CO2 VALUE | AI | DCO2
11 | SPARE | SPARE ICT | XFMR_P | DGA CH4 VALUE | AI | DCH4
12 | SPARE | SPARE ICT | XFMR_P | DGA C2H6 VALUE | AI | C2H6
13 | SPARE | SPARE ICT | XFMR_P | DGA C2H4 VALUE | AI | C2H4
14 | SPARE | SPARE ICT | XFMR_P | DGA O2 VALUE | AI | DGO2
1 | ABC | FSC | FSC-X | MOV TEMPERATURE R PHASE | AI
2 | ABC | FSC | FSC-X | MOV TEMPERATURE Y PHASE | AI
3 | ABC | FSC | FSC-X | MOV TEMPERATURE B PHASE | AI
4 | ABC | FSC | FSC-X | CAPACITOR R PHASE CURRENT | AI
5 | ABC | FSC | FSC-X | CAPACITOR Y PHASE CURRENT | AI
6 | ABC | FSC | FSC-X | CAPACITOR B PHASE CURRENT | AI
7 | ABC | FSC | FSC-X | CAPACITOR R PHASE UNBALANCED CURRENT | AI
8 | ABC | FSC | FSC-X | CAPACITOR Y PHASE UNBALANCED CURRENT | AI
9 | ABC | FSC | FSC-X | CAPACITOR B PHASE UNBALANCED CURRENT | AI
10 | ABC | FSC | FSC-X | LINE CT CURRENT R-PH | AI
11 | ABC | FSC | FSC-X | LINE CT CURRENT Y-PH | AI
12 | ABC | FSC | FSC-X | LINE CT CURRENT B-PH | AI
13 | ABC | FSC | FSC-X | KIOSK TEMP | AI
1 | 220VDC | DCDB | 220V_DCDB-1 | 220V DCDB -1 VOLTAGE | AI
2 | 220VDC | DCDB | 220V_DCDB-1 | 220V BATTERY SET-1 CURRENT | AI
3 | 220VDC | DCDB | 220V_DCDB-2 | 220V DCDB -2 VOLTAGE | AI
4 | 220VDC | DCDB | 220V_DCDB-2 | 220V BATTERY SET-2 CURRENT | AI
5 | 48 VDC | DCDB | 48V_DCDB-1 | 48V DCDB -1 VOLTAGE | AI
6 | 48 VDC | DCDB | 48V_DCDB-1 | 48V BATTERY SET-1 CURRENT | AI
7 | 48 VDC | DCDB | 48V_DCDB-2 | 48V DCDB -2 VOLTAGE | AI
8 | 48 VDC | DCDB | 48V_DCDB-2 | 48V BATTERY SET-2 CURRENT | AI
9 | 220VDC | BCHRG | BATCHRG220V-1 | 220V BATTERY CHARGER-1 CURRENT | AI
10 | 220VDC | BCHRG | BATCHRG220V-2 | 220V BATTERY CHARGER-2 CURRENT | AI
11 | 48 VDC | BCHRG | BATCHRG48V-1 | 48V BATTERY CHARGER-1 CURRENT | AI
12 | 48 VDC | BCHRG | BATCHRG48V-2 | 48V BATTERY CHARGER-2 CURRENT | AI
13 | 415 V | FP | FIREPROTN | FIRE FIGHTING PRESSURE MONITORING | AI
14 | 415 V | FP | DPUMP | DIESEL ENGINE BATTERY-1 VOLTAGE | AI
15 | 415 V | FP | DPUMP | DIESEL ENGINE BATTERY-2 VOLTAGE | AI
16 | 415 V | FP | ICT | FF NIS Nitrogen Cylinder Pressure | AI
17 |  |  |  | WIND SPEED | AI
18 |  |  |  | WIND DIRECTION | AI
19 | 415 V | AIRCON | G_KIOSK_1 | 765KV KIOSK-1 TEMP | AI
20 | 415 V | AIRCON | F_KIOSK_1 | 400KV KIOSK-1 TEMP | AI
21 | 415 V | AIRCON | TEMP_MON | CONTROL ROOM TEMPRATURE | AI
22 | 415 V | AIRCON | TEMP_MON | BATTERY ROOM TEMPRATURE | AI
23 | 415 V | AIRCON | TEMP_MON | AMBIENT TEMPERATURE OUTDOOR | AI
24 | 415 V | AIRCON | TEMP_MON | AMBIENT RELATIVE HUMIDITY OUTDOOR | AI
25 | 415 V | DG Set | DGSET-1 | VOLTAGE (R-Y PHASE) | AI
26 | 415 V | DG Set | DGSET-1 | VOLTAGE (Y-B PHASE) | AI
27 | 415 V | DG Set | DGSET-1 | VOLTAGE (B-R PHASE) | AI
28 | 415 V | DG Set | DGSET-1 | CURRENT (R-PHASE) | AI
29 | 415 V | DG Set | DGSET-1 | CURRENT (Y-PHASE) | AI
30 | 415 V | DG Set | DGSET-1 | CURRENT (B-PHASE) | AI
31 | 415 V | DG Set | DGSET-1 | DG SET BATTERY-1 VOLTAGE | AI
32 | 415 V | DG Set | DGSET-1 | DG SET BATTERY-2 VOLTAGE | AI
33 | 415 V | LTSUP | MSB-1 | VOLTAGE (R-Y PHASE) | AI
34 | 415 V | LTSUP | MSB-1 | VOLTAGE (Y-B PHASE) | AI
35 | 415 V | LTSUP | MSB-1 | VOLTAGE (B-R PHASE) | AI
36 | 415 V | LTSUP | MSB-1 | CURRENT (R-PHASE) | AI
37 | 415 V | LTSUP | MSB-1 | CURRENT (Y-PHASE) | AI
38 | 415 V | LTSUP | MSB-1 | CURRENT (B-PHASE) | AI
39 | 415 V | LTSUP | MSB-2 | VOLTAGE (R-Y PHASE) | AI
40 | 415 V | LTSUP | MSB-2 | VOLTAGE (Y-B PHASE) | AI
41 | 415 V | LTSUP | MSB-2 | VOLTAGE (B-R PHASE) | AI
42 | 415 V | LTSUP | MSB-2 | CURRENT (R-PHASE) | AI
43 | 415 V | LTSUP | MSB-2 | CURRENT (Y-PHASE) | AI
44 | 415 V | LTSUP | MSB-2 | CURRENT (B-PHASE) | AI
STATCOM (SIEMENS)
1 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY | HV Main Bay Voltage R-Y | AI
2 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY | HV Main Bay Voltage Y-B | AI
3 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY | HV Main Bay Voltage B-R | AI
4 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY | HV Main Bay Current_Phase R | AI
5 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY | HV Main Bay Current_Phase Y | AI
6 | 4XX | STATCOM HV SIDE MAIN BAY | STATCOM HV BAY | HV Main Bay Current_Phase B | AI
7 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER | COUPLING TRANSFORMER MVAR HV SIDE | AI
8 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA CARBON DIOXIDE | AI
9 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA ETHYLENE | AI
10 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA ACETYLENE | AI
11 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA ETHANE | AI
12 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA HYDROGEN | AI
13 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA OXYGEN | AI
14 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA METHANE | AI
15 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA CARBON MONOXIDE | AI
16 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA NITROGEN | AI
17 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA WATER | AI
18 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-R | TRANSFORMER T01_L1 DGA COMBUSTIBLE GASSES | AI
19 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA CARBON DIOXIDE | AI
20 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA ETHYLENE | AI
21 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA ACETYLENE | AI
22 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA ETHANE | AI
23 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA HYDROGEN | AI
24 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA OXYGEN | AI
25 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA METHANE | AI
26 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA CARBON MONOXIDE | AI
27 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA NITROGEN | AI
28 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA WATER | AI
29 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-Y | TRANSFORMER T01_L2 DGA COMBUSTIBLE GASSES | AI
30 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA CARBON DIOXIDE | AI
31 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA ETHYLENE | AI
32 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA ACETYLENE | AI
33 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA ETHANE | AI
34 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA HYDROGEN | AI
35 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA OXYGEN | AI
36 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA METHANE | AI
37 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA CARBON MONOXIDE | AI
38 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA NITROGEN | AI
39 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA WATER | AI
40 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-B | TRANSFORMER T01_L3 DGA COMBUSTIBLE GASSES | AI
41 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA CARBON DIOXIDE | AI
42 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA ETHYLENE | AI
43 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA ACETYLENE | AI
44 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA ETHANE | AI
45 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA HYDROGEN | AI
46 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA OXYGEN | AI
47 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA METHANE | AI
48 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA CARBON MONOXIDE | AI
49 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA NITROGEN | AI
50 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA WATER | AI
51 | 4XX | STATCOM HV SIDE MAIN BAY | COUPLING TRANSFORMER (HV) T01-S | TRANSFORMER T01_LX DGA COMBUSTIBLE GASSES | AI
52 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY | HV Tie Bay Current_Phase R | AI
53 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY | HV Tie Bay Current_Phase Y | AI
54 | 4YY | STATCOM HV SIDE TIE BAY | TIE BAY 4YY | HV Tie Bay Current_Phase B | AI
55 | STATCOM | STATCOM | MV BUS BAR | MV BUS VOLTAGE | AI
56 | J11 | STATCOM VSC-1 BAY | VSC-1 MV-J11 | STATCOM 1 MVAR | AI
57 | J12 | STATCOM VSC-2 BAY | VSC-2 MV-J12 | STATCOM 2 MVAR | AI
58 | J21 | STATCOM MSR-1 BAY | MSR-1 MV-J21 | MSR 1 MVAR | AI
59 | J22 | STATCOM MSR-2 BAY | MSR-2 MV-J22 | MSR 2 MVAR | AI
60 | J31 | STATCOM MSC-1 BAY | MSC-1 MV-J31 | MSC 1 MVAR | AI
61 | J32 | STATCOM MSC-2 BAY | MSC-2 MV-J32 | MSC 2 MVAR | AI
62 | STATCOM | STATCOM | STATCOM OPERATION | SLOPE | AI
63 | STATCOM | STATCOM | STATCOM OPERATION | UP-SET U-REF(PU) | AI
64 | STATCOM | STATCOM | STATCOM OPERATION | DN-SET U-REF(PU) | AI
65 | STATCOM | STATCOM | STATCOM OPERATION | Q-SET REF(PU) | AI
66 | STATCOM | STATCOM | STATCOM OPERATION | LOAD FACTOR SETPOINT | AI
67 | STATCOM | STATCOM | STATCOM OPERATION | FIXED REACTIVE POWER SETPOINT(FS REF) | AI
68 | STATCOM | STATCOM | STATCOM OPERATION | NPS DEADBAND SETPOINT | AI
69 | STATCOM | STATCOM | STATCOM OPERATION | VQ MIN SETPOINT | AI
70 | STATCOM | STATCOM | STATCOM OPERATION | VQ MAX SETPOINT | AI
71 | STATCOM | STATCOM | STATCOM OPERATION | GAIN FACTOR SETPOINT | AI
72 | STATCOM | STATCOM | STATCOM OPERATION | INDUCTIVE VOLTAGE SETPOINT | AI
73 | STATCOM | STATCOM | STATCOM OPERATION | CAPACITIVE VOLTAGE SETPOINT | AI
74 | STATCOM | STATCOM | STATCOM OPERATION | LOAD FACTOR SETPOINT | AI
75 | STATCOM | STATCOM | STATCOM OPERATION | FIXED REACTIVE POWER SETPOINT(FS REF) | AI
76 | STATCOM | STATCOM | STATCOM OPERATION | REACTIVE POWER SETPOINT (QREF) | AI
77 | STATCOM | STATCOM | STATCOM OPERATION | NPS DEADBAND SETPOINT | AI
78 | STATCOM | STATCOM | STATCOM OPERATION | VQ MIN SETPOINT | AI
79 | STATCOM | STATCOM | STATCOM OPERATION | VQ MAX SETPOINT | AI
80 | STATCOM | STATCOM | STATCOM OPERATION | SLOPE SETPOINT | AI
81 | STATCOM | STATCOM | STATCOM OPERATION | GAIN FACTOR SETPOINT | AI
478 | STATCOM | STATCOM | STATCOM OPERATION | INDUCTIVE VOLTAGE SETPOINT | APC
479 | STATCOM | STATCOM | STATCOM OPERATION | CAPACITIVE VOLTAGE SETPOINT | APC
480 | STATCOM | STATCOM | STATCOM OPERATION | LOAD FACTOR SETPOINT | APC
481 | STATCOM | STATCOM | STATCOM OPERATION | FIXED REACTIVE POWER SETPOINT(FS REF) | APC
482 | STATCOM | STATCOM | STATCOM OPERATION | REACTIVE POWER SETPOINT (QREF) | APC
483 | STATCOM | STATCOM | STATCOM OPERATION | NPS DEADBAND SETPOINT | APC
484 | STATCOM | STATCOM | STATCOM OPERATION | VQ MIN SETPOINT | APC
485 | STATCOM | STATCOM | STATCOM OPERATION | VQ MAX SETPOINT | APC
486 | STATCOM | STATCOM | STATCOM OPERATION | SLOPE SETPOINT | APC
487 | STATCOM | STATCOM | STATCOM OPERATION | GAIN FACTOR SETPOINT | APC
STATCOM (RXPE)
1 | ABC | FUTURE& COUPLING T/F-1 TIE |  | TIE BAY CURRENT PHASE_R | AI
2 | ABC | FUTURE& COUPLING T/F-1 TIE |  | TIE BAY CURRENT PHASE_Y | AI
3 | ABC | FUTURE& COUPLING T/F-1 TIE |  | TIE BAY CURRENT PHASE_B | AI
4 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI-R-PH TEMP (HV SIDE) | AI
5 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI -R-PHTEMP (IV SIDE) | AI
6 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI -R-PH TEMP (LV SIDE) | AI
7 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OTI R-PH TEMP | AI
8 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TAP POSITION INDICATION R-PH | AI
9 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI-Y-PH TEMP (HV SIDE) | AI
10 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI -Y-PH TEMP (IV SIDE) | AI
11 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI -Y-PH TEMP (LV SIDE) | AI
12 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OTI Y-PH TEMP | AI
13 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TAP POSITION INDICATION Y-PH | AI
14 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI-B-PH TEMP (HV SIDE) | AI
15 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI -B-PH TEMP (IV SIDE) | AI
16 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI -B-PH TEMP (LV SIDE) | AI
17 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OTI B-PH TEMP | AI
18 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TAP POSITION INDICATION B-PH | AI
19 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI- SP-PH TEMP (HV SIDE) | AI
20 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI -SP-PH TEMP (IV SIDE) | AI
21 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | WTI -SP-PH TEMP (LV SIDE) | AI
22 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | OTI SP-PH TEMP | AI
23 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | TAP POSITION SP-PH INDICATION | AI
24 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | I (R-PHASE) | AI
25 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | I (Y-PHASE) | AI
26 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | I B-PHASE) | AI
27 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | MVAR | AI
28 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | MW | AI
29 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | V (B-R PHASE) | AI
30 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | V (R-Y PHASE) | AI
31 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | V (Y-B PHASE) | AI
32 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | FREQUENCY | AI
33 | ABC | COUPLING TRANSFORMER | STATCOM HV BAY - RPH | DGA H2O INDICATION R phase | AI
34 | ABC | COUPLING TRANSFORMER | STATCOM HV BAY - RPH | DGA H2 LEVEL INDICATION R phase | AI
35 | ABC | COUPLING TRANSFORMER | STATCOM HV BAY - YPH | DGA H2O INDICATION Y phase | AI
36 | ABC | COUPLING TRANSFORMER | STATCOM HV BAY - YPH | DGA H2 LEVEL INDICATION Y phase | AI
37 | ABC | COUPLING TRANSFORMER | STATCOM HV BAY - BPH | DGA H2O INDICATION B phase | AI
38 | ABC | COUPLING TRANSFORMER | STATCOM HV BAY - BPH | DGA H2 LEVEL INDICATION B phase | AI
39 | ABC | COUPLING TRANSFORMER | STATCOM HV BAY - SPARE PH | DGA H2O INDICATION Spare phase | AI
40 | ABC | COUPLING TRANSFORMER | STATCOM HV BAY - SPARE PH | DGA H2 LEVEL INDICATION Spare phase | AI
41 | 38.5KV | MV BUS BAR | MV BUS BAR | MV BUS VOLTAGE | AI
42 | 38.5KV | STATCOM- 1 | VSC-1 | STATCOM- 1 MVAR | AI
43 | 38.5KV | STATCOM- 2 | VSC-2 | STATCOM- 2 MVAR | AI
44 | 38.5KV | MSC | MSC | MSC MVAR | AI
45 | 38.5KV | MSR- 1 | MSR-1 | MSR- 1 MVAR | AI
46 | 38.5KV | MSR- 2 | MSR-2 | MSR- 2 MVAR | AI
47 | 38.5KV | STATCOM CONTROL | STATCOM | SLOPE OF INDUCTIVE POWER | AI
48 | 38.5KV | STATCOM CONTROL | STATCOM | SLOPE OF CAPACITIVE POWER | AI
49 | 38.5KV | STATCOM CONTROL | STATCOM | UP-SET U-REF(PU) | AI
50 | 38.5KV | STATCOM CONTROL | STATCOM | DN-SET U-REF(PU) | AI
51 | 38.5KV | STATCOM CONTROL | STATCOM | Q-SET REF(PU)/FS REF(PU) | AI
52 | 415 V | AUX | DCDB-1 | DCDB-1 VOLTAGE | AI
53 | 415 V | AUX | DCDB-1 | BATTERY SET-1 CURRENT | AI
54 | 415 V | AUX | CHARGER-1 | BATTERY CHARGER-1 CURRENT | AI
55 | 415 V | AUX | DCDB-2 | DCDB-2 VOLTAGE | AI
56 | 415 V | AUX | DCDB-2 | BATTERY SET-2 CURRENT | AI
57 | 415 V | AUX | CHARGER-2 | BATTERY CHARGER-2 CURRENT | AI
58 | 415 V | AUX | MSB INCOMER-1 | VOLTAGE R-Y | AI
59 | 415 V | AUX | MSB INCOMER-1 | VOLTAGE Y-B | AI
60 | 415 V | AUX | MSB INCOMER-1 | VOLTAGE B-R | AI
61 | 415 V | AUX | MSB INCOMER-1 | CURRENT R | AI
62 | 415 V | AUX | MSB INCOMER-1 | CURRENT Y | AI
63 | 415 V | AUX | MSB INCOMER-1 | CURRENT B | AI
64 | 415 V | AUX | MSB INCOMER-2 | VOLTAGE R-Y | AI
65 | 415 V | AUX | MSB INCOMER-2 | VOLTAGE Y-B | AI
66 | 415 V | AUX | MSB INCOMER-2 | VOLTAGE B-R | AI
67 | 415 V | AUX | MSB INCOMER-2 | CURRENT R | AI
68 | 415 V | AUX | MSB INCOMER-2 | CURRENT Y | AI
69 | 415 V | AUX | MSB INCOMER-2 | CURRENT B | AI
70 | 415 V | AUX | AIRCON AMBIENT | AMBIENT TEMPERATURE SWITCHYARD | AI
71 | 415 V | AUX | AIRCON CONTROL ROOM | CONTROL ROOM TEMPERATURE | AI
72 | 415 V | AUX | AIRCON BATTERY ROOM | BATTERY ROOM TEMPERATURE | AI
73 | 415 V | AUX | AIRCON UPS ROOM | UPS ROOM TEMPERATURE | AI
STATCOM (HYOSUNG)
1 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY Voltage R-Y | AI
2 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY Voltage Y-B | AI
3 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN BAY Voltage B-R | AI
4 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN + TIE Current_Phase R | AI
5 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN + TIE Current_Phase Y | AI
6 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | 400kV MAIN + TIE Current_Phase B | AI
7 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | MVAR OF COUPLING TRANSFORMER HV SIDE | AI
8 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA R-PH) C2H2 | AI
9 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA R-PH) C2H4 | AI
10 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA R-PH) C2H6 | AI
11 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA R-PH) CH4 | AI
12 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA R-PH) CO2 | AI
13 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA R-PH) CO | AI
14 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA R-PH) H2O | AI
15 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA R-PH) H2 | AI
16 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA Y-PH) C2H2 | AI
17 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA Y-PH) C2H4 | AI
18 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA Y-PH) C2H6 | AI
19 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA Y-PH) CH4 | AI
20 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA Y-PH) CO2 | AI
21 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA Y-PH) CO | AI
22 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA Y-PH) H2O | AI
23 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA Y-PH) H2 | AI
24 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA B-PH) C2H2 | AI
25 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA B-PH) C2H4 | AI
26 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA B-PH) C2H6 | AI
27 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA B-PH) CH4 | AI
28 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA B-PH) CO2 | AI
29 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA B-PH) CO | AI
30 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA B-PH) H2O | AI
31 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA B-PH) H2 | AI
32 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA SP-PH) C2H2 | AI
33 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA SP-PH) C2H4 | AI
34 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA SP-PH) C2H6 | AI
35 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA SP-PH) CH4 | AI
36 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA SP-PH) CO2 | AI
37 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA SP-PH) CO | AI
38 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA SP-PH) H2O | AI
39 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (ODGA SP-PH) H2 | AI
40 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) WTI-HV | AI
41 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) WTI-LV | AI
42 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO R-PH) OTI | AI
43 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) WTI-HV | AI
44 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) WTI-LV | AI
45 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO Y-PH) OTI | AI
46 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) WTI-HV | AI
47 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) WTI-LV | AI
48 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO B-PH) OTI | AI
49 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) WTI-HV | AI
50 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) WTI-LV | AI
51 | ABC | COUPLING TRANSFORMER (HV) | TRAFO (HV) | (C. TRAFO SP-PH) OTI | AI
52 | 20KV | STATCOM-1 | VSC-1 | STATCOM UNIT-1 MVAR | AI
53 | 20KV | STATCOM-2 | VSC-2 | STATCOM UNIT-2 MVAR | AI
54 | 20KV | STATCOM CONTROL | STATCOM | V-REF SETTING | AI
55 | 20KV | STATCOM CONTROL | STATCOM | DROOP SETTING | AI
56 | 20KV | STATCOM CONTROL | STATCOM | DEAD-BAND UP SETTING | AI
57 | 20KV | STATCOM CONTROL | STATCOM | DEAD-BAND DN SETTING | AI
58 | 20KV | STATCOM CONTROL | STATCOM | Q-REF SETTING | AI
59 | 20KV | MV BUS BAR | MV BUS BAR | MV BUS VOLTAGE | AI
60 | 20KV | AUX.T/F | MV AUX T/F | KW | AI
61 | 20KV | AUX.T/F | MV AUX T/F | KVAR | AI
62 | 33KV | AUX.T/F | TERTIARY | KW | AI
63 | 33KV | AUX.T/F | TERTIARY | KVAR | AI
64 | 415 V | DCDB | DCDB-1 | 220V DCDB-1 VOLTAGE | AI
65 | 415 V | DCDB | DCDB-1 | 220V BATTERY SET-1 CURRENT | AI
66 | 415 V | DCDB | DCDB-1 | 220V BATTERY CHARGER-1 CURRENT | AI
67 | 415 V | DCDB | DCDB-2 | 220V DCDB-2 VOLTAGE | AI
68 | 415 V | DCDB | DCDB-2 | 220V BATTERY SET-2 CURRENT | AI
69 | 415 V | DCDB | DCDB-2 | 220V BATTERY CHARGER-2 CURRENT | AI
70 | 415 V | LTSUP | MSB-1 | (R-PH) INCOMER-1 VOLTAGE | AI
71 | 415 V | LTSUP | MSB-1 | (Y-PH) INCOMER-1 VOLTAGE | AI
72 | 415 V | LTSUP | MSB-1 | (B-PH) INCOMER-1 VOLTAGE | AI
73 | 415 V | LTSUP | MSB-2 | (R-PH) INCOMER-2 VOLTAGE | AI
74 | 415 V | LTSUP | MSB-2 | (Y-PH) INCOMER-2 VOLTAGE | AI
75 | 415 V | LTSUP | MSB-2 | (B-PH) INCOMER-2 VOLTAGE | AI
76 | 415 V | LTSUP | MSB-1 | (R-PH) INCOMER-1 CURRENT | AI
77 | 415 V | LTSUP | MSB-1 | (Y-PH) INCOMER-1 CURRENT | AI
78 | 415 V | LTSUP | MSB-1 | (B-PH) INCOMER-1 CURRENT | AI
79 | 415 V | LTSUP | MSB-2 | (R-PH) INCOMER-2 CURRENT | AI
80 | 415 V | LTSUP | MSB-2 | (Y-PH) INCOMER-2 CURRENT | AI
81 | 415 V | LTSUP | MSB-2 | (B-PH) INCOMER-2 CURRENT | AI
82 | 415 V | LTSUP | DGSET | (R-PH) DG FEEDER VOLTAGE | AI
83 | 415 V | LTSUP | DGSET | (Y-PH) DG FEEDER VOLTAGE | AI
84 | 415 V | LTSUP | DGSET | (B-PH) DG FEEDER VOLTAGE | AI
85 | 415 V | LTSUP | DGSET | (R-PH) DG FEEDER CURRENT | AI
86 | 415 V | LTSUP | DGSET | (Y-PH) DG FEEDER CURRENT | AI
87 | 415 V | LTSUP | DGSET | (B-PH) DG FEEDER CURRENT | AI
88 | 20KV | MSR-1 | MSR | MSR-1 MVAR | AI
89 | 20KV | MSR-2 | MSR | MSR-2 MVAR | AI
90 | 20KV | MSC | MSC | MSC MVAR | AI
91 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | CONTROL MODE : MANUAL Q CONTROL / AUTOMATIC VOLTAGE | APC |  | 1 : Manual Q / 5 : Automatic Voltage
92 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | V-REF SETTING | APC
93 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | DEAD-BAND UP SETTING | APC
94 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | DEAD-BAND DN SETTING | APC
95 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | DROOP SETTING | APC
96 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | Q-REF SETTING | APC
97 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | POD CONTROL ENABLE | APC |  | 1 : Manual Q / 5 : Automatic Voltage
98 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | SSOD CONTROL ENABLE | APC |  | 1 : Manual Q / 5 : Automatic Voltage
99 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | ADACTIVE GAIN REDUCTION ENABLE | APC |  | 1 : Manual Q / 5 : Automatic Voltage
100 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | ADACTIVE GAIN CLACULATION ENABLE | APC |  | 1 : Manual Q / 5 : Automatic Voltage
101 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | NEGATIVE SEQ. VOLTAGE CONTROL ENABLE | APC |  | 1 : Manual Q / 5 : Automatic Voltage
102 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | MSC CONTROL MODE - AUTOMATIC / MANUAL | APC |  | 1 : Manual Q / 5 : Automatic Voltage
103 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | MSR-1 CONTROL MODE - AUTOMATIC / MANUAL | APC |  | 1 : Manual Q / 5 : Automatic Voltage
104 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | MSR-2 CONTROL MODE - AUTOMATIC / MANUAL | APC |  | 1 : Manual Q / 5 : Automatic Voltage
105 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | HV BR MAIN BAY CONTROL MODE - AUTOMATIC (HYD ONLY) | APC |  | 1 : Manual Q / 5 : Automatic Voltage
106 | 20KV | STATCOM-1 | STATCOM CONTROLLER A | HV BR TIE BAY CONTROL MODE - AUTOMATIC (HYD ONLY) | APC |  | 1 : Manual Q / 5 : Automatic Voltage
107 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | CONTROL MODE : MANUAL Q CONTROL / AUTOMATIC VOLTAGE | APC |  | 1 : Manual Q / 5 : Automatic Voltage
108 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | V-REF SETTING | APC
109 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | DEAD-BAND UP SETTING | APC
110 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | DEAD-BAND DN SETTING | APC
111 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | DROOP SETTING | APC
112 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | Q-REF SETTING | APC
113 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | POD CONTROL ENABLE | APC |  | 1 : Manual Q / 5 : Automatic Voltage
114 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | SSOD CONTROL ENABLE | APC |  | 1 : Manual Q / 5 : Automatic Voltage
115 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | ADACTIVE GAIN REDUCTION ENABLE | APC |  | 1 : Manual Q / 5 : Automatic Voltage
116 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | ADACTIVE GAIN CLACULATION ENABLE | APC |  | 1 : Manual Q / 5 : Automatic Voltage
117 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | NEGATIVE SEQ. VOLTAGE CONTROL ENABLE | APC |  | 1 : Manual Q / 5 : Automatic Voltage
118 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | MSC CONTROL MODE - AUTOMATIC / MANUAL | APC |  | 1 : Manual Q / 5 : Automatic Voltage
119 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | MSR-1 CONTROL MODE - AUTOMATIC / MANUAL | APC |  | 1 : Manual Q / 5 : Automatic Voltage
120 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | MSR-2 CONTROL MODE - AUTOMATIC / MANUAL | APC |  | 1 : Manual Q / 5 : Automatic Voltage
121 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | HV BR MAIN BAY CONTROL MODE - AUTOMATIC / MANUAL (HYD ONLY) | APC |  | 1 : Manual Q / 5 : Automatic Voltage
122 | 20KV | STATCOM-2 | STATCOM CONTROLLER B | HV BR TIE BAY CONTROL MODE - AUTOMATIC / MANUAL (HYD ONLY) | APC |  | 1 : Manual Q / 5 : Automatic Voltage