## NEW (hidden)
S. No. | VOLT. LEVEL | BAY NAME | BAY NUM. | FEEDER TYPE | DEVICE IDENTIFICATION | POINT DESCRIPTION | DATA TYPE | IEC 104 ADDRESS | REMARK
1 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB OPEN/CLOSE STATUS | DPS
3 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR-RPh | BPCB R PHASE OPEN/CLOSE STATUS | DPS
5 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR-YPh | BPCB Y PHASE OPEN/CLOSE STATUS | DPS
7 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR-Bph | BPCB B PHASE OPEN/CLOSE STATUS | DPS
9 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS MBS ISOLATOR OPEN/CLOSE STATUS | DPS
10 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | ISOLATOR 1 OPEN/CLOSE STATUS | DPS
11 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | ISOLATOR 2 OPEN/CLOSE STATUS | DPS
12 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89ES1 | EARTH SWITCH 1 OPERATION INTERLOCK | SPS
13 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89ES2 | EARTH SWITCH 2 OPERATION INTERLOCK | SPS
14 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89ES1 | EARTH SWITCH 1 OPEN/CLOSE STATUS | DPS
15 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89ES2 | EARTH SWITCH 2 OPEN/CLOSE STATUS | DPS
16 | …KV | XXXXXX | BAY NO | FSC | BAY NO | LINE DE-ENRGIZED | SPS
17 | …KV | XXXXXX | BAY NO | FSC | BAY NO | FAULT TO PLATFORM TRIP-1/2 | SPS
18 | …KV | XXXXXX | BAY NO | FSC | BAY NO | PERMANENT BYPASS | SPS
19 | …KV | XXXXXX | BAY NO | FSC | BAY NO | MOV TEMPERATURE R PHASE | AI
20 | …KV | XXXXXX | BAY NO | FSC | BAY NO | MOV TEMPERATURE Y PHASE | AI
21 | …KV | XXXXXX | BAY NO | FSC | BAY NO | MOV TEMPERATURE B PHASE | AI
22 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR R PHASE CURRENT | AI
23 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR Y PHASE CURRENT | AI
24 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR B PHASE CURRENT | AI
25 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR R PHASE UNBALANCED CURRENT | AI
26 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR Y PHASE UNBALANCED CURRENT | AI
27 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR B PHASE UNBALANCED CURRENT | AI
28 | …KV | XXXXXX | BAY NO | FSC | BAY NO | LINE CT CURRENT R-PH | AI
29 | …KV | XXXXXX | BAY NO | FSC | BAY NO | LINE CT CURRENT Y-PH | AI
30 | …KV | XXXXXX | BAY NO | FSC | BAY NO | LINE CT CURRENT B-PH | AI
31 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB STATUS DISCREPANCY | SPS
32 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB AUX CONTACT DISCORDANCE | SPS
33 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | GENRAL LOCKOUT/MIN OIL PRESSURE LOCKOUT | SPS
34 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB POLE DISCREPANCY | SPS
35 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB DC 1/2 FAIL | SPS
36 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB LOSS OF SF6 | SPS
37 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | 1POLE REINSERTION DURING AR | SPS
38 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER FAIL TO OPEN | SPS |  | COMMON- R-PH,Y-PH,B-PH FAIL TO OPEN
39 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER SWITCHWED WITHOUT COMMAND | SPS
40 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER FAIL TO CLOSE | SPS |  | COMMON- R-PH,Y-PH,B-PH FAIL TO CLOSE
41 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS CB SPRING DISCHARGE/FAILURE | SPS
42 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB OPEN CMD | DPC
43 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB CLOSE CMD | DPC
44 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB OPERATION INTERLOCK | SPS
45 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS MBS OPEN CMD | DPC
46 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS MBS CLOSE CMD | DPC
47 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS MBS OPERATION INTERLOCK | SPS
48 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | BYPASS CAP ISO 1 OPEN CMD | DPC
49 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | BYPASS CAP ISO 1 CLOSE CMD | DPC
50 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | BYPASS CAP ISO 1 OPERATION INTERLOCK | SPS
51 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | BYPASS CAP ISO 2 OPEN CMD | DPC
52 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | BYPASS CAP ISO 2 CLOSE CMD | DPC
53 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | DISCONNECTOR 1 PHASE DISAGREEMENT | SPS
54 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | GENERAL ALARM | SPS
55 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS DISCONNECTOR ALARM | SPS
56 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | DISCONNECTOR 2 PHASE DISAGREEMENT | SPS
57 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | GENERAL ALARM | SPS
58 | …KV | XXXXXX | BAY NO | FSC | BAY NO-CAP | CAPACITOR UNBALANCE ALARM | SPS
59 | …KV | XXXXXX | BAY NO | FSC | BAY NO-CAP | CAPACITOR UNBALANCED TRIP | SPS |  | FOR BOTH HIGH SET AND LOW SET (IF AVAILABLE)
60 | …KV | XXXXXX | BAY NO | FSC | BAY NO-CAP | CAPACITOR OVERLOAD ALARM | SPS
61 | …KV | XXXXXX | BAY NO | FSC | BAY NO-CAP | CAPACITOR OVERLOAD TRIP | SPS
62 | …KV | XXXXXX | BAY NO | FSC | BAY NO-MOV | MOV TRIP | SPS
63 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM FAIL-1 | SPS
64 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM FAIL-2 | SPS
65 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | SIGNAL TRANSMISSION POWER FAIL | SPS
66 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | MASTER TRIP | SPS
67 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | GPS TIME SYNC FAIL | SPS
68 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | DIRECT TRIP RECEIVE | SPS
69 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | COMMUNICATION CHANNEL FAIL | SPS
70 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | BYPASS CAP ISO 2 OPERATION INTERLOCK | SPS
71 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | MASTER TRIP RST | SPC
72 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | MOV FAIL | SPS |  | COMMON- R-PH,Y-PH,B-PH
73 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | KIOSK TEMP | AI
74 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL SYSTEM 1 HARDWARE ALARM | SPS |  | Group Alarm
75 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM 1 HARDWARE ALARM | SPS |  | Group Alarm
76 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL & PROTECTION SYSTEM 1 COMMUNICATION FAULT | SPS |  | Group Alarm
77 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM 1 MEASURING SYSTEM WARNING | SPS |  | Group Alarm
78 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL SYSTEM 2 HARDWARE ALARM | SPS |  | Group Alarm
79 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM 2 HARDWARE ALARM | SPS |  | Group Alarm
80 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL & PROTECTION SYSTEM 2 COMMUNICATION FAULT | SPS |  | Group Alarm
81 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM 2 MEASURING SYSTEM WARNING | SPS |  | Group Alarm
82 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL & PROTECTION SYSTEM POWER SUPPLY ALARM | SPS |  | Group Alarm
83 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL & PROTECTION SYSTEM REDUNDANCY DISTURBED | SPS |  | Group Alarm
84 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | EARTH SWITCH 1 ALARM | SPS |  | Group Alarm
85 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | EARTH SWITCH 2 ALARM | SPS |  | Group Alarm
86 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | DISCONNECTOR SWITCH 1 ALARM | SPS |  | Group Alarm
87 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | DISCONNECTOR SWITCH 2 ALARM | SPS |  | Group Alarm
88 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | LINE EARTH SWITCH ALARM | SPS |  | Group Alarm
89 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | BYPASS BREAKER ALARM | SPS |  | Group Alarm
90 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | MAIN BYPASS SWITCH ALARM | SPS |  | Group Alarm
91 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | LINE SIDE 1: DE-ENERGIZED | SPS
92 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | LINE SIDE 2: DE-ENERGIZED | SPS
93 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER LOCAL/REMOTE CONTROL | SPS
94 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER MAIN CLOSING COIL UNHEALTHY | SPS
95 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER BACKUP CLOSING COIL UNHEALTHY | SPS
96 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | FIRE FIGHTING SYSTEM: ALARM | SPS
97 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV OVERLOAD | SPS
98 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV TEMPERATURE TRIP | SPS
99 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV TEMPERATURE GRADIENT LOW SET | SPS
100 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV TEMPERATURE GRADIENT HIGH SET | SPS
101 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV UNBALANCE | SPS
102 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV HIGH CURRENT | SPS
103 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP FAILED TO TRIGGER | SPS
104 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP DELAYED TRIGGER | SPS
105 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP PROLONGED CONDUCTION | SPS
106 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP SELF TRIGGER | SPS
107 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP TRIGGER (R,Y,B) | SPS |  | R,Y,B Phase to be combined
108 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: BYPASS BREAKER FAIL | SPS
109 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: PREVENT REINSERTION ACTIVE | SPS
110 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: PERMANENT BYPASS | SPS
111 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: TEMPORARY BYPASS PHASE(R,Y,B) | SPS |  | R,Y,B Phase to be combined
112 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: REINSERTION | SPS
113 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: LINE TRIP | SPS
114 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV OVERLOAD | SPS
115 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV TEMPERATURE TRIP | SPS
116 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV TEMPERATURE GRADIENT LOW SET | SPS
117 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV TEMPERATURE GRADIENT HIGH SET | SPS
118 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV UNBALANCE | SPS
119 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV HIGH CURRENT | SPS
120 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP FAILED TO TRIGGER | SPS
121 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP DELAYED TRIGGER | SPS
122 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP PROLONGED CONDUCTION | SPS
123 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP SELF TRIGGER | SPS
124 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP TRIGGER (R,Y,B) | SPS |  | R,Y,B Phase to be combined
125 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: BYPASS BREAKER FAIL | SPS
126 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: PREVENT REINSERTION ACTIVE | SPS
127 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: PERMANENT BYPASS | SPS
128 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: TEMPORARY BYPASS PHASE(R,Y,B) | SPS |  | R,Y,B Phase to be combined
129 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: REINSERTION | SPS
130 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: LINE TRIP | SPS

## FSC SIGNALS-SIEMENS (hidden)
S. No. | VOLT. LEVEL | BAY NAME | BAY NUM. | FEEDER TYPE | DEVICE IDENTIFICATION | POINT DESCRIPTION | DATA TYPE | IEC 104 ADDRESS | REMARK
1 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB OPEN/CLOSE STATUS | DPS
3 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR-RPh | BPCB R PHASE OPEN/CLOSE STATUS | DPS
5 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR-YPh | BPCB Y PHASE OPEN/CLOSE STATUS | DPS
7 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR-Bph | BPCB B PHASE OPEN/CLOSE STATUS | DPS
9 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS MBS ISOLATOR OPEN/CLOSE STATUS | DPS
10 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | ISOLATOR 1 OPEN/CLOSE STATUS | DPS
11 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | ISOLATOR 2 OPEN/CLOSE STATUS | DPS
12 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89ES1 | EARTH SWITCH 1 OPERATION INTERLOCK | SPS
13 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89ES2 | EARTH SWITCH 2 OPERATION INTERLOCK | SPS
14 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89ES1 | EARTH SWITCH 1 OPEN/CLOSE STATUS | DPS
15 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89ES2 | EARTH SWITCH 2 OPEN/CLOSE STATUS | DPS
16 | …KV | XXXXXX | BAY NO | FSC | BAY NO | LINE DE-ENRGIZED | SPS
17 | …KV | XXXXXX | BAY NO | FSC | BAY NO | FAULT TO PLATFORM TRIP-1/2 | SPS
18 | …KV | XXXXXX | BAY NO | FSC | BAY NO | PERMANENT BYPASS | SPS
19 | …KV | XXXXXX | BAY NO | FSC | BAY NO | MOV TEMPERATURE R PHASE | AI
20 | …KV | XXXXXX | BAY NO | FSC | BAY NO | MOV TEMPERATURE Y PHASE | AI
21 | …KV | XXXXXX | BAY NO | FSC | BAY NO | MOV TEMPERATURE B PHASE | AI
22 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR R PHASE CURRENT | AI
23 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR Y PHASE CURRENT | AI
24 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR B PHASE CURRENT | AI
25 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR R PHASE UNBALANCED CURRENT | AI
26 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR Y PHASE UNBALANCED CURRENT | AI
27 | …KV | XXXXXX | BAY NO | FSC | BAY NO | CAPACITOR B PHASE UNBALANCED CURRENT | AI
28 | …KV | XXXXXX | BAY NO | FSC | BAY NO | LINE CT CURRENT R-PH | AI
29 | …KV | XXXXXX | BAY NO | FSC | BAY NO | LINE CT CURRENT Y-PH | AI
30 | …KV | XXXXXX | BAY NO | FSC | BAY NO | LINE CT CURRENT B-PH | AI
31 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB STATUS DISCREPANCY | SPS
32 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB AUX CONTACT DISCORDANCE | SPS
33 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | GENRAL LOCKOUT/MIN OIL PRESSURE LOCKOUT | SPS
34 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB POLE DISCREPANCY | SPS
35 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB DC 1/2 FAIL | SPS
36 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB LOSS OF SF6 | SPS
37 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | 1POLE REINSERTION DURING AR | SPS
38 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER FAIL TO OPEN | SPS |  | COMMON- R-PH,Y-PH,B-PH FAIL TO OPEN
39 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER SWITCHWED WITHOUT COMMAND | SPS
40 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER FAIL TO CLOSE | SPS |  | COMMON- R-PH,Y-PH,B-PH FAIL TO CLOSE
41 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS CB SPRING DISCHARGE/FAILURE | SPS
42 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB OPEN CMD | DPC
43 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB CLOSE CMD | DPC
44 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BPCB OPERATION INTERLOCK | SPS
45 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS MBS OPEN CMD | DPC
46 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS MBS CLOSE CMD | DPC
47 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS MBS OPERATION INTERLOCK | SPS
48 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | BYPASS CAP ISO 1 OPEN CMD | DPC
49 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | BYPASS CAP ISO 1 CLOSE CMD | DPC
50 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | BYPASS CAP ISO 1 OPERATION INTERLOCK | SPS
51 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | BYPASS CAP ISO 2 OPEN CMD | DPC
52 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | BYPASS CAP ISO 2 CLOSE CMD | DPC
53 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | DISCONNECTOR 1 PHASE DISAGREEMENT | SPS
54 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS1 | GENERAL ALARM | SPS
55 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89MBS | BYPASS DISCONNECTOR ALARM | SPS
56 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | DISCONNECTOR 2 PHASE DISAGREEMENT | SPS
57 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | GENERAL ALARM | SPS
58 | …KV | XXXXXX | BAY NO | FSC | BAY NO-CAP | CAPACITOR UNBALANCE ALARM | SPS
59 | …KV | XXXXXX | BAY NO | FSC | BAY NO-CAP | CAPACITOR UNBALANCED TRIP | SPS |  | FOR BOTH HIGH SET AND LOW SET (IF AVAILABLE)
60 | …KV | XXXXXX | BAY NO | FSC | BAY NO-CAP | CAPACITOR OVERLOAD ALARM | SPS
61 | …KV | XXXXXX | BAY NO | FSC | BAY NO-CAP | CAPACITOR OVERLOAD TRIP | SPS
62 | …KV | XXXXXX | BAY NO | FSC | BAY NO-MOV | MOV TRIP | SPS
63 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM FAIL-1 | SPS
64 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM FAIL-2 | SPS
65 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | SIGNAL TRANSMISSION POWER FAIL | SPS
66 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | MASTER TRIP | SPS
67 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | GPS TIME SYNC FAIL | SPS
68 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | DIRECT TRIP RECEIVE | SPS
69 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | COMMUNICATION CHANNEL FAIL | SPS
70 | …KV | XXXXXX | BAY NO | FSC | BAY NO-89DS2 | BYPASS CAP ISO 2 OPERATION INTERLOCK | SPS
71 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | MASTER TRIP RST | SPC
72 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | MOV FAIL | SPS |  | COMMON- R-PH,Y-PH,B-PH
73 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | KIOSK TEMP | AI
74 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL SYSTEM 1 HARDWARE ALARM | SPS |  | Group Alarm
75 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM 1 HARDWARE ALARM | SPS |  | Group Alarm
76 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL & PROTECTION SYSTEM 1 COMMUNICATION FAULT | SPS |  | Group Alarm
77 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM 1 MEASURING SYSTEM WARNING | SPS |  | Group Alarm
78 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL SYSTEM 2 HARDWARE ALARM | SPS |  | Group Alarm
79 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM 2 HARDWARE ALARM | SPS |  | Group Alarm
80 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL & PROTECTION SYSTEM 2 COMMUNICATION FAULT | SPS |  | Group Alarm
81 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | PROTECTION SYSTEM 2 MEASURING SYSTEM WARNING | SPS |  | Group Alarm
82 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL & PROTECTION SYSTEM POWER SUPPLY ALARM | SPS |  | Group Alarm
83 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | CONTROL & PROTECTION SYSTEM REDUNDANCY DISTURBED | SPS |  | Group Alarm
84 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | EARTH SWITCH 1 ALARM | SPS |  | Group Alarm
85 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | EARTH SWITCH 2 ALARM | SPS |  | Group Alarm
86 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | DISCONNECTOR SWITCH 1 ALARM | SPS |  | Group Alarm
87 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | DISCONNECTOR SWITCH 2 ALARM | SPS |  | Group Alarm
88 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | LINE EARTH SWITCH ALARM | SPS |  | Group Alarm
89 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | BYPASS BREAKER ALARM | SPS |  | Group Alarm
90 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | MAIN BYPASS SWITCH ALARM | SPS |  | Group Alarm
91 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | LINE SIDE 1: DE-ENERGIZED | SPS
92 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | LINE SIDE 2: DE-ENERGIZED | SPS
93 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER LOCAL/REMOTE CONTROL | SPS
94 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER MAIN CLOSING COIL UNHEALTHY | SPS
95 | …KV | XXXXXX | BAY NO | FSC | BAY NO-52BBR | BYPASS BREAKER BACKUP CLOSING COIL UNHEALTHY | SPS
96 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT | FIRE FIGHTING SYSTEM: ALARM | SPS
97 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV OVERLOAD | SPS
98 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV TEMPERATURE TRIP | SPS
99 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV TEMPERATURE GRADIENT LOW SET | SPS
100 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV TEMPERATURE GRADIENT HIGH SET | SPS
101 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV UNBALANCE | SPS
102 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: MOV HIGH CURRENT | SPS
103 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP FAILED TO TRIGGER | SPS
104 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP DELAYED TRIGGER | SPS
105 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP PROLONGED CONDUCTION | SPS
106 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP SELF TRIGGER | SPS
107 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: SPARK GAP TRIGGER (R,Y,B) | SPS |  | R,Y,B Phase to be combined
108 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: BYPASS BREAKER FAIL | SPS
109 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: PREVENT REINSERTION ACTIVE | SPS
110 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: PERMANENT BYPASS | SPS
111 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: TEMPORARY BYPASS PHASE(R,Y,B) | SPS |  | R,Y,B Phase to be combined
112 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: REINSERTION | SPS
113 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-1 | SYSTEM 1: LINE TRIP | SPS
114 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV OVERLOAD | SPS
115 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV TEMPERATURE TRIP | SPS
116 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV TEMPERATURE GRADIENT LOW SET | SPS
117 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV TEMPERATURE GRADIENT HIGH SET | SPS
118 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV UNBALANCE | SPS
119 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: MOV HIGH CURRENT | SPS
120 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP FAILED TO TRIGGER | SPS
121 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP DELAYED TRIGGER | SPS
122 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP PROLONGED CONDUCTION | SPS
123 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP SELF TRIGGER | SPS
124 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: SPARK GAP TRIGGER (R,Y,B) | SPS |  | R,Y,B Phase to be combined
125 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: BYPASS BREAKER FAIL | SPS
126 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: PREVENT REINSERTION ACTIVE | SPS
127 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: PERMANENT BYPASS | SPS
128 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: TEMPORARY BYPASS PHASE(R,Y,B) | SPS |  | R,Y,B Phase to be combined
129 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: REINSERTION | SPS
130 | …KV | XXXXXX | BAY NO | FSC | BAY NO-PROT-2 | SYSTEM 2: LINE TRIP | SPS

## SVC
NTAMC TYPICAL SIGNALS FOR SVC
SVC CONTROLLER AND PROTECTION |  |  | TSC/TCR |  |  | DTF FILTER
S.No | Signal name | TYPE | S.No | Signal name | TYPE | S.No | Signal name | TYPE
1 | SVC CONTROLLER 1 ALARM | SPS | 1 | TCR ALARM | SPS | 1 | DTF Filter Ararm | SPS
2 | SVC CONTROLLER 1 TRIP | SPS | 2 | TCR TRIP | SPS | 2 | DTF Filter Trip | SPS
3 | SVC CONTROLLER 2 ALARM | SPS | 3 | TCR Protn A Fail | SPS | 3 | Double Tunned Filter Protn A Fail | SPS
4 | SVC CONTROLLER 2 TRIP | SPS | 4 | TCR Protn A Trip | SPS | 4 | Double Tunned Filter Protn A Alarm | SPS
5 | Q-MODE ENABLED | SPS | 5 | TCR Protn A Alarm | SPS | 5 | Double Tunned Filter Protn A Trip | SPS
6 | SVC AUTOMATIC MODE (VCM) | SPS | 6 | TCR Protn B Fail | SPS | 6 | Double Tunned Filter Protn B Fail | SPS
7 | SVC CONTROL FROM LOCAL HMI 1/2 | SPS | 7 | TCR Protn B Trip | SPS | 7 | Double Tunned Filter Protn B Alarm | SPS
8 | SVC CONTROL FROM RCI 1/2 | SPS | 8 | TCR Protn B Alarm | SPS | 8 | Double Tunned Filter Protn B Trip | SPS
9 | SVC CONTROL FROM REMOTE HMI 1/2 | SPS | 9 | VALVE BASE ELECTRONIC TCR ALARM | SPS | 9 | DTF Cap Unbalance Protn A Failure/ Alarm Stage 2 | SPS
10 | SVC MANUAL MODE (FSM) | SPS | 10 | VALVE BASE ELECTRONIC TCR TRIP | SPS | 10 | DTF Cap Unbalance Protn A Unbalance Alarm/ Stage 1 | SPS
11 | SVC OFF | SPS | 11 | TSC -Cap unbalance protn A Failure | SPS | 11 | DTF Cap Unbalance Protn A TRIP | SPS
12 | SVC ON | SPS | 12 | TSC -Cap unbalance protn A Alarm | SPS | 12 | DTF Cap Unbalance Protn B Failure/ Alarm Stage 2 | SPS
13 | SVC READY FOR SWITCHING ON | SPS | 13 | TSC -Cap unbalance protn TRIP | SPS | 13 | DTF Cap Unbalance Protn B Unbalance Alarm Stage 1 | SPS
14 | SVC READY FOR SWITCHING OFF | SPS | 14 | TCR CURRENT PHASE A-B | AI | 14 | DTF Cap Unbalance Protn B TRIP | SPS
15 | SVC AUTOMATIC GAIN ADJUSTMENT ENABLED | SPS | 15 | TCR CURRENT PHASE B-C | AI | 15 | FILTER LOCK-OUT RELAY 1 RESET | SPC
16 | DTF 1/2 FILTER DISCHARGE TIME RUNNING | SPS | 16 | TCR CURRENT PHASE C-A | AI | 16 | FILTER LOCK-OUT RELAY 2 RESET | SPC
17 | SVC Control DEGRADED MODE | SPS | 17 | TCR LOCK-OUT RELAY 1 RESET | SPC | 17 | Filter Current R-Y | AI
18 | POWER OSCILLATION DAMPING ENABLED | SPS | 18 | TCR LOCK-OUT RELAY 2 RESET | SPC | 18 | Filter Current Y-B | AI
19 | POWER OSCILLATION DAMPING DISABLED | SPS | NOTE- 1)Sr.No. 11,12,13 is specific to TSC 2) Signal to be included for all TCRs & TSCs |  |  | 19 | Filter Current B-R | AI
20 | SVC AUTOMATIC GAIN ADJUSTMENT DISABLED | SPS |  |  |  | Note | Signal list to be included for all filters
21 | SVC Q-MODE DISABLED | SPS
22 | SVC CONTROL FROM FIELD | SPS
23 | SVC CONTROLLER-1/2 ALARM | SPS
24 | SVC CONTROLLER-1/2 TRIP | SPS | HV BUSBAR |  |  | STAR COUPLER
25 | SVC -PROTN SYSTEM-1/2 ALARM | SPS | S.No | Signal name | TYPE | S.No | Signal name | TYPE
26 | CONTROL SYSTEM 1 ACTIVE | SPS | 1 | HV BUSBAR ALARM | SPS | 1 | OTI ALARM | SPS
27 | CONTROL SYSTEM 2 ACTIVE | SPS | 2 | HV BUSBAR TRIP | SPS | 2 | OIL LOW LEVEL ALARM | SPS
28 | SVC ON SEQUENCE RUNNING | SPS | 3 | HV BUSBAR VOLTAGE R-Y | AI | 3 | BUCHHOLZ RELAY TRIP | SPS
29 | SVC OFF SEQUENCE RUNNING | SPS | 4 | HV BUSBAR VOLTAGE Y-B | AI | 4 | PRESSURE RELIEF DEVICE TRIP | SPS
30 | SVC NO SEQUENCE IS RUNNING | SPS | 5 | HV BUSBAR VOLTAGE B-R | AI | 5 | Bunchholz Alarm | SPS
31 | DIGITAL FAULT RECORDER FAULTY (DFR) | SPS |  |  |  | 6 | WTI ALARM | SPS
32 | DIGITAL FAULT RECORDER TRIGGERED (DFR) | SPS |  |  |  | 7 | WTI TRIP | SPS
33 | AC VOLTAGE STABELIZER ALARM | SPS | MV BUSBAR |  |  | 8 | OTI TRIP | SPS
34 | SVC -PROTN SYSTEM-1 ALARM | SPS | S.No | Signal name | TYPE | 9 | Neutral Star Coupler TFR Protn A FAIL | SPS
35 | SVC -PROTN SYSTEM-1 TRIP | SPS | 1 | MV BB Protn 1 FAILURE | SPS | 10 | Neutral Star Coupler TFR Protn A Trip | SPS
36 | SVC -PROTN SYSTEM-2 ALARM | SPS | 2 | MV BB Protn 1 TRIP | SPS | 11 | Neutral Star Coupler TFR Protn A Alarm | SPS
37 | SVC -PROTN SYSTEM-2 TRIP | SPS | 3 | MV BB Protn 1 ALARM | SPS | 12 | Neutral Star Coupler TFR Protn B FAIL | SPS
38 | PROTN 1 - ANY TEST SWITCH IN USE | SPS | 4 | MV BB Protn 2 FAILURE | SPS | 13 | Neutral Star Coupler TFR Protn B Trip | SPS
39 | PROTN 2 - ANY TEST SWITCH IN USE | SPS | 5 | MV BB Protn 2 TRIP | SPS | 14 | Neutral Star Coupler TFR Protn B Alarm | SPS
40 | SVC EMERGENCY TRIP 1 | SPC | 6 | MV BB Protn 2 ALARM | SPS
41 | SVC EMERGENCY TRIP 2 | SPC | 7 | MV BUSBAR ALARM | SPS | AUXILIARY TRANSFORMER
42 | CONTROL VIA RCI 1/2 COMMAND | SPC | 8 | MV BUSBAR TRIP | SPS | S.No | Signal name | TYPE
43 | POD POWER SELECTION COMMAND | SPC | 9 | MV BUSBAR VOLTAGE R-Y | AI | 1 | OTI ALARM | SPS
44 | POD FREQUENCY SELECTION COMMAND | SPC | 10 | MV BUSBAR VOLTAGE Y-B | AI | 2 | OTI TRIP | SPS
45 | AUTOMATIC CONTROL SELECTION (VOLTAGE CONT. MODE) | DPC | 11 | MV BUSBAR VOLTAGE B-R | AI | 3 | WTI ALARM | SPS
46 | MANUAL CONTROL SELECTION (FIXED SUSCEPT. MODE) | DPC |  |  |  | 4 | WTI TRIP | SPS
47 | Q CONTROL MODE ENABLE/ DISABLE COMMAND | DPC |  |  |  | 5 | OIL LOW LEVEL ALARM | SPS
48 | GAIN ADJUSTMENT ENABLE/ DISABLE COMMAND | DPC |  |  |  | 6 | BUCHHOLZ ALARM | SPS
49 | POWER OSCILLATION DAMPING CONTROL ENABLE/ DISABLE COMMAND | DPC |  |  |  | 7 | BUCHHOLZ RELAY TRIP | SPS
50 | REFERENCE VOLTAGE RAISE/ LOWER COMMAND | DPC | AUXILIARY |  |  | 8 | PRESSURE RELIEF DEVICE TRIP | SPS
51 | REACTIVE POWER MORE CAPACITIVE (RAISE)/ INDUCTIVE (LOWER) COMMAND | DPC | S.No | Signal name | TYPE | 9 | Aux Tfr Protn A FAIL | SPS
52 | MANUAL MODE REACTIVE OUTPUT MORE CAPACITIVE (RAISE)/ INDUCTIVE (LOWER) COMMAND | DPC | 1 | AHU Motor 1 Thermal overload trip | SPS | 10 | Aux Tfr Protn A Trip | SPS
53 | CONTROL SYSTEM SLOPE RAISE/ LOWER COMMAND | DPC | 2 | AHU Motor 2 Thermal overload trip | SPS | 11 | Aux Tfr Protn A Alarm | SPS
54 | VQ MINIMUM RAISE/ LOWER COMMAND | DPC | 3 | AHU Motor 1 Healthy | SPS | 12 | Aux Tfr Protn B FAIL | SPS
55 | VQ MAXIMUM RAISE/ LOWER COMMAND | DPC | 4 | AHU Motor 2 Healthy | SPS | 13 | Aux Tfr Protn B Trip | SPS
56 | UNDER VOLTAGE DETECTION RAISE/ LOWER COMMAND | DPC | 5 | AHU Motor 1 in service | SPS | 14 | Aux Tfr Protn B Alarm | SPS
57 | UNDER VOLTAGE RELEASE RAISE/ LOWER COMMAND | DPC | 6 | AHU Motor 2 in service | SPS | 15 | Auxilliary Tfr supply trip | SPS
58 | UNDER VOLTAGE DETECTION VALUE | AI | 7 | UPS Overload alarm | SPS | 16 | AUX LOCK-OUT RELAY 1 RESET | SPC
59 | UNDER VOLTAGE RELEASE VALUE | AI | 8 | UPS Overload trip | SPS | 17 | AUX LOCK-OUT RELAY 2 RESET | SPC
60 | ACTUAL VOLTAGE VALUE | AI | 9 | UPS Battery Under Voltage | SPS
61 | SVC REACTIVE POWER | AI | 10 | UPS main supply Off | SPS
62 | FREQUENCY | AI | 11 | BATTERY ROOM General Alarm | SPS
63 | CONTROLLER GAIN | AI | 12 | SVC CONTROL ROOM General alarm | SPS
64 | SVC REACTIVE POWER REFERENCE VALUE | AI | 13 | UPS Fan failure | SPS | COOLING SYSTEM
65 | SVC REACTIVE POWER REFERENCE VALUE | AI | 14 | UPS-1 BATTERY MCCB OFF/TRIP | SPS | S.No | Signal name | TYPE
66 | SLOPE VALUE | AI | 15 | UPS-1 TROUBLE COMMON ALARM | SPS | 1 | COOLING SYSTEM FLOW | AI
67 | FIXED SUSCEPTANCE REFERENCE VALUE | AI | NOTE- 1)Other signals are to be taken from Auxiliary typical list. |  |  | 2 | COOLING SYSTEM PRESSURE VALVE INLET | AI
68 | MINIMUM VALUE FOR Q-CONTROLLER | AI |  |  |  | 3 | COOLING SYSTEM EXPANSION TANK LEVEL | AI
69 | MAXIMUM VALUE FOR Q-CONTROLLER | AI |  |  |  | 4 | COOLING SYSTEM CONDUCTIVITY MAIN CIRCUIT | AI
70 | GAIN REDUCTION FACTOR | AI |  |  |  | 5 | COOLING SYSTEM CONDUCTIVITY ION EXCHANGER | AI
71 | DEGRADED MODE | AI |  |  |  | 6 | COOLING SYSTEM VALVE INLET TEMPERATURE | AI
72 | SVC PRIMARY CURRENT R | AI |  |  |  | 7 | THYRISTOR COOLING SYSTEM - ALARM | SPS
73 | SVC PRIMARY CURRENT Y | AI |  |  |  | 8 | THYRISTOR COOLING SYSTEM - TRIP | SPS
74 | SVC PRIMARY CURRENT B | AI
75 | DIGITAL FAULT RECORDER FAULTY (DFR) | SPS
76 | DIGITAL FAULT RECORDER TRIGGERED (DFR) | SPS
NOTE- 1. For 400KV bays, Typical datalist of respective bay is to be referred. 2. For all CB, ISOLATOR and Earthswitch, Typical list of Switchgears to be referred. 3. Grouping of Signals may be done as per site condition. 4. If any other signal is required for remote operation as per site condition, it needs to be incorporated in final signal list. 5. Indexing of Equipments in signal list may be done as per design and availability.
NOTE- If any other signal is required for remote operation as per site condition, it needs to be incorporated in final signal list.